## Workflow
| Asset Population (% completion?) | [6 empty] | PM Population
Plant Area | Asset List Step 1 complete | Photos taken on plant | Folder Structure Generated | Make / Model / Serial Found | Manuals Found | Asset List Step 2 complete | Documents/ Drawings/Manuals added to assets | ? | ? | ? | ? | ?
1000 - General Plant and Weighscales
1100 - Receiving
1200 - FCON
1300 - Digesters
1400 - Digestate
1500 - Gas Plant
1600 - Utilities
1700 - BioSolids
1800 - Water Management

## Categories & Custom Columns
Category | Custom Columns | Todo Now (*) 1200 & 1300 | Person
Global
Make
Model
Serial
| P&ID Doc Name | *
| P&ID Page | *
| P&ID Tag | * [DONE]
Locations And Facilities
Equipment
Equipment Voltage
Equipment Amps
Equipment Power
Equipment Fluid
Equipment Material of Construction
Equipment Diameter
Equipment Classification
Equipment Power Feed Location
| Equipment Type | * [DONE] | Neil
Lines
| Line Fluid | *[DONE] | Neil
| Line Material of Construction | * | Neil
| Line Diameter | * | Neil
| Line From | * | Neil
| Line To | * | Neil
| Line Insulation | * | Neil
| Line Design Pressure | * | Neil
| Line Schedule |  | Neil
| Line Flange Class | * | Neil
Valves
| Valve Voltage | * | Miro
| Valve Fluid | [DONE] | Miro
| Valve Material of Construction | [DONE] | Miro
| Valve Diameter | *[DONE] | Miro
| Valve Power Feed Location |  | Miro
| Valve Seal Material | * | Miro
| Valve Auto/Manual | *[DONE] | Miro
| Valve Type | *[DONE] | Miro
| Valve Actuator Type | * | Miro
| Valve Connection Type | [DONE] | Miro
| Valve Seat Material | [DONE] | Miro
Tanks
| Tank Fluid | * [DONE] | Neil
| Tank Material of Construction | * [DONE] | Neil
| Tank Diameter | * [DONE] | Neil
| Tank Height | * [DONE] | Neil
| Tank Volume | * [DONE] | Neil
| Tank Working Volume | * [DONE] | Neil
| Tank Working Height | * [DONE] | Neil
| Tank Type | * [DONE] | Neil
Instruments
| Instrument Voltage |  | Miro
| Instrument Fluid | [DONE] | Miro
| Instrument Classification |  | Miro
| Instrument Connection Type | [DONE] | Miro
| Instrument Power Feed Location |  | Miro
| Instrument Type | *[DONE] | Miro
| Instrument Wire Count |  | Miro
| Instrument Analog/Digital | [DONE] | Miro
| Instrument Mount Detail |  | Miro
Panels |  | * | Neil
Panels Voltage
Panels Amps
Panels Power Feed Location
Panel Type
Permits
Permit Number
Permit Description
Permit Title
Permit Permitting Body
Permit Plant Area
Permit Revision Number
Permit Expiry
Packages
Package Voltage
Package Amps
Package Power
Package Power Feed Location
Note on B3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not a real category

## Master Template
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Material of Construction | Instrument Diameter | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes

## 1000 - General Plant
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Material of Construction | Instrument Diameter | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes

## 1100 - Receiving
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual RQD | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Connection Type | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | *Any Custom Fields* | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes
1100 - Receiving Area | C2NC-1100 | C2NC | Locations And Facilities | Receiving
Villari Feedstock | C2NC-1100-VLR | C2NC-1100 | Locations And Facilities | Villari Feedstock
Receiving Area Unloading | C2NC-1100-UNL | C2NC-1100 | Locations And Facilities | Tanker Unloading
Feedstock Slurry | C2NC-1100-SLR | C2NC-1100 | Locations And Facilities | Feedstock Slurry
Receiving Pit | C2NC-1100-000 | C2NC-1100 | Locations And Facilities | Receiving Pit
4 inch VAC Tanker Truck Unloading Plug Valve MV_101 | C2NC-1100-UNL-MV_101 | C2NC-1100-UNL | Valves | 4 inch VAC Tanker Truck Unloading Plug Valve 4 inch VAC Tanker Truck Unloading Plug Valve MV_101 | [34 empty] | Liquid Waste |  | 4 inch |  |  |  | Plug Valve
4 inch VAC Tanker Truck Unloading Plug Valve MV_102 | C2NC-1100-UNL-MV_102 | C2NC-1100-UNL | Valves | 4 inch VAC Tanker Truck Unloading Plug Valve 4 inch VAC Tanker Truck Unloading Plug Valve MV_102 | [34 empty] | Liquid Waste |  | 4 inch |  |  |  | Plug Valve
4 inch VAC Tanker Truck Unloading Plug Valve MV_103 | C2NC-1100-UNL-MV_103 | C2NC-1100-UNL | Valves | 4 inch VAC Tanker Truck Unloading Plug Valve 4 inch VAC Tanker Truck Unloading Plug Valve MV_103 | [34 empty] | Liquid Waste |  | 4 inch |  |  |  | Plug Valve
1 inch VAC Tanker Truck Unloading Ball Valve MV_104 | C2NC-1100-UNL-MV_104 | C2NC-1100-UNL | Valves | 1 inch VAC Tanker Truck Unloading Ball Valve 1 inch VAC Tanker Truck Unloading Ball Valve MV_104 | [34 empty] | Liquid Waste |  | 1 inch |  |  |  | Ball Valve
4 inch VAC Tanker Truck Unloading Check Valve CV_101 | C2NC-1100-UNL-CV_101 | C2NC-1100-UNL | Valves | 4 inch VAC Tanker Truck Unloading Check Valve 4 inch VAC Tanker Truck Unloading Check Valve CV_101 | [34 empty] | Liquid Waste |  | 4 inch |  |  |  | Check Valve
4 inch VAC Tanker Truck Unloading Check Valve CV_102 | C2NC-1100-UNL-CV_102 | C2NC-1100-UNL | Valves | 4 inch VAC Tanker Truck Unloading Check Valve 4 inch VAC Tanker Truck Unloading Check Valve CV_102 | [34 empty] | Liquid Waste |  | 4 inch |  |  |  | Check Valve
4 inch VAC Tanker Truck Unloading Check Valve CV_103 | C2NC-1100-UNL-CV_103 | C2NC-1100-UNL | Valves | 4 inch VAC Tanker Truck Unloading Check Valve 4 inch VAC Tanker Truck Unloading Check Valve CV_103 | [34 empty] | Liquid Waste |  | 4 inch |  |  |  | Check Valve
4 inch Receiving Pit Plug Valve MV_127 | C2NC-1100-UNL-MV_127 | C2NC-1100-UNL | Valves | 4 inch Receiving Pit Plug Valve 4 inch Receiving Pit Plug Valve MV_127 | [34 empty] | Villari Lagoon Water |  | 4 inch |  |  |  | Plug Valve
1.5 inch Receiving Pit Plug Valve MV_128 | C2NC-1100-UNL-MV_128 | C2NC-1100-UNL | Valves | 1.5 inch Receiving Pit Plug Valve 1.5 inch Receiving Pit Plug Valve MV_128 | [34 empty] | Villari Lagoon Water |  | 1.5 inch |  |  |  | Plug Valve
4 inch Receiving Pit Plug Valve MV_129 | C2NC-1100-UNL-MV_129 | C2NC-1100-UNL | Valves | 4 inch Receiving Pit Plug Valve 4 inch Receiving Pit Plug Valve MV_129 | [34 empty] | Villari Lagoon Water |  | 4 inch |  |  |  | Plug Valve
4 inch Receiving Pit Plug Valve MV_130 | C2NC-1100-UNL-MV_130 | C2NC-1100-UNL | Valves | 4 inch Receiving Pit Plug Valve 4 inch Receiving Pit Plug Valve MV_130 | [34 empty] | Villari Lagoon Water |  | 4 inch |  |  |  | Plug Valve
3 inch Receiving Pit Plug Valve MV_131 | C2NC-1100-UNL-MV_131 | C2NC-1100-UNL | Valves | 3 inch Receiving Pit Plug Valve 3 inch Receiving Pit Plug Valve MV_131 | [34 empty] | Villari Lagoon Water |  | 3 inch |  |  |  | Plug Valve
4 inch Receiving Pit Butterfly Valve MV_132 | C2NC-1100-UNL-MV_132 | C2NC-1100-UNL | Valves | 4 inch Receiving Pit Butterfly Valve 4 inch Receiving Pit Butterfly Valve MV_132 | [34 empty] | Villari Lagoon Water |  | 4 inch |  |  |  | Butterfly Valve
4 inch VAC Tanker Truck Unloading Plug Valve MV_105 | C2NC-1100-UNL-MV_105 | C2NC-1100-UNL | Valves | 4 inch VAC Tanker Truck Unloading Plug Valve 4 inch VAC Tanker Truck Unloading Plug Valve MV_105 | [34 empty] | Liquid Waste |  | 4 inch |  |  |  | Plug Valve
4 inch VAC Tanker Truck Unloading Plug Valve MV_106 | C2NC-1100-UNL-MV_106 | C2NC-1100-UNL | Valves | 4 inch VAC Tanker Truck Unloading Plug Valve 4 inch VAC Tanker Truck Unloading Plug Valve MV_106 | [34 empty] | Liquid Waste |  | 4 inch |  |  |  | Plug Valve
1 inch VAC Tanker Truck Unloading Ball Valve MV_107 | C2NC-1100-UNL-MV_107 | C2NC-1100-UNL | Valves | 1 inch VAC Tanker Truck Unloading Ball Valve 1 inch VAC Tanker Truck Unloading Ball Valve MV_107 | [34 empty] | Liquid Waste |  | 1 inch |  |  |  | Ball Valve
6 inch VAC Tanker Truck Unloading Plug Valve MV_108 | C2NC-1100-UNL-MV_108 | C2NC-1100-UNL | Valves | 6 inch VAC Tanker Truck Unloading Plug Valve 6 inch VAC Tanker Truck Unloading Plug Valve MV_108 | [34 empty] | Liquid Waste |  | 6 inch |  |  |  | Plug Valve
3 inch VAC Tanker Truck Unloading Plug Valve MV_109 | C2NC-1100-UNL-MV_109 | C2NC-1100-UNL | Valves | 3 inch VAC Tanker Truck Unloading Plug Valve 3 inch VAC Tanker Truck Unloading Plug Valve MV_109 | [34 empty] | Liquid Waste |  | 3 inch |  |  |  | Plug Valve
1.5 inch VAC Tanker Truck Unloading Plug Valve MV_110 | C2NC-1100-UNL-MV_110 | C2NC-1100-UNL | Valves | 1.5 inch VAC Tanker Truck Unloading Plug Valve 1.5 inch VAC Tanker Truck Unloading Plug Valve MV_110 | [34 empty] | Liquid Waste |  | 1.5 inch |  |  |  | Plug Valve
1.5 inch VAC Tanker Truck Unloading Plug Valve MV_111 | C2NC-1100-UNL-MV_111 | C2NC-1100-UNL | Valves | 1.5 inch VAC Tanker Truck Unloading Plug Valve 1.5 inch VAC Tanker Truck Unloading Plug Valve MV_111 | [34 empty] | Liquid Waste |  | 1.5 inch |  |  |  | Plug Valve
1.5 inch VAC Tanker Truck Unloading Ball Valve MV_112 | C2NC-1100-UNL-MV_112 | C2NC-1100-UNL | Valves | 1.5 inch VAC Tanker Truck Unloading Ball Valve 1.5 inch VAC Tanker Truck Unloading Ball Valve MV_112 | [34 empty] | Liquid Waste |  | 1.5 inch |  |  |  | Ball Valve
1 inch VAC Tanker Truck Unloading Ball Valve MV_113 | C2NC-1100-UNL-MV_113 | C2NC-1100-UNL | Valves | 1 inch VAC Tanker Truck Unloading Ball Valve 1 inch VAC Tanker Truck Unloading Ball Valve MV_113 | [34 empty] | Liquid Waste |  | 1 inch |  |  |  | Ball Valve
1 inch VAC Tanker Truck Unloading Ball Valve MV_114 | C2NC-1100-UNL-MV_114 | C2NC-1100-UNL | Valves | 1 inch VAC Tanker Truck Unloading Ball Valve 1 inch VAC Tanker Truck Unloading Ball Valve MV_114 | [34 empty] | Liquid Waste |  | 1 inch |  |  |  | Ball Valve
0.5 inch VAC Tanker Truck Unloading Ball Valve MV_115 | C2NC-1100-UNL-MV_115 | C2NC-1100-UNL | Valves | 0.5 inch VAC Tanker Truck Unloading Ball Valve 0.5 inch VAC Tanker Truck Unloading Ball Valve MV_115 | [34 empty] | Liquid Waste |  | 0.5 inch |  |  |  | Ball Valve
3 inch VAC Tanker Truck Unloading Plug Valve MV_116 | C2NC-1100-UNL-MV_116 | C2NC-1100-UNL | Valves | 3 inch VAC Tanker Truck Unloading Plug Valve 3 inch VAC Tanker Truck Unloading Plug Valve MV_116 | [34 empty] | Liquid Waste |  | 3 inch |  |  |  | Plug Valve
6 inch VAC Tanker Truck Unloading Plug Valve MV_117 | C2NC-1100-UNL-MV_117 | C2NC-1100-UNL | Valves | 6 inch VAC Tanker Truck Unloading Plug Valve 6 inch VAC Tanker Truck Unloading Plug Valve MV_117 | [34 empty] | Liquid Waste |  | 6 inch |  |  |  | Plug Valve
4 inch VAC Tanker Truck Unloading Plug Valve MV_118 | C2NC-1100-UNL-MV_118 | C2NC-1100-UNL | Valves | 4 inch VAC Tanker Truck Unloading Plug Valve 4 inch VAC Tanker Truck Unloading Plug Valve MV_118 | [34 empty] | Liquid Waste |  | 4 inch |  |  |  | Plug Valve
4 inch VAC Tanker Truck Unloading Plug Valve MV_119 | C2NC-1100-UNL-MV_119 | C2NC-1100-UNL | Valves | 4 inch VAC Tanker Truck Unloading Plug Valve 4 inch VAC Tanker Truck Unloading Plug Valve MV_119 | [34 empty] | Liquid Waste |  | 4 inch |  |  |  | Plug Valve
1 inch VAC Tanker Truck Unloading Ball Valve MV_120 | C2NC-1100-UNL-MV_120 | C2NC-1100-UNL | Valves | 1 inch VAC Tanker Truck Unloading Ball Valve 1 inch VAC Tanker Truck Unloading Ball Valve MV_120 | [34 empty] | Liquid Waste |  | 1 inch |  |  |  | Ball Valve
1.5 inch VAC Tanker Truck Unloading Plug Valve MV_121 | C2NC-1100-UNL-MV_121 | C2NC-1100-UNL | Valves | 1.5 inch VAC Tanker Truck Unloading Plug Valve 1.5 inch VAC Tanker Truck Unloading Plug Valve MV_121 | [34 empty] | Liquid Waste |  | 1.5 inch |  |  |  | Plug Valve
1.5 inch VAC Tanker Truck Unloading Plug Valve MV_122 | C2NC-1100-UNL-MV_122 | C2NC-1100-UNL | Valves | 1.5 inch VAC Tanker Truck Unloading Plug Valve 1.5 inch VAC Tanker Truck Unloading Plug Valve MV_122 | [34 empty] | Liquid Waste |  | 1.5 inch |  |  |  | Plug Valve
1 inch Receiving Pit Service Water Ball Valve MV_134 | C2NC-1100-UNL-MV_134 | C2NC-1100-UNL | Valves | 1 inch Receiving Pit Service Water Ball Valve 1 inch Receiving Pit Service Water Ball Valve MV_134 | [34 empty] | Service Water |  | 1 inch |  |  |  | Ball Valve
4 inch Receiving Pit Service Water Butterfly Valve MV_135 | C2NC-1100-UNL-MV_135 | C2NC-1100-UNL | Valves | 4 inch Receiving Pit Service Water Butterfly Valve 4 inch Receiving Pit Service Water Butterfly Valve MV_135 | [34 empty] | Service Water |  | 4 inch |  |  |  | Butterfly Valve
4 inch Receiving Pit Service Water Gate Valve MV_136 | C2NC-1100-UNL-MV_136 | C2NC-1100-UNL | Valves | 4 inch Receiving Pit Service Water Gate Valve 4 inch Receiving Pit Service Water Gate Valve MV_136 | [34 empty] | Service Water |  | 4 inch |  |  |  | Gate Valve
3 inch Receiving Pit Service Water Gate Valve MV_137 | C2NC-1100-UNL-MV_137 | C2NC-1100-UNL | Valves | 3 inch Receiving Pit Service Water Gate Valve 3 inch Receiving Pit Service Water Gate Valve MV_137 | [34 empty] | Service Water |  | 3 inch |  |  |  | Gate Valve
4 inch Receiving Pit Service Water Butterfly Valve MV_138 | C2NC-1100-UNL-MV_138 | C2NC-1100-UNL | Valves | 4 inch Receiving Pit Service Water Butterfly Valve 4 inch Receiving Pit Service Water Butterfly Valve MV_138 | [34 empty] | Service Water |  | 4 inch |  |  |  | Butterfly Valve
2 inch Receiving Pit Service Water Ball Valve MV_139 | C2NC-1100-UNL-MV_139 | C2NC-1100-UNL | Valves | 2 inch Receiving Pit Service Water Ball Valve 2 inch Receiving Pit Service Water Ball Valve MV_139 | [34 empty] | Service Water |  | 2 inch |  |  |  | Ball Valve
2 inch Receiving Pit Service Water Check Valve CV_104 | C2NC-1100-UNL-CV_104 | C2NC-1100-UNL | Valves | 2 inch Receiving Pit Service Water Check Valve 2 inch Receiving Pit Service Water Check Valve CV_104 | [34 empty] | Service Water |  | 2 inch |  |  |  | Check Valve
Receiving Pit Service Water Check Valve CV_105 | C2NC-1100-UNL-CV_105 | C2NC-1100-UNL | Valves | Receiving Pit Service Water Check Valve Receiving Pit Service Water Check Valve CV_105 | [34 empty] | Service Water | [5 empty] | Check Valve
1 inch Receiving Pit Service Water Ball Valve MV_146 | C2NC-1100-UNL-MV_146 | C2NC-1100-UNL | Valves | 1 inch Receiving Pit Service Water Ball Valve 1 inch Receiving Pit Service Water Ball Valve MV_146 | [34 empty] | Service Water |  | 1 inch |  |  |  | Ball Valve
2 inch Receiving Pit Service Water Isolation Ball Valve MV_140 | C2NC-1100-UNL-MV_140 | C2NC-1100-UNL | Valves | 2 inch Receiving Pit Service Water Isolation Ball Valve 2 inch Receiving Pit Service Water Isolation Ball Valve MV_140 | [34 empty] | Service Water |  | 2 inch |  |  |  | Ball Valve
2 inch Receiving Pit Service Water Isolation Ball Valve MV_141 | C2NC-1100-UNL-MV_141 | C2NC-1100-UNL | Valves | 2 inch Receiving Pit Service Water Isolation Ball Valve 2 inch Receiving Pit Service Water Isolation Ball Valve MV_141 | [34 empty] | Service Water |  | 2 inch |  |  |  | Ball Valve
2 inch Receiving Pit Service Water Isolation Ball Valve MV_142 | C2NC-1100-UNL-MV_142 | C2NC-1100-UNL | Valves | 2 inch Receiving Pit Service Water Isolation Ball Valve 2 inch Receiving Pit Service Water Isolation Ball Valve MV_142 | [34 empty] | Service Water |  | 2 inch |  |  |  | Ball Valve
2 inch Pump and Grinder Pad Service Water Ball Valve MV_143 | C2NC-1100-UNL-MV_143 | C2NC-1100-UNL | Valves | 2 inch Pump and Grinder Pad Service Water Ball Valve 2 inch Pump and Grinder Pad Service Water Ball Valve MV_143 | [34 empty] | Service Water |  | 2 inch |  |  |  | Ball Valve
1 inch Truck Unloading Washdown Hoses Ball Valve MV_144 | C2NC-1100-UNL-MV_144 | C2NC-1100-UNL | Valves | 1 inch Truck Unloading Washdown Hoses Ball Valve 1 inch Truck Unloading Washdown Hoses Ball Valve MV_144 | [34 empty] | Service Water |  | 1 inch |  |  |  | Ball Valve
1 inch Truck Unloading Washdown Hoses Ball Valve MV_145 | C2NC-1100-UNL-MV_145 | C2NC-1100-UNL | Valves | 1 inch Truck Unloading Washdown Hoses Ball Valve 1 inch Truck Unloading Washdown Hoses Ball Valve MV_145 | [34 empty] | Service Water |  | 1 inch |  |  |  | Ball Valve
1 inch Truck Unloading Washdown Hoses Ball Valve MV_146 | C2NC-1100-UNL-MV_146 | C2NC-1100-UNL | Valves | 1 inch Truck Unloading Washdown Hoses Ball Valve 1 inch Truck Unloading Washdown Hoses Ball Valve MV_146 | [34 empty] | Service Water |  | 1 inch |  |  |  | Ball Valve
1 inch Truck Unloading Washdown Hoses Ball Valve MV_147 | C2NC-1100-UNL-MV_147 | C2NC-1100-UNL | Valves | 1 inch Truck Unloading Washdown Hoses Ball Valve 1 inch Truck Unloading Washdown Hoses Ball Valve MV_147 | [34 empty] | Service Water |  | 1 inch |  |  |  | Ball Valve
1 inch Truck Unloading Washdown Hoses Ball Valve MV_148 | C2NC-1100-UNL-MV_148 | C2NC-1100-UNL | Valves | 1 inch Truck Unloading Washdown Hoses Ball Valve 1 inch Truck Unloading Washdown Hoses Ball Valve MV_148 | [34 empty] | Service Water |  | 1 inch |  |  |  | Ball Valve
10 inch Feedstock Grinder Transfer ? MV_149 | C2NC-1100-SLR-MV_149 | C2NC-1100-SLR | Valves | 10 inch Feedstock Grinder Transfer ? 10 inch Feedstock Grinder Transfer ? MV_149 | [34 empty] | Service Water |  | 10 inch |  |  |  | ?
1.5 inch Feedstock Grinder Transfer Plug Valve MV_150 | C2NC-1100-SLR-MV_150 | C2NC-1100-SLR | Valves | 1.5 inch Feedstock Grinder Transfer Plug Valve 1.5 inch Feedstock Grinder Transfer Plug Valve MV_150 | [34 empty] | Service Water |  | 1.5 inch |  |  |  | Plug Valve
1.5 inch Feedstock Grinder Transfer Plug Valve MV_151 | C2NC-1100-SLR-MV_151 | C2NC-1100-SLR | Valves | 1.5 inch Feedstock Grinder Transfer Plug Valve 1.5 inch Feedstock Grinder Transfer Plug Valve MV_151 | [34 empty] | Service Water |  | 1.5 inch |  |  |  | Plug Valve
1.5 inch Feedstock Grinder Transfer Ball Valve MV_152 | C2NC-1100-SLR-MV_152 | C2NC-1100-SLR | Valves | 1.5 inch Feedstock Grinder Transfer Ball Valve 1.5 inch Feedstock Grinder Transfer Ball Valve MV_152 | [34 empty] | Service Water |  | 1.5 inch |  |  |  | Ball Valve
1 inch Feedstock Grinder Transfer Ball Valve MV_153 | C2NC-1100-SLR-MV_153 | C2NC-1100-SLR | Valves | 1 inch Feedstock Grinder Transfer Ball Valve 1 inch Feedstock Grinder Transfer Ball Valve MV_153 | [34 empty] | Service Water |  | 1 inch |  |  |  | Ball Valve
1 inch Feedstock Grinder Transfer Ball Valve MV_154 | C2NC-1100-SLR-MV_154 | C2NC-1100-SLR | Valves | 1 inch Feedstock Grinder Transfer Ball Valve 1 inch Feedstock Grinder Transfer Ball Valve MV_154 | [34 empty] | Service Water |  | 1 inch |  |  |  | Ball Valve
0.5 inch Feedstock Grinder Transfer Ball Valve MV_155 | C2NC-1100-SLR-MV_155 | C2NC-1100-SLR | Valves | 0.5 inch Feedstock Grinder Transfer Ball Valve 0.5 inch Feedstock Grinder Transfer Ball Valve MV_155 | [34 empty] | Service Water |  | 0.5 inch |  |  |  | Ball Valve
10 inch Feedstock Grinder Transfer ? MV_156 | C2NC-1100-SLR-MV_156 | C2NC-1100-SLR | Valves | 10 inch Feedstock Grinder Transfer ? 10 inch Feedstock Grinder Transfer ? MV_156 | [34 empty] | Service Water |  | 10 inch |  |  |  | ?
10 inch Feedstock Grinder Transfer ? MV_157 | C2NC-1100-UNL-FIQ-101 | C2NC-1100-UNL | Instruments | 10 inch Feedstock Grinder Transfer ? MV_157 | [55 empty] | Villari Lagoon Water
1.5 inch Feedstock Grinder Transfer Plug Valve MV_158 | C2NC-1100-UNL-FIT-101 | C2NC-1100-UNL | Instruments | 1.5 inch Feedstock Grinder Transfer Plug Valve MV_158 | [55 empty] | Villari Lagoon Water
1.5 inch Feedstock Grinder Transfer Plug Valve MV_159 | C2NC-1100-UNL-FE-101 | C2NC-1100-UNL | Instruments | 1.5 inch Feedstock Grinder Transfer Plug Valve MV_159 | [55 empty] | Villari Lagoon Water
1.5 inch Feedstock Grinder Transfer Ball Valve MV_160 | C2NC-1100-UNL-YA-103 | C2NC-1100-UNL | Instruments | 1.5 inch Feedstock Grinder Transfer Ball Valve MV_160 | [55 empty] | Villari Lagoon Water
1 inch Feedstock Grinder Transfer Ball Valve MV_161 | C2NC-1100-UNL-FE-102 | C2NC-1100-UNL | Instruments | 1 inch Feedstock Grinder Transfer Ball Valve MV_161 | [55 empty] | Service Water
1 inch Feedstock Grinder Transfer Ball Valve MV_162 | C2NC-1100-UNL-FIT-102 | C2NC-1100-UNL | Instruments | 1 inch Feedstock Grinder Transfer Ball Valve MV_162 | [55 empty] | Service Water
0.5 inch Feedstock Grinder Transfer Ball Valve MV_163 | C2NC-1100-UNL-FIQ-102 | C2NC-1100-UNL | Instruments | 0.5 inch Feedstock Grinder Transfer Ball Valve MV_163 | [55 empty] | Service Water
8 inch Feedstock Grinder Transfer ? MV_164 | C2NC-1100-UNL-HS-114 | C2NC-1100-UNL | Instruments | 8 inch Feedstock Grinder Transfer ? MV_164 | [55 empty] | Liquid Waste
3 inch Feedstock Grinder Transfer Plug Valve MV_165 | C2NC-1100-UNL-HS-104 | C2NC-1100-UNL | Instruments | 3 inch Feedstock Grinder Transfer Plug Valve MV_165 | [55 empty] | Liquid Waste
10 inch Feedstock Grinder Transfer ? MV_166 | C2NC-1100-UNL-HS-113 | C2NC-1100-UNL | Instruments | 10 inch Feedstock Grinder Transfer ? MV_166 | [55 empty] | Liquid Waste
2 inch Feedstock Grinder Transfer Ball Valve MV_167 | C2NC-1100-UNL-HS-103 | C2NC-1100-UNL | Instruments | 2 inch Feedstock Grinder Transfer Ball Valve MV_167 | [55 empty] | Liquid Waste
8 inch Feedstock Grinder Transfer ? MV_168 | C2NC-1100-UNL-HS-112 | C2NC-1100-UNL | Instruments | 8 inch Feedstock Grinder Transfer ? MV_168 | [55 empty] | Liquid Waste
2 inch Feedstock Grinder Transfer Ball Valve MV_169 | C2NC-1100-UNL-TAH-102 | C2NC-1100-UNL | Instruments | 2 inch Feedstock Grinder Transfer Ball Valve MV_169 | [55 empty] | Liquid Waste
4 inch Villari Lagoon Transfer Check Valve CV_106 | C2NC-1100-UNL-HS-102 | C2NC-1100-UNL | Instruments | 4 inch Villari Lagoon Transfer Check Valve CV_106 | [55 empty] | Liquid Waste
1 inch Villari Lagoon Transfer Ball Valve MV_170 | C2NC-1100-UNL-SIC-102 | C2NC-1100-UNL | Instruments | 1 inch Villari Lagoon Transfer Ball Valve MV_170 | [55 empty] | Liquid Waste
1.5 inch Villari Lagoon Transfer Plug Valve MV_171 | C2NC-1100-UNL-PR_102 | C2NC-1100-UNL | Equipment | 1.5 inch Villari Lagoon Transfer Plug Valve MV_171 | Vogelsang | VX186-260 | [14 empty] | 20hp | Liquid Waste | CAST IRON, GALVANIZED STEEL, NBR |  |  | Rotary Lobe Pump
4 inch Villari Lagoon Transfer Plug Valve MV_172 | C2NC-1100-UNL-PR_105 | C2NC-1100-UNL | Equipment | 4 inch Villari Lagoon Transfer Plug Valve MV_172 | Vogelsang | VX186-260 | [14 empty] | 20hp | Liquid Waste | CAST IRON, GALVANIZED STEEL, NBR |  |  | Rotary Lobe Pump
AR_101 | C2NC-1100-UNL-AR_101 | C2NC-1100-UNL | Equipment | Receiving Pit Mixer 1 | Suma | Optimix 2G 150-325 | [14 empty] | 20hp | Liquid Waste | DUCTILE IRON, 304 SS |  |  | Submersible Mixer
AR_102 | C2NC-1100-UNL-AR_102 | C2NC-1100-UNL | Equipment | Receiving Pit Mixer 2 | Suma | Optimix 2G 150-325 | [14 empty] | 20hp | Liquid Waste | DUCTILE IRON, 304 SS |  |  | Submersible Mixer
TE-102 | C2NC-1100-UNL-TE-102 | C2NC-1100-UNL | Instruments | [56 empty] | Liquid Waste
MV_157 | C2NC-1100-SLR-MV_157 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 10 inch |  |  |  | ?
MV_158 | C2NC-1100-SLR-MV_158 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 1.5 inch |  |  |  | Plug Valve
MV_159 | C2NC-1100-SLR-MV_159 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 1.5 inch |  |  |  | Plug Valve
MV_160 | C2NC-1100-SLR-MV_160 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 1.5 inch |  |  |  | Ball Valve
MV_161 | C2NC-1100-SLR-MV_161 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 1 inch |  |  |  | Ball Valve
MV_162 | C2NC-1100-SLR-MV_162 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 1 inch |  |  |  | Ball Valve
MV_163 | C2NC-1100-SLR-MV_163 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 0.5 inch |  |  |  | Ball Valve
MV_164 | C2NC-1100-SLR-MV_164 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 8 inch |  |  |  | ?
MV_165 | C2NC-1100-SLR-MV_165 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 3 inch |  |  |  | Plug Valve
MV_166 | C2NC-1100-SLR-MV_166 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 10 inch |  |  |  | ?
MV_167 | C2NC-1100-SLR-MV_167 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 2 inch |  |  |  | Ball Valve
MV_168 | C2NC-1100-SLR-MV_168 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 8 inch |  |  |  | ?
MV_169 | C2NC-1100-SLR-MV_169 | C2NC-1100-SLR | Valves | Feedstock Grinder Transfer | [34 empty] | Feedstock Slurry |  | 2 inch |  |  |  | Ball Valve
HS_106 | C2NC-1100-SLR-HS_106 | C2NC-1100-SLR | Instruments
HS_116 | C2NC-1100-SLR-HS_116 | C2NC-1100-SLR | Instruments
HS_126 | C2NC-1100-SLR-HS_126 | C2NC-1100-SLR | Instruments
TAH_104 | C2NC-1100-SLR-TAH_104 | C2NC-1100-SLR | Instruments
TE_104 | C2NC-1100-SLR-TE_104 | C2NC-1100-SLR | Instruments
PI_104 | C2NC-1100-SLR-PI_104 | C2NC-1100-SLR | Instruments
PT_104 | C2NC-1100-SLR-PT_104 | C2NC-1100-SLR | Instruments
PAH_104 | C2NC-1100-SLR-PAH_104 | C2NC-1100-SLR | Instruments
HS_107 | C2NC-1100-SLR-HS_107 | C2NC-1100-SLR | Instruments
HS_117 | C2NC-1100-SLR-HS_117 | C2NC-1100-SLR | Instruments
HS_127 | C2NC-1100-SLR-HS_127 | C2NC-1100-SLR | Instruments
YA_101 | C2NC-1100-SLR-YA_101 | C2NC-1100-SLR | Instruments
YA_102 | C2NC-1100-SLR-YA_102 | C2NC-1100-SLR | Instruments
HS_105 | C2NC-1100-SLR-HS_105 | C2NC-1100-SLR | Instruments
HS_115 | C2NC-1100-SLR-HS_115 | C2NC-1100-SLR | Instruments
HS_125 | C2NC-1100-SLR-HS_125 | C2NC-1100-SLR | Instruments
TAH_103 | C2NC-1100-SLR-TAH_103 | C2NC-1100-SLR | Instruments
TE_103 | C2NC-1100-SLR-TE_103 | C2NC-1100-SLR | Instruments
PI_103 | C2NC-1100-SLR-PI_103 | C2NC-1100-SLR | Instruments
PT_103 | C2NC-1100-SLR-PT_103 | C2NC-1100-SLR | Instruments
PAH_103 | C2NC-1100-SLR-PAH_103 | C2NC-1100-SLR | Instruments
QR_100 | C2NC-1100-SLR-QR_100 | C2NC-1100-SLR | Equipment | Feedstock Grinder | JWCE | 4-HYDRO-I-2412 | [14 empty] | 15hp | Feedstock Slurry | Ductile Iron, Alloy Steel, BUNA-N |  |  | In-Line Grinder
PR_103 | C2NC-1100-SLR-PR_103 | C2NC-1100-SLR | Equipment | Feedstock Slurry Pump | VOGELSANG | VX186-260H4QD | [14 empty] | 60hp | Feedstock Slurry | Cast Iron, Coated Special Steel |  |  | Rotary Lobe Pump
PR_104 | C2NC-1100-SLR-PR_104 | C2NC-1100-SLR | Equipment | Feedstock Slurry Pump | VOGELSANG | VX186-260H4QD | [14 empty] | 60hp | Feedstock Slurry | Cast Iron, Coated Special Steel |  |  | Rotary Lobe Pump
PR_101 | C2NC-1100-VLR-PR_101 | C2NC-1100-VLR | Equipment | Villari Transfer Pump | Gorman-Rupp | GORMAN-RUPP T3A60S-B/F | [14 empty] | 20hp | Villari Lagoon Water | Cast Iron |  |  | Self-Priming Centrifugal Pump
CV_106 | C2NC-1100-VLR-CV_106 | C2NC-1100-VLR | Valves | Villari Lagoon Transfer | [34 empty] | Villari Lagoon Water |  | 4 inch |  |  |  | Check Valve
MV_170 | C2NC-1100-VLR-MV_170 | C2NC-1100-VLR | Valves | Villari Lagoon Transfer | [34 empty] | Villari Lagoon Water |  | 1 inch |  |  |  | Ball Valve
MV_171 | C2NC-1100-VLR-MV_171 | C2NC-1100-VLR | Valves | Villari Lagoon Transfer | [34 empty] | Villari Lagoon Water |  | 1.5 inch |  |  |  | Plug Valve
MV_172 | C2NC-1100-VLR-MV_172 | C2NC-1100-VLR | Valves | Villari Lagoon Transfer | [34 empty] | Villari Lagoon Water |  | 4 inch |  |  |  | Plug Valve
HS_108 | C2NC-1100-VLR-HS_108 | C2NC-1100-VLR | Instruments
HS_118 | C2NC-1100-VLR-HS_118 | C2NC-1100-VLR | Instruments
HS_128 | C2NC-1100-VLR-HS_128 | C2NC-1100-VLR | Instruments
PI_105 | C2NC-1100-VLR-PI_105 | C2NC-1100-VLR | Instruments
8"-AC30-FF-1100-07 | C2NC-1100-UNL-8"-AC30-FF-1100-07 | C2NC-1100-UNL | Lines | 8 inch Feedstock Slurry to Receiving Pit Line | [23 empty] | Feedstock Slurry |  | 8 inch | Feedstock Slurry | Receiving Pit
4"-AC30-WS-1100-09 | C2NC-1100-UNL-4"-AC30-WS-1100-09 | C2NC-1100-UNL | Lines | 4 inch Service Water to Receiving Pit Line | [23 empty] | Service Water |  | 4 inch | Service Water | Receiving Pit
6"-AC30-FL-1100-01 | C2NC-1100-UNL-6"-AC30-FL-1100-01 | C2NC-1100-UNL | Lines | 6 inch Tanker Unloading to Receiving Pit 1 Line | [23 empty] | Liquid Waste |  | 6 inch | Tanker Unloading | Receiving Pit
4"-AE30-FL-1100-08 | C2NC-1100-UNL-4"-AE30-FL-1100-08 | C2NC-1100-UNL | Lines | 4 inch Villari Lagoon Water to Receiving Pit Line | [23 empty] | Villari Lagoon Water |  | 4 inch | Villari Lagoon Water | Receiving Pit
6"-AC30-FL-1100-02 | C2NC-1100-UNL-6"-AC30-FL-1100-02 | C2NC-1100-UNL | Lines | 6 inch Tanker Unloading to Receiving Pit 2 Line | [23 empty] | ? |  | 6 inch | Tanker Unloading | Receiving Pit
6"-AC30-FL-1100-03 | C2NC-1100-UNL-6"-AC30-FL-1100-03 | C2NC-1100-UNL | Lines | 6 inch Tanker Unloading to Receiving Pit 3 Line | [23 empty] | Liquid Waste |  | 6 inch | Tanker Unloading | Receiving Pit
10"-AC30-FF-1100-05 | C2NC-1100-UNL-10"-AC30-FF-1100-05 | C2NC-1100-UNL | Lines | 10 inch Receiving Pit to Feedstock Slurry Line | [23 empty] | Feedstock Slurry |  | 10 inch | Receiving Pit | Feedstock Slurry
10"-AC30-FF-1100-04 | C2NC-1100-UNL-10"-AC30-FF-1100-04 | C2NC-1100-UNL | Lines | 10 inch Receiving Pit to Feedstock Slurry Line | [23 empty] | Feedstock Slurry |  | 10 inch | Receiving Pit | Feedstock Slurry
10"-AC30-FF-1100-12 | C2NC-1100-UNL-10"-AC30-FF-1100-12 | C2NC-1100-UNL | Lines | 10 inch Service Water to Receiving Pit Line | [23 empty] | Feedstock Slurry |  | 10 inch | Service Water | Receiving Pit
2"-AC30-WS-1100-10 | C2NC-1100-UNL-2"-AC30-WS-1100-10 | C2NC-1100-UNL | Lines | 2 inch Service Water to Receiving Pit Line | [23 empty] | Service Water |  | 2 inch | Service Water | Receiving Pit
1"-AC30-WS-1100-11 | C2NC-1100-UNL-1"-AC30-WS-1100-11 | C2NC-1100-UNL | Lines | 1 inch Service Water to Receiving Pit Line | [23 empty] | Service Water |  | 1 inch | Service Water | Receiving Pit
10"-AC30-FF-1100-06 | C2NC-1100-SLR-10"-AC30-FF-1100-06 | C2NC-1100-SLR | Lines | 10 inch Receiving Pit to Feedstock Slurry Line | [23 empty] | Feedstock Slurry |  | 10 inch | Receiving Pit | Feedstock Slurry
4"-PV91-FL-1100-08 | C2NC-1100-VLR-4"-PV91-FL-1100-08 | C2NC-1100-VLR | Lines | 4 inch Villari Lagoon Water to Receiving Pit Line | [23 empty] | Villari Lagoon Water |  | 4 inch | Villari Lagoon Water | Receiving Pit
1"-PV91-AV-1100-13 | C2NC-1100-VLR-1"-PV91-AV-1100-13 | C2NC-1100-VLR | Lines | 1 inch Villari Lagoon Water Air Release Line | [23 empty] | Villari Lagoon Water |  | 1 inch | Villari Lagoon Water | Receiving Pit
10 Inch PVC Diluted Feedstock Line 08 | CNC2-1100-10_AC30_FF_1100_08 | C2NC-1100 | Lines | 10 Inch PVC Diluted Feedstock Line | [11 empty] | D0-1 | 10_AC30_FF_1100_08 | [10 empty] | Diluted Feedstock | PVC | 10 inch |  |  | N

## 1200 - FCon
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual RQD | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Connection Type | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | *Any Custom Fields* | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes
FCON - Instrument - Isolation - 04 | C2NC-1200-050-FCV_31204 | C2NC-1200-050 | Valves | Instrument Isolation Solenoid Valve | [7 empty] | Y |  |  |  | D-01 | FCV_31204 | [21 empty] | DFS |  | 1 |  |  | Automatic | Solenoid
FCON - Heating - 3-way - Hot - Water - 01A | C2NC-1200-HTG-EV_44201A | C2NC-1200-HTG | Valves | 3-way Hot Water 3 Way Valve | [7 empty] | Y |  |  |  | D-02 | EV_44201A | [21 empty] | HW |  | 6 |  |  | Automatic | 3 Way
FCON - Antifoam - 01 | C2NC-1200-AF-HV_21101 | C2NC-1200-AF | Valves | Antifoam Ball Valve | [11 empty] | D-01 | HV_21101 | [21 empty] | ADA |  | 1 |  |  | Manual | Ball
FCON - Antifoam - 21 | C2NC-1200-AF-HV_21121 | C2NC-1200-AF | Valves | Antifoam Ball Valve | [11 empty] | D-01 | HV_21121 | [21 empty] | DFS |  | 0.5 |  |  | Manual | Ball
FCON - Antifoam - 22 | C2NC-1200-AF-HV_21122 | C2NC-1200-AF | Valves | Antifoam Ball Valve | [11 empty] | D-01 | HV_21122 | [21 empty] | DFS |  | 0.5 |  |  | Manual | Ball
FCON - Antifoam - 23 | C2NC-1200-AF-HV_21123 | C2NC-1200-AF | Valves | Antifoam Ball Valve | [11 empty] | D-01 | HV_21123 | [21 empty] | DFS |  | 0.5 |  |  | Manual | Ball
FCON Immediate Area | C2NC-1200-050 | C2NC-1200 | Locations And Facilities | Fcon Tank Immediate Area
FCON - Heating - 3-way - Hot - Water - 01B | C2NC-1200-HTG-EV_44201B | C2NC-1200-HTG | Valves | 3-way Hot Water 3 Way Valve | [7 empty] | Y |  |  |  | D-02 | EV_44201B | [21 empty] | HW |  | 6 |  |  | Automatic | 3 Way
FCON - Feed - 02 | C2NC-1200-FD-HV_21102 | C2NC-1200-FD | Valves | FCON Feed Knife Gate Valve | [11 empty] | D-01 | HV_21102 | [21 empty] | DFS |  | 10 |  |  | Manual | Knife Gate
FCON - Heating - Nutrient - Dosing - 03A | C2NC-1200-HTG-CV_31103A | C2NC-1200-HTG | Valves | Nutrient Dosing Check Valve | [11 empty] | D-02 | CV_31103A | [21 empty] | ADA |  | 1 |  |  | Manual | Check
FCON - Heating - Nutrient - Dosing - 03B | C2NC-1200-HTG-CV_31103B | C2NC-1200-HTG | Valves | Nutrient Dosing Check Valve | [11 empty] | D-02 | CV_31103B | [21 empty] | ADA |  | 1 |  |  | Manual | Check
FCON - Heating - Nutrient - Isolation - 03A | C2NC-1200-HTG-HV_31103A | C2NC-1200-HTG | Valves | Nutrient Isolation Ball Valve | [11 empty] | D-02 | HV_31103A | [21 empty] | ADA |  | 1 |  |  | Manual | Ball
FCON - Heating - Nutrient - Isolation - 03B | C2NC-1200-HTG-HV_31103B | C2NC-1200-HTG | Valves | Nutrient Isolation Ball Valve | [11 empty] | D-02 | HV_31103B | [21 empty] | ADA |  | 1 |  |  | Manual | Ball
FCON - Heating - HX - Pump - 1 - 01A | C2NC-1200-HTG-HV_44201A | C2NC-1200-HTG | Valves | FCON HX Pump 1 Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-02 | HV_44201A | [21 empty] | DFS | CF8M | 10 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Heating - HX - Pump - 2 - 01B | C2NC-1200-HTG-HV_44201B | C2NC-1200-HTG | Valves | FCON HX Pump 2 Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-02 | HV_44201B | [21 empty] | DFS | CF8M | 10 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Heating - Drain - Valve - 02A | C2NC-1200-HTG-HV_44202A | C2NC-1200-HTG | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-02 | HV_44202A | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
FCON - Heating - Drain - Valve - 02B | C2NC-1200-HTG-HV_44202B | C2NC-1200-HTG | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-02 | HV_44202B | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
FCON - Heating - HW - Pump - 3 - 05A | C2NC-1200-HTG-HV_44205A | C2NC-1200-HTG | Valves | HW Pump 3 Butterfly Valve | [11 empty] | D-02 | HV_44205A | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
FCON - Heating - HW - Pump - 4 - 05B | C2NC-1200-HTG-HV_44205B | C2NC-1200-HTG | Valves | HW Pump 4 Butterfly Valve | [11 empty] | D-02 | HV_44205B | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
FCON - Heating - Drain - Valve - 06A | C2NC-1200-HTG-HV_44206A | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44206A | [21 empty] | HW |  |  |  |  | Manual | Ball
FCON - Heating - Drain - Valve - 06B | C2NC-1200-HTG-HV_44206B | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44206B | [21 empty] | HW |  |  |  |  | Manual | Ball
FCON - Heating - Drain - Valve - 11A | C2NC-1200-HTG-HV_44211A | C2NC-1200-HTG | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-02 | HV_44211A | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
FCON - Heating - Drain - Valve - 11B | C2NC-1200-HTG-HV_44211B | C2NC-1200-HTG | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-02 | HV_44211B | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
FCON - Heating - Drain - Valve - 12A | C2NC-1200-HTG-HV_44212A | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44212A | [21 empty] | DFS |  | 1 |  |  | Manual | Ball
FCON - Heating - Drain - Valve - 12B | C2NC-1200-HTG-HV_44212B | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44212B | [21 empty] | DFS |  | 1 |  |  | Manual | Ball
FCON - Heating - HX - isolation - 13A | C2NC-1200-HTG-HV_44213A | C2NC-1200-HTG | Valves | HX isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-02 | HV_44213A | [21 empty] | DFS | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Heating - HX - isolation - 13B | C2NC-1200-HTG-HV_44213B | C2NC-1200-HTG | Valves | HX isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-02 | HV_44213B | [21 empty] | DFS | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Heating - Boiler - Return - Isolation - 15A | C2NC-1200-HTG-HV_44215A | C2NC-1200-HTG | Valves | Boiler Return Isolation Butterfly Valve | [11 empty] | D-02 | HV_44215A | [21 empty] | HW |  |  |  |  | Manual | Butterfly
FCON - Heating - Boiler - Return - Isolation - 15B | C2NC-1200-HTG-HV_44215B | C2NC-1200-HTG | Valves | Boiler Return Isolation Butterfly Valve | [11 empty] | D-02 | HV_44215B | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
FCON - Heating - HX - isolation - 16A | C2NC-1200-HTG-HV_44216A | C2NC-1200-HTG | Valves | HX isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-02 | HV_44216A | [21 empty] | DFS | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Heating - HX - isolation - 16B | C2NC-1200-HTG-HV_44216B | C2NC-1200-HTG | Valves | HX isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-02 | HV_44216B | [21 empty] | DFS | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Heating - HX - isolation - 17A | C2NC-1200-HTG-HV_44217A | C2NC-1200-HTG | Valves | HX isolation Butterfly Valve | [11 empty] | D-02 | HV_44217A | [21 empty] | DFS |  | 4 |  |  | Manual | Butterfly
FCON - Heating - HX - isolation - 17B | C2NC-1200-HTG-HV_44217B | C2NC-1200-HTG | Valves | HX isolation Butterfly Valve | [11 empty] | D-02 | HV_44217B | [21 empty] | DFS |  | 4 |  |  | Manual | Butterfly
FCON - Heating - HX - isolation - 18A | C2NC-1200-HTG-HV_44218A | C2NC-1200-HTG | Valves | HX isolation Butterfly Valve | [11 empty] | D-02 | HV_44218A | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
FCON - Heating - HX - isolation - 18B | C2NC-1200-HTG-HV_44218B | C2NC-1200-HTG | Valves | HX isolation Butterfly Valve | [11 empty] | D-02 | HV_44218B | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
FCON - Heating - Drain - Valve - 19A | C2NC-1200-HTG-HV_44219A | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44219A | [21 empty] | HW |  | 1 |  |  | Manual | Ball
FCON - Heating - Drain - Valve - 19B | C2NC-1200-HTG-HV_44219B | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44219B | [21 empty] | HW |  | 1 |  |  | Manual | Ball
FCON - Heating - HX - isolation - 20A | C2NC-1200-HTG-HV_44220A | C2NC-1200-HTG | Valves | HX isolation Butterfly Valve | [11 empty] | D-02 | HV_44220A | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
FCON - Heating - HX - isolation - 20B | C2NC-1200-HTG-HV_44220B | C2NC-1200-HTG | Valves | HX isolation Butterfly Valve | [11 empty] | D-02 | HV_44220B | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
FCON - Heating - Drain - Valve - 21A | C2NC-1200-HTG-HV_44221A | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44221A | [21 empty] | HW |  | 1 |  |  | Manual | Ball
FCON - Heating - Drain - Valve - 21B | C2NC-1200-HTG-HV_44221B | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44221B | [21 empty] | HW |  | 1 |  |  | Manual | Ball
FCON - Heating - Drain - Valve - 22A | C2NC-1200-HTG-HV_44222A | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44222A | [21 empty] | HW |  |  |  |  | Manual | Ball
FCON - Heating - Drain - Valve - 22B | C2NC-1200-HTG-HV_44222B | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44222B | [21 empty] | HW |  |  |  |  | Manual | Ball
FCON - Heating - Drain - Valve - 23A | C2NC-1200-HTG-HV_44223A | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44223A | [21 empty] | DFS |  |  |  |  | Manual | Ball
FCON - Heating - Drain - Valve - 23B | C2NC-1200-HTG-HV_44223B | C2NC-1200-HTG | Valves | Drain Valve Ball Valve | [11 empty] | D-02 | HV_44223B | [21 empty] | DFS |  |  |  |  | Manual | Ball
FCON - Heating - Instrument - Isolation - 24A | C2NC-1200-HTG-HV_44224A | C2NC-1200-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-02 | HV_44224A | [21 empty] | DFS |  |  |  |  | Manual | Ball
FCON - Heating - Instrument - Isolation - 24B | C2NC-1200-HTG-HV_44224B | C2NC-1200-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-02 | HV_44224B | [21 empty] | DFS |  |  |  |  | Manual | Ball
FCON - Heating - Instrument - Isolation - 25A | C2NC-1200-HTG-HV_44225A | C2NC-1200-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-02 | HV_44225A | [21 empty] | HW |  |  |  |  | Manual | Ball
FCON - Heating - Instrument - Isolation - 25B | C2NC-1200-HTG-HV_44225B | C2NC-1200-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-02 | HV_44225B | [21 empty] | HW |  |  |  |  | Manual | Ball
FCON - Heating - Instrument - Isolation - 26A | C2NC-1200-HTG-HV_44226A | C2NC-1200-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-02 | HV_44226A | [21 empty] | HW |  |  |  |  | Manual | Ball
FCON - Heating - Instrument - Isolation - 26B | C2NC-1200-HTG-HV_44226B | C2NC-1200-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-02 | HV_44226B | [21 empty] | HW |  |  |  |  | Manual | Ball
FCON - Instrument - Isolation - 01A | C2NC-1200-050-HV_21101A | C2NC-1200-050 | Valves | Instrument Isolation Ball Valve | [12 empty] | HV_21101A | [26 empty] | Manual
FCON - Sight - Glass - 05A | C2NC-1200-050-HV_21105A | C2NC-1200-050 | Valves | FCON Sight Glass Ball Valve | [11 empty] | D-01 | HV_21105A | [21 empty] | WU |  | 2 |  |  | Manual | Ball
FCON - Sight - Glass - 05B | C2NC-1200-050-HV_21105B | C2NC-1200-050 | Valves | FCON Sight Glass Ball Valve | [11 empty] | D-01 | HV_21105B | [21 empty] | WU |  | 2 |  |  | Manual | Ball
FCON - From - HX1 - 06 | C2NC-1200-050-HV_21106 | C2NC-1200-050 | Valves | From HX1 Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-01 | HV_21106 | [21 empty] | DFS | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - From - HX2 - 07 | C2NC-1200-050-HV_21107 | C2NC-1200-050 | Valves | From HX2 Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-01 | HV_21107 | [21 empty] | DFS | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Biogas - Sample - Port - 08 | C2NC-1200-050-HV_21108 | C2NC-1200-050 | Valves | FCON Biogas Sample Port Ball Valve | [11 empty] | D-01 | HV_21108 | [21 empty] | BG |  | 1 |  |  | Manual | Ball
FCON - Biogas - Isolation - 09 | C2NC-1200-050-HV_21109 | C2NC-1200-050 | Valves | FCON Biogas Isolation Butterfly Valve | [11 empty] | D-01 | HV_21109 | [21 empty] | BG |  | 12 |  |  | Manual | Butterfly
FCON - Discharge - #1 - Isolation - 12 | C2NC-1200-050-HV_21112 | C2NC-1200-050 | Valves | Discharge #1 Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-01 | HV_21112 | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Discharge - #2 - Isolation - 13 | C2NC-1200-050-HV_21113 | C2NC-1200-050 | Valves | Discharge #2 Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-01 | HV_21113 | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Discharge - #3 - Isolation - 14 | C2NC-1200-050-HV_21114 | C2NC-1200-050 | Valves | Discharge #3 Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-01 | HV_21114 | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - To - HX1 - Isolation - 15 | C2NC-1200-050-HV_21115 | C2NC-1200-050 | Valves | To HX1 Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-01 | HV_21115 | [21 empty] | DFS | CF8M | 10 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - To - HX2 - Isolation - 16 | C2NC-1200-050-HV_21116 | C2NC-1200-050 | Valves | To HX2 Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-01 | HV_21116 | [21 empty] | DFS | CF8M | 10 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Drain - A - 17A | C2NC-1200-050-HV_21117A | C2NC-1200-050 | Valves | FCON Drain A Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-01 | HV_21117A | [21 empty] | DFS | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Drain - B - 17B | C2NC-1200-050-HV_21117B | C2NC-1200-050 | Valves | FCON Drain B Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-01 | HV_21117B | [21 empty] | DFS | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Spare - 18 | C2NC-1200-050-HV_21118 | C2NC-1200-050 | Valves | Spare Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-01 | HV_21118 | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Spare - 19 | C2NC-1200-050-HV_21119 | C2NC-1200-050 | Valves | Spare Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-01 | HV_21119 | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
FCON - Spare - Nozzle - 2 - 20A | C2NC-1200-050-HV_21120A | C2NC-1200-050 | Valves | Spare Nozzle 2 Eccentric Plug Valve | [11 empty] | D-01 | HV_21120A | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
FCON - Spare - Nozzle - 4 - 20B | C2NC-1200-050-HV_21120B | C2NC-1200-050 | Valves | Spare Nozzle 4 Eccentric Plug Valve | [11 empty] | D-01 | HV_21120B | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
FCON - Instrument - Isolation - 24 | C2NC-1200-050-HV_21124 | C2NC-1200-050 | Valves | Instrument Isolation Ball Valve | [11 empty] | D-01 | HV_21124 | [21 empty] | DFS |  | 1.5 |  |  | Manual | Ball
FCON - Instrument - Isolation - 25 | C2NC-1200-050-HV_21125 | C2NC-1200-050 | Valves | Instrument Isolation Ball Valve | [11 empty] | D-01 | HV_21125 | [21 empty] | DFS |  | 1 |  |  | Manual | Ball
FCON - Drain - 26 | C2NC-1200-050-HV_21126 | C2NC-1200-050 | Valves | Drain Ball Valve | [11 empty] | D-01 | HV_21126 | [21 empty] | DFS |  |  |  |  | Manual | Ball
FCON - Drain - 27 | C2NC-1200-050-HV_21127 | C2NC-1200-050 | Valves | Drain Ball Valve | [11 empty] | D-01 | HV_21127 | [21 empty] | DFS |  |  |  |  | Manual | Ball
FCON - Instrument - Isolation - 28 | C2NC-1200-050-HV_21128 | C2NC-1200-050 | Valves | Instrument Isolation Ball Valve | [11 empty] | D-01 | HV_21128 | [21 empty] | DFS |  |  |  |  | Manual | Ball
FCON Anti-Foam Tote Isolation Valve | C2NC-1200-AF-HV_31201 | C2NC-1200-AF | Valves | FCON Anti-foam Tote Isolation Ball Valve | [11 empty] | D-08 | HV_31201 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
FCON Anti-Foam Dosing Check Valve | C2NC-1200-AF-CV_31201 | C2NC-1200-AF | Valves | FCON Anti-Foam Dosing Check Valve | [11 empty] | D-08 | HV_31201 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
FCON Anti-Foam Dosing Valve 1 | C2NC-1200-AF-HV_31202 | C2NC-1200-AF | Valves | FCON Anti-Foam Dosing Valve 1 | [11 empty] | D-08 | HV_31202 | [21 empty] | AF |  | 1 |  |  | Manual | Ball
FCON - Tank | C2NC-1200-050-TK_21101 | C2NC-1200-050 | Tanks | Bolted steel, insulated feed holding tank | Tarsco | [10 empty] | D-01 | TK_21101 | [8 empty] | Tank | [23 empty] | Digestate | Epoxy Coated Steel + SS316 | 71 ft | 59 ft | 1.75 Million Gallons | 1.63 Million Gallons | 55 ft | Bolted Steel
FCON Anti-Foam Tote | C2NC-1200-AF-TK_31201 | C2NC-1200-AF | Tanks | FCON Anti-foam Tote | [11 empty] | D-10 | TK_31201 | [8 empty] | Tank | [23 empty] | Antifoam | HDPE |  | 4 ft | 275 Gallons | 275 Gallons | 4 ft | Tote
FCON - Potable - Water - 04 | C2NC-1200-PW_HV_21104 | C2NC-1200-PW | Valves | FCON Potable Water Knife Gate Valve | [11 empty] | D-01 | HV_21104 | [21 empty] | WU |  | 3 |  |  | Manual | Knife Gate
FCON Service Water | C2NC-1200-SW | C2NC-1200 | Locations And Facilities | Service Water | [11 empty] | D-07
FCON Potable Water | C2NC-1200-PW | C2NC-1200 | Locations And Facilities | Process Water | [11 empty] | D-04
FCON Heating | C2NC-1200-HTG | C2NC-1200 | Locations And Facilities | FCON Heating | [11 empty] | D-02
FCON - Service - Water - 03 | C2NC-1200-SW_HV_21103 | C2NC-1200-SW | Valves | FCON Service Water Knife Gate Valve | [11 empty] | D-01 | HV_21103 | [21 empty] | SW |  | 3 |  |  | Manual | Knife Gate
FCON Feed | C2NC-1200-FD | C2NC-1200 | Locations And Facilities | FCON FEED | [11 empty] | D-01
FCON Antifoam | C2NC-1200-AF | C2NC-1200 | Locations And Facilities | FCON Antifoam
1200 - FCON | C2NC-1200 | C2NC | Locations And Facilities | FCON Area
0.5 Inch Tube Service Water Line 01 | CNC2-1200-SW-0.5_WC01_WS_1200_01 | C2NC-1200-SW | Lines | 0.5 Inch Tube Service Water Line | [11 empty] | D0-1 | 0.5_WC01_WS_1200_01 | [10 empty] | Service Water | Tube | 0.5 inch |  |  | N
10 Inch PVC Diluted Feedstock Line 06 | CNC2-1200-050-10_AC30_FF_1200_06 | C2NC-1200-050 | Lines | 10 Inch PVC Diluted Feedstock Line | [11 empty] | D0-2 | 10_AC30_FF_1200_06 | [10 empty] | Diluted Feedstock | PVC | 10 inch |  |  | N
10 Inch PVC Diluted Feedstock Line 07 | CNC2-1200-050-10_AC30_FF_1200_07 | C2NC-1200-050 | Lines | 10 Inch PVC Diluted Feedstock Line | [11 empty] | D0-2 | 10_AC30_FF_1200_07 | [10 empty] | Diluted Feedstock | PVC | 10 inch |  |  | N
10 Inch Carbon Steel Diluted Feedstock Line 06 | CNC2-1200-FD-10_AE30RT_FF_1200_06 | C2NC-1200-FD | Lines | 10 Inch Carbon Steel Diluted Feedstock Line | [11 empty] | D0-1 | 10_AE30RT_FF_1200_06 | [10 empty] | Diluted Feedstock | Carbon Steel | 10 inch |  |  | N
10 Inch Carbon Steel Diluted Feedstock Line 07 | CNC2-1200-FD-10_AE30RT_FF_1200_07 | C2NC-1200-FD | Lines | 10 Inch Carbon Steel Diluted Feedstock Line | [11 empty] | D0-1 | 10_AE30RT_FF_1200_07 | [10 empty] | Diluted Feedstock | Carbon Steel | 10 inch |  |  | N
12 Inch Stainless Steel Biogas Line 1200_02 | CNC2-1200-050-12_AS30_GB_1200_02 | C2NC-1200-050 | Lines | 12 Inch Stainless Steel Biogas Line | [11 empty] | D0-1 | 12_AS30_GB_1200_02 | [10 empty] | Biogas | Stainless Steel | 12 inch |  |  | N
4 Inch PVC Diluted Feedstock Line 03 | CNC2-1200-FD-4_AC30_FF_1200_03 | C2NC-1200-FD | Lines | 4 Inch PVC Diluted Feedstock Line | [11 empty] | D0-3 | 4_AC30_FF_1200_03 | [10 empty] | Diluted Feedstock | PVC | 4 inch |  |  | N
4 Inch PVC Diluted Feedstock Line 04 | CNC2-1200-FD-4_AC30_FF_1200_04 | C2NC-1200-FD | Lines | 4 Inch PVC Diluted Feedstock Line | [11 empty] | D0-3 | 4_AC30_FF_1200_04 | [10 empty] | Diluted Feedstock | PVC | 4 inch |  |  | N
4 Inch PVC Diluted Feedstock Line 05 | CNC2-1200-FD-4_AC30_FF_1200_05 | C2NC-1200-FD | Lines | 4 Inch PVC Diluted Feedstock Line | [11 empty] | D0-3 | 4_AC30_FF_1200_05 | [10 empty] | Diluted Feedstock | PVC | 4 inch |  |  | N
6 Inch Carbon Steel Diluted Feedstock Line 03 | CNC2-1200-FD-6_AE30RT_FF_1200_03 | C2NC-1200-FD | Lines | 6 Inch Carbon Steel Diluted Feedstock Line | [11 empty] | D0-1 | 6_AE30RT_FF_1200_03 | [10 empty] | Diluted Feedstock | Carbon Steel | 6 inch |  |  | N
6 Inch Carbon Steel Diluted Feedstock Line 04 | CNC2-1200-FD-6_AE30RT_FF_1200_04 | C2NC-1200-FD | Lines | 6 Inch Carbon Steel Diluted Feedstock Line | [11 empty] | D0-1 | 6_AE30RT_FF_1200_04 | [10 empty] | Diluted Feedstock | Carbon Steel | 6 inch |  |  | N
6 Inch Carbon Steel Diluted Feedstock Line 05 | CNC2-1200-FD-6_AE30RT_FF_1200_05 | C2NC-1200-FD | Lines | 6 Inch Carbon Steel Diluted Feedstock Line | [11 empty] | D0-1 | 6_AE30RT_FF_1200_05 | [10 empty] | Diluted Feedstock | Carbon Steel | 6 inch |  |  | N
8 Inch PVC Diluted Feedstock Line 06 | CNC2-1200-050-8_AC30_FF_1200_06 | C2NC-1200-050 | Lines | 8 Inch PVC Diluted Feedstock Line | [11 empty] | D0-1 | 8_AC30_FF_1200_06 | [10 empty] | Diluted Feedstock | PVC | 8 inch |  |  | N
8 Inch PVC Diluted Feedstock Line 07 | CNC2-1200-FD-8_AC30_FF_1200_07 | C2NC-1200-FD | Lines | 8 Inch PVC Diluted Feedstock Line | [11 empty] | D0-1 | 8_AC30_FF_1200_07 | [10 empty] | Diluted Feedstock | PVC | 8 inch |  |  | N
FCON - Level - Indicating - Transmitter - 21101 | C2NC-1200-050-LIT_21101 | C2NC-1200-050 | Instruments | Level transmitter for FCON tank (at bottom) - Instruments | [7 empty] | Y |  | Analog |  | D-01 | LIT_21101 | [42 empty] | DFS | 0 |  | Level Indicating Transmitter |  | Analog
FCON - Level - Sensor - 21102 | C2NC-1200-050-LIT_21102 | C2NC-1200-050 | Instruments | Level sensor for FCON tank (ultrasonic) - Instruments | [7 empty] | Y |  | Analog |  | D-01 | LIT_21102 | [42 empty] | DFS | 0 |  | Level Sensor |  | Analog
FCON - Level - High - High - Switch - 21101 | C2NC-1200-050-LSHH_21101 | C2NC-1200-050 | Instruments | Level switch for FCON tank (at top) - Instruments | [7 empty] | Y |  | Digital |  | D-01 | LSHH_21101 | [42 empty] | DFS | 0 |  | Level High High Switch |  | Digital
FCON - Pressure - Indicating - Transmitter - 21101 | C2NC-1200-050-PIT_21101 | C2NC-1200-050 | Instruments | Pressure transmitter for biogas line from FCON - Instruments | [7 empty] | Y |  | Analog |  | D-01 | PIT_21101 | [42 empty] | BG | 0 |  | Pressure Indicating Transmitter |  | Analog
FCON - Temperature - Indicating - Transmitter - 21101 | C2NC-1200-050-TIT_21101 | C2NC-1200-050 | Instruments | Temperature transmitter for FCON tank with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-01 | TIT_21101 | [42 empty] | DFS | 0 |  | Temperature Indicating Transmitter |  | Analog
FCON - Temperature - Indicating - Transmitter - 21102 | C2NC-1200-050-TIT_21102 | C2NC-1200-050 | Instruments | Second temperature transmitter for FCON tank with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-01 | TIT_21102 | [42 empty] | DFS | 0 |  | Temperature Indicating Transmitter |  | Analog
FCON - Thermowell - 21101 | C2NC-1200-050-TW_21101 | C2NC-1200-050 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-01 | TW_21101 | [42 empty] | DFS | 0 |  | Temperature Indicating Transmitter |  | Analog
FCON - Thermowell - 21102 | C2NC-1200-050-TW_21102 | C2NC-1200-050 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-01 | TW_21102 | [42 empty] | DFS | 0 |  | Temperature Indicating Transmitter |  | Analog
FCON - Mixer - #1 | C2NC-1200-050-MX_21101 | C2NC-1200-050 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSMA4_XP 940 | [5 empty] | P |  |  |  | D-01 | MX_21101 |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
FCON - Mixer - #2 | C2NC-1200-050-MX_21102 | C2NC-1200-050 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSMA4_XP 940 | [5 empty] | P |  |  |  | D-01 | MX_21102 |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
FCON - Mixer - #3 | C2NC-1200-050-MX_21103 | C2NC-1200-050 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSMA4_XP 940 | [5 empty] | P |  |  |  | D-01 | MX_21103 |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
FCON - Mixer - #4 | C2NC-1200-050-MX_21104 | C2NC-1200-050 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSMA4_XP 940 | [5 empty] | P |  |  |  | D-01 | MX_21104 |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
FCON - Mixer - #5 | C2NC-1200-050-MX_21105 | C2NC-1200-050 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSMA4_XP 940 | [5 empty] | P |  |  |  | D-01 | MX_21105 |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
FCON - Mixer - #6 | C2NC-1200-050-MX_21106 | C2NC-1200-050 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSMA4_XP 940 | [5 empty] | P |  |  |  | D-01 | MX_21106 |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
FCON Anti-Foam Dosing Pump | C2NC-1200-AF-P_31201A | C2NC-1200-AF | Equipment | FCON Anti-Foam Dosing Pump | Seepex | MD 003-12 | [5 empty] | P |  |  |  | D-04 | P_31201A |  | 120 |  | 1 HP |  |  |  |  | Pump
FCON Anti-Foam Dosing Pump Standby | C2NC-1200-AF-P_31201B | C2NC-1200-AF | Equipment | FCON Anti-Foam Dosing Pump Standby | Seepex | MD 003-12 | [5 empty] | P |  |  |  | D-04 | P_31201B |  | 120 |  | 1 HP |  |  |  |  | Pump
FCON - Mixer - Service - Box - #1 | C2NC-1200-050-SB_21101 | C2NC-1200-050 | Equipment | Service Box Pro for fixed cover roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-01 | SB_21101 | [8 empty] | Service Box
FCON - Mixer - Service - Box - #2 | C2NC-1200-050-SB_21102 | C2NC-1200-050 | Equipment | Service Box Pro for fixed cover roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-01 | SB_21102 | [8 empty] | Service Box
FCON - Mixer - Service - Box - #3 | C2NC-1200-050-SB_21103 | C2NC-1200-050 | Equipment | Service Box Pro for fixed cover roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-01 | SB_21103 | [8 empty] | Service Box
FCON - Mixer - Service - Box - #4 | C2NC-1200-050-SB_21104 | C2NC-1200-050 | Equipment | Service Box Pro for fixed cover roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-01 | SB_21104 | [8 empty] | Service Box
FCON - Mixer - Service - Box - #5 | C2NC-1200-050-SB_21105 | C2NC-1200-050 | Equipment | Service Box Pro for fixed cover roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-01 | SB_21105 | [8 empty] | Service Box
FCON - Mixer - Service - Box - #6 | C2NC-1200-050-SB_21106 | C2NC-1200-050 | Equipment | Service Box Pro for fixed cover roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-01 | SB_21106 | [8 empty] | Service Box
FCON - Mixer - Auto-Positioner - #1 | C2NC-1200-050-SB_M_21101 | C2NC-1200-050 | Equipment | FCON - Mixer - Auto-Positioner - #1 | AUMA | [6 empty] | Y |  |  |  | D-04 | SB_M_21101 | [8 empty] | Electric Positioner
FCON - Mixer - Auto-Positioner - #2 | C2NC-1200-050-SB_M_21102 | C2NC-1200-050 | Equipment | FCON - Mixer - Auto-Positioner - #2 | AUMA | [6 empty] | Y |  |  |  | D-04 | SB_M_21102 | [8 empty] | Electric Positioner
FCON - Mixer - Auto-Positioner - #3 | C2NC-1200-050-SB_M_21103 | C2NC-1200-050 | Equipment | FCON - Mixer - Auto-Positioner - #3 | AUMA | [6 empty] | Y |  |  |  | D-04 | SB_M_21103 | [8 empty] | Electric Positioner
FCON - Mixer - Auto-Positioner - #4 | C2NC-1200-050-SB_M_21104 | C2NC-1200-050 | Equipment | FCON - Mixer - Auto-Positioner - #4 | AUMA | [6 empty] | Y |  |  |  | D-04 | SB_M_21104 | [8 empty] | Electric Positioner
FCON - Mixer - Auto-Positioner - #5 | C2NC-1200-050-SB_M_21105 | C2NC-1200-050 | Equipment | FCON - Mixer - Auto-Positioner - #5 | AUMA | [6 empty] | Y |  |  |  | D-04 | SB_M_21105 | [8 empty] | Electric Positioner
FCON - Mixer - Auto-Positioner - #6 | C2NC-1200-050-SB_M_21106 | C2NC-1200-050 | Equipment | FCON - Mixer - Auto-Positioner - #6 | AUMA | [6 empty] | Y |  |  |  | D-04 | SB_M_21106 | [8 empty] | Electric Positioner
FCON - Sight - Glass 1 | C2NC-1200-050-SG_21101 | C2NC-1200-050 | Equipment | FCON Sight Glass | [11 empty] | D-01 | SG_21101 | [8 empty] | Sight Glass
FCON - Sight - Glass 2 | C2NC-1200-050-SG_21102 | C2NC-1200-050 | Equipment | FCON Sight Glass | [11 empty] | D-01 | SG_21102 | [8 empty] | Sight Glass
FCON - Heat - Exchanger - #1 | C2NC-1200-HTG-HX_44201A | C2NC-1200-HTG | Equipment | 1250kW duty heat exchanger | Lackeby | [6 empty] | Y |  |  |  | D-02 | HX_44201A | [8 empty] | Heat Exchanger
FCON - Heat - Exchanger - #2 | C2NC-1200-HTG-HX_44201B | C2NC-1200-HTG | Equipment | 1250kW duty heat exchanger | Lackeby | [6 empty] | Y |  |  |  | D-02 | HX_44201B | [8 empty] | Heat Exchanger
FCON - Heat - Exchanger - Pump - #1 | C2NC-1200-HTG-P_44201A | C2NC-1200-HTG | Equipment | FCON - Heat - Exchanger - Pump - #1 | Boerger | EL 1000 | [5 empty] | P |  |  |  | D-02 | P_44201A |  | 480 |  | 100 HP |  |  |  |  | Pump
FCON - Heat - Exchanger - Pump - #2 | C2NC-1200-HTG-P_44201B | C2NC-1200-HTG | Equipment | FCON - Heat - Exchanger - Pump - #2 | Boerger | EL 1000 | [5 empty] | P |  |  |  | D-02 | P_44201B |  | 480 |  | 100 HP |  |  |  |  | Pump
Hot - Water - Pump - #3 | C2NC-1200-HTG-P_44202A | C2NC-1200-HTG | Equipment | Hot - Water - Pump - #3 | [7 empty] | P |  |  |  | D-02 | P_44202A |  | 460 |  | 30 HP |  |  |  |  | Pump
Hot - Water - Pump - #4 | C2NC-1200-HTG-P_44202B | C2NC-1200-HTG | Equipment | Hot - Water - Pump - #4 | [7 empty] | P |  |  |  | D-02 | P_44202B |  | 460 |  | 30 HP |  |  |  |  | Pump
Sight Glass
Electric Positioner

## 1300 - Digesters
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual RQD | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Connection Type | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | *Any Custom Fields* | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes
Digester Condensate | C2NC-1300-CND | C2NC-1300 | Locations And Facilities | Digester Condensate
Digester Service Water | C2NC-1300-SW | C2NC-1300 | Locations And Facilities | Digester Service Water
Digester Biogas | C2NC-1300-BG | C2NC-1300 | Locations And Facilities | Digester Biogas
Digester Digestate | C2NC-1300-DG | C2NC-1300 | Locations And Facilities | Digester Digestate
Digester - 1 - Antifoam - 01A | C2NC-1300-100-FCV_31201 | C2NC-1300-100 | Valves | Antifoam Solenoid Valve | [7 empty] | Y |  |  |  | D-08 | FCV_31201 | [21 empty] | ADA |  | 25DN |  |  | Automatic | Solenoid
Digester - 1 - Service - Water - 01A | C2NC-1300-100-FCV_41201A | C2NC-1300-100 | Valves | Service Water Solenoid Valve | [7 empty] | Y |  |  |  | D-04 | FCV_41201A | [21 empty] | SW |  | 0.5 |  |  | Automatic | Solenoid
Digester - 2 - Antifoam - 02 | C2NC-1300-200-FCV_31202 | C2NC-1300-200 | Valves | Antifoam Solenoid Valve | [7 empty] | Y |  |  |  | D-05 | FCV_31202 | [21 empty] | CH |  | 1 |  |  | Automatic | Solenoid
Digester - 2 - Service - Water - 01B | C2NC-1300-200-FCV_41201B | C2NC-1300-200 | Valves | Service Water Solenoid Valve | [7 empty] | Y |  |  |  | D-05 | FCV_41201B | [21 empty] | SW |  | 0.5 |  |  | Automatic | Solenoid
Digester - 3 - Antifoam - 03 | C2NC-1300-300-FCV_31203 | C2NC-1300-300 | Valves | Antifoam Solenoid Valve | [7 empty] | Y |  |  |  | D-06 | FCV_31203 | [21 empty] | CH |  | 1 |  |  | Automatic | Solenoid
Digester - 3 - Service - Water - 01C | C2NC-1300-300-FCV_41201C | C2NC-1300-300 | Valves | Service Water Solenoid Valve | [7 empty] | Y |  |  |  | D-06 | FCV_41201C | [21 empty] | SW |  | 0.5 |  |  | Automatic | Solenoid
Sodium Hydroxide - Solenoid Valve - 01 | C2NC-1300-CHEM-FCV_31101 | C2NC-1300-CHEM | Valves | Solenoid Valve | [7 empty] | Y |  |  |  | D-08 | FCV_31101 | [21 empty] | ADA |  | 25DN |  |  | Automatic | Solenoid
Sodium Hydroxide - Solenoid Valve - 02 | C2NC-1300-CHEM-FCV_31102 | C2NC-1300-CHEM | Valves | Solenoid Valve | [7 empty] | Y |  |  |  | D-08 | FCV_31102 | [21 empty] | ADA |  | 25DN |  |  | Automatic | Solenoid
Sodium Hydroxide - Solenoid Valve - 03 | C2NC-1300-CHEM-FCV_31103 | C2NC-1300-CHEM | Valves | Solenoid Valve | [7 empty] | Y |  |  |  | D-08 | FCV_31103 | [21 empty] | ADA |  | 25DN |  |  | Automatic | Solenoid
Sodium Hydroxide - Solenoid Valve - 04 | C2NC-1300-CHEM-FCV_31104 | C2NC-1300-CHEM | Valves | Solenoid Valve | [7 empty] | Y |  |  |  | D-08 | FCV_31104 | [21 empty] | ADA |  | 25DN |  |  | Automatic | Solenoid
Sodium Hypochlorite - Solenoid Valve - 01 | C2NC-1300-CHEM-FCV_31201 | C2NC-1300-CHEM | Valves | Solenoid Valve | [7 empty] | Y |  |  |  | D-08 | FCV_31201 | [21 empty] | ADA |  | 25DN |  |  | Automatic | Solenoid
Sodium Hypochlorite - Solenoid Valve - 02 | C2NC-1300-CHEM-FCV_31202 | C2NC-1300-CHEM | Valves | Solenoid Valve | [7 empty] | Y |  |  |  | D-05 | FCV_31202 | [21 empty] | CH |  | 1 |  |  | Automatic | Solenoid
Sodium Hypochlorite - Valve Solenoid - 03 | C2NC-1300-CHEM-FCV_31203 | C2NC-1300-CHEM | Valves | Solenoid Valve | [7 empty] | Y |  |  |  | D-06 | FCV_31203 | [21 empty] | CH |  | 1 |  |  | Automatic | Solenoid
Sodium Hypochlorite - Solenoid Valve - 04 | C2NC-1300-CHEM-FCV_31204 | C2NC-1300-CHEM | Valves | Solenoid Valve | [7 empty] | Y |  |  |  | D-01 | FCV_31204 | [21 empty] | DFS |  | 1 |  |  | Automatic | Solenoid
Digester - Heat - Exchangers - Hot - Water - Flow - Control - 01A | C2NC-1300-HTG-EV_44101A | C2NC-1300-HTG | Valves | Hot Water Flow Control 3 Way Valve | [7 empty] | Y |  |  |  | D-09 | EV_44101A | [21 empty] | HW |  |  |  |  | Automatic | 3 Way
Digester - Heat - Exchangers - Hot - Water - Flow - Control - 01B | C2NC-1300-HTG-EV_44101B | C2NC-1300-HTG | Valves | Hot Water Flow Control 3 Way Valve | [7 empty] | Y |  |  |  | D-09 | EV_44101B | [21 empty] | HW |  |  |  |  | Automatic | 3 Way
Digester - Heat - Exchangers - Hot - Water - Flow - Control - 01C | C2NC-1300-HTG-EV_44101C | C2NC-1300-HTG | Valves | Hot Water Flow Control 3 Way Valve | [7 empty] | Y |  |  |  | D-09 | EV_44101C | [21 empty] | HW |  |  |  |  | Automatic | 3 Way
Condensate - Trap | C2NC-1300-CND-TK_41202 | C2NC-1300-CND | Tanks | Condensate trap for combined biogas line from all tanks | [11 empty] | D-07 | TK_41202 | [8 empty] | Tank | [23 empty] | Condensate | HDPE | [5 empty] | Prefabricated HDPE
Membrane - Cover - for - Digester - #1 | C2NC-1300-100-MC_41201A | C2NC-1300-100 | Tanks | Double Membrane Tank Cover - Semi Sphere | Ecomembrane | [10 empty] | D-06 | MC_41201A | [8 empty] | Tank | [23 empty] | Biogas | PVC Coated PE | 115 ft | 31 ft | 150400 ft3 | 150400 ft3 |  | Inflatable Membrane
Anaerobic - Digester - #1 | C2NC-1300-100-TK_41201A | C2NC-1300-100 | Tanks | Bolted steel, insulated digester | Tarsco | [10 empty] | D-04 | TK_41201A | [8 empty] | Tank | [23 empty] | Digestate | Epoxy Coated Steel + SS316 | 115 ft | 59 ft | 4.58 Million Gallons | 4.27 Million Gallons | 55 ft | Bolted Steel
Membrane - Cover - for - Digester - #2 | C2NC-1300-200-MC_41201B | C2NC-1300-200 | Tanks | Double Membrane Tank Cover - Semi Sphere | Ecomembrane | [10 empty] | D-09 | MC_41201B | [8 empty] | Tank | [23 empty] | Biogas | PVC Coated PE | 115 ft | 31 ft | 150400 ft3 | 150400 ft3 |  | Inflatable Membrane
Anaerobic - Digester - #2 | C2NC-1300-200-TK_41201B | C2NC-1300-200 | Tanks | Bolted steel, insulated digester | Tarsco | [10 empty] | D-05 | TK_41201B | [8 empty] | Tank | [23 empty] | Digestate | Epoxy Coated Steel + SS316 | 115 ft | 59 ft | 4.58 Million Gallons | 4.27 Million Gallons | 55 ft | Bolted Steel
Membrane - Cover - for - Digester - #3 | C2NC-1300-300-MC_41201C | C2NC-1300-300 | Tanks | Double Membrane Tank Cover - Semi Sphere | Ecomembrane | [10 empty] | D-06 | MC_41201C | [8 empty] | Tank | [23 empty] | Biogas | PVC Coated PE | 115 ft | 31 ft | 150400 ft3 | 150400 ft3 |  | Inflatable Membrane
Anaerobic - Digester - #3 | C2NC-1300-300-TK_41201C | C2NC-1300-300 | Tanks | Bolted steel, insulated digester | Tarsco | [10 empty] | D-06 | TK_41201C | [8 empty] | Tank | [23 empty] | Digestate | Epoxy Coated Steel + SS316 | 115 ft | 59 ft | 4.58 Million Gallons | 4.27 Million Gallons | 55 ft | Bolted Steel
Nutrient - Tote | C2NC-1300-CHEM-TK_31101 | C2NC-1300-CHEM | Tanks | Tank for micronutrients suitable for AD And FCON | [11 empty] | D-08 | TK_31101 | [8 empty] | Tank | [23 empty] | Micronutrient | HDPE |  | 4 ft | 275 Gallons | 275 Gallons | 4 ft | Tote
Anti-Foam - Tote | C2NC-1300-CHEM-TK_31201 | C2NC-1300-CHEM | Tanks | Tank for anti-foam | [11 empty] | D-08 | TK_31201 | [8 empty] | Tank | [23 empty] | Antifoam | HDPE |  | 4 ft | 275 Gallons | 275 Gallons | 4 ft | Tote
Digester Heating System | C2NC-1300-HTG | C2NC-1300 | Locations And Facilities | Heating System
Digester Feeding | C2NC-1300-FD | C2NC-1300 | Locations And Facilities | Digester Feeding
Digester Chemical Dosing | C2NC-1300-CHEM | C2NC-1300 | Locations And Facilities | Digester Chemical Dosing
Digester #3 | C2NC-1300-300 | C2NC-1300 | Locations And Facilities | DIGESTER #3 | [11 empty] | D-06
Digester #2 | C2NC-1300-200 | C2NC-1300 | Locations And Facilities | DIGESTER #2 | [11 empty] | D-03
Digester #1 | C2NC-1300-100 | C2NC-1300 | Locations And Facilities | DIGESTER #1 | [11 empty] | D-04
1300 - Digesters | C2NC-1300 | C2NC | Locations And Facilities | DIGESTERS | [11 empty] | D-04
Digester - 1 - Membrane - Blower - Check Valve - 01A | C2NC-1300-100-CV_41201A | C2NC-1300-100 | Valves | Membrane Blower Check Valve | [11 empty] | D-04 | CV_41201A | [21 empty] | AU |  | 8 |  |  | Manual | Check
Digester - 1 - Antifoam - 18A | C2NC-1300-100-HV_41218A | C2NC-1300-100 | Valves | Antifoam Ball Valve | [11 empty] | D-04 | HV_41218A | [21 empty] | ADA |  | 1 |  |  | Manual | Ball
Digester - 1 - Service - Water - 19A | C2NC-1300-100-HV_41219A | C2NC-1300-100 | Valves | Service Water Knife Gate Valve | [11 empty] | D-04 | HV_41219A | [21 empty] | WU |  | 3 |  |  | Manual | Knife Gate
Digester - 1 - Sight - Glass - 20A | C2NC-1300-100-HV_41220A | C2NC-1300-100 | Valves | Sight Glass Ball Valve | [11 empty] | D-04 | HV_41220A | [21 empty] | WU |  | 0.5 |  |  | Manual | Ball
Digester - 1 - Feed - Line - 21A | C2NC-1300-100-HV_41221A | C2NC-1300-100 | Valves | Feed Line Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-04 | HV_41221A | [21 empty] | DFS | CF8M | 4 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 1 - Service - Water - 22A | C2NC-1300-100-HV_41222A | C2NC-1300-100 | Valves | Service Water Knife Gate Valve | [11 empty] | D-04 | HV_41222A | [21 empty] | SW |  | 3 |  |  | Manual | Knife Gate
Digester - 1 - Return - from - HX - 23A | C2NC-1300-100-HV_41223A | C2NC-1300-100 | Valves | Return from HX Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-04 | HV_41223A | [21 empty] | DGT | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 1 - Membrane - Blower - 24A | C2NC-1300-100-HV_41224A | C2NC-1300-100 | Valves | Membrane Blower Butterfly Valve | [11 empty] | D-04 | HV_41224A | [21 empty] | AU |  | 8 |  |  | Manual | Butterfly
Digester - 1 - Biogas - Offtake - 25A | C2NC-1300-100-HV_41225A | C2NC-1300-100 | Valves | Biogas Offtake Butterfly Valve | [11 empty] | D-04 | HV_41225A | [21 empty] | BG |  | 8 |  |  | Manual | Butterfly
Digester - 1 - Biogas - Offtake - 28A | C2NC-1300-100-HV_41228A | C2NC-1300-100 | Valves | Biogas Offtake Butterfly Valve | [11 empty] | D-04 | HV_41228A | [21 empty] | BG |  | 8 |  |  | Manual | Butterfly
Digester - 1 - Sight - Glass - 29A | C2NC-1300-100-HV_41229A | C2NC-1300-100 | Valves | Sight Glass Ball Valve Valve | [11 empty] | D-04 | HV_41229A | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Biogas - Offtake - 31A | C2NC-1300-100-HV_41231A | C2NC-1300-100 | Valves | Biogas Offtake Butterfly Valve | [11 empty] | D-04 | HV_41231A | [21 empty] | BG |  | 8 |  |  | Manual | Butterfly
Digester - 1 - Service - Water - 34A | C2NC-1300-100-HV_41234A | C2NC-1300-100 | Valves | Service Water Ball Valve Valve | [11 empty] | D-04 | HV_41234A | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Service - Water - 35A | C2NC-1300-100-HV_41235A | C2NC-1300-100 | Valves | Service Water Ball Valve Valve | [11 empty] | D-04 | HV_41235A | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Service - Water - 36A | C2NC-1300-100-HV_41236A | C2NC-1300-100 | Valves | Service Water Ball Valve Valve | [11 empty] | D-04 | HV_41236A | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Service - Water - 37A | C2NC-1300-100-HV_41237A | C2NC-1300-100 | Valves | Service Water Ball Valve Valve | [11 empty] | D-04 | HV_41237A | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Service - Water - 38A | C2NC-1300-100-HV_41238A | C2NC-1300-100 | Valves | Service Water Ball Valve Valve | [11 empty] | D-04 | HV_41238A | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Instrument - Isolation - 39A | C2NC-1300-100-HV_41239A | C2NC-1300-100 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-04 | HV_41239A | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Drain - 40A | C2NC-1300-100-HV_41240A | C2NC-1300-100 | Valves | Drain Ball Valve Valve | [11 empty] | D-04 | HV_41240A | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Biogas - to - AD2 - 41A | C2NC-1300-100-HV_41241A | C2NC-1300-100 | Valves | Biogas to AD2 Butterfly Valve | [11 empty] | D-04 | HV_41241A | [21 empty] | BG |  | 12 |  |  | Manual | Butterfly
Digester - 1 - Discharge - 42A | C2NC-1300-100-HV_41242A | C2NC-1300-100 | Valves | Discharge Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-04 | HV_41242A | [21 empty] | DGT | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 1 - To - HX - 43A | C2NC-1300-100-HV_41243A | C2NC-1300-100 | Valves | To HX Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-04 | HV_41243A | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 1 - Drain - 44A | C2NC-1300-100-HV_41244A | C2NC-1300-100 | Valves | Drain Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-04 | HV_41244A | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 1 - Drain - Valve - 45A | C2NC-1300-100-HV_41245A | C2NC-1300-100 | Valves | Drain Valve Ball Valve | [11 empty] | D-04 | HV_41245A | [21 empty] | DGT |  | 0.5 |  |  | Manual | Ball
Digester - 1 - Instrument - Isolation - 46A | C2NC-1300-100-HV_41246A | C2NC-1300-100 | Valves | Instrument Isolation Ball Valve | Orbinox | BT Series 22 | [9 empty] | D-04 | HV_41246A | [21 empty] | DGT |  | 0.5 |  |  | Manual | Ball
Digester - 1 - Spare - Nozzle - 47A | C2NC-1300-100-HV_41247A | C2NC-1300-100 | Valves | Spare Nozzle Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-04 | HV_41247A | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 1 - Spare - Nozzle - 48A | C2NC-1300-100-HV_41248A | C2NC-1300-100 | Valves | Spare Nozzle Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-04 | HV_41248A | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 1 - Drain - 49A | C2NC-1300-100-HV_41249A | C2NC-1300-100 | Valves | Drain Ball Valve Valve | [11 empty] | D-04 | HV_41249A | [21 empty] | BG |  | 12 |  |  | Manual | Butterfly
Digester - 1 - Drain - 50A | C2NC-1300-100-HV_41250A | C2NC-1300-100 | Valves | Drain Ball Valve Valve | [11 empty] | D-04 | HV_41250A | [21 empty] | DGT |  | 2 |  |  | Manual | Ball Valve
Digester - 1 - Instrument - Isolation - 51A | C2NC-1300-100-HV_41251A | C2NC-1300-100 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-04 | HV_41251A | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - 1 - Instrument - Isolation - 52A | C2NC-1300-100-HV_41252A | C2NC-1300-100 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-04 | HV_41252A | [21 empty] | DGT |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Drain - 53A | C2NC-1300-100-HV_41253A | C2NC-1300-100 | Valves | Drain Ball Valve Valve | [11 empty] | D-04 | HV_41253A | [21 empty] | DGT |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Biogas - from - FCON - 54A | C2NC-1300-100-HV_41254A | C2NC-1300-100 | Valves | Biogas from FCON Butterfly Valve | [11 empty] | D-07 | HV_41254A | [21 empty] | BG |  | 12 |  |  | Manual | Butterfly
Digester - 1 - Instrument - Isolation - 55A | C2NC-1300-100-HV_41255A | C2NC-1300-100 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-04 | HV_41255A | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Drain - 56A | C2NC-1300-100-HV_41256A | C2NC-1300-100 | Valves | Drain Ball Valve Valve | [11 empty] | D-04 | HV_41256A | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Instrument - Isolation - 57A | C2NC-1300-100-HV_41257A | C2NC-1300-100 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-04 | HV_41257A | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Drain - 58A | C2NC-1300-100-HV_41258A | C2NC-1300-100 | Valves | Drain Ball Valve Valve | [11 empty] | D-04 | HV_41258A | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 1 - Drain - 59A | C2NC-1300-100-HV_41259A | C2NC-1300-100 | Valves | Drain Eccentric Plug Valve | Orbinox | BT Series 22 | [9 empty] | D-10 | HV_41259A | [21 empty] | DGT | CF8M | 150DN |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 1 - Gas - Recirculation - 63A | C2NC-1300-100-HV_41263A | C2NC-1300-100 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-04 | HV_41263A | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 1 - Gas - Recirculation - 64A | C2NC-1300-100-HV_41264A | C2NC-1300-100 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-04 | HV_41264A | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 1 - Gas - Recirculation - 65A | C2NC-1300-100-HV_41265A | C2NC-1300-100 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-04 | HV_41265A | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 1 - Gas - Recirculation - 66A | C2NC-1300-100-HV_41266A | C2NC-1300-100 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-04 | HV_41266A | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 1 - Gas - Recirculation - 70A | C2NC-1300-100-HV_41270A | C2NC-1300-100 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-04 | HV_41270A | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 1 - Gas - Recirculation - 71A | C2NC-1300-100-HV_41271A | C2NC-1300-100 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-04 | HV_41271A | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 1 - Gas - Recirculation - 72A | C2NC-1300-100-HV_41272A | C2NC-1300-100 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-04 | HV_41272A | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 1 - Gas - Recirculation - 73A | C2NC-1300-100-HV_41273A | C2NC-1300-100 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-04 | HV_41273A | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 1 - Gas - Recirculation - 74A | C2NC-1300-100-HV_41274A | C2NC-1300-100 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-04 | HV_41274A | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
0.5 Inch Tube Service Water Line 1310_02 | CNC2-1300-SW-0.5_WC01_WS_1310_02 | C2NC-1300-SW | Lines | 0.5 Inch Tube Service Water Line | [11 empty] | D0-4 | 0.5_WC01_WS_1310_02 | [10 empty] | Service Water | Tube | 0.5 inch |  |  | N
0.5 Inch Tube Service Water Line 1320_02 | CNC2-1300-SW-0.5_WC01_WS_1320_02 | C2NC-1300-SW | Lines | 0.5 Inch Tube Service Water Line | [11 empty] | D0-5 | 0.5_WC01_WS_1320_02 | [10 empty] | Service Water | Tube | 0.5 inch |  |  | N
0.5 Inch Tube Service Water Line 1330_02 | CNC2-1300-SW-0.5_WC01_WS_1330_02 | C2NC-1300-SW | Lines | 0.5 Inch Tube Service Water Line | [11 empty] | D0-6 | 0.5_WC01_WS_1330_02 | [10 empty] | Service Water | Tube | 0.5 inch |  |  | N
1 Inch PVC Antifoam Line 01 | CNC2-1300-CHEM-1_AC30_CH_1300_01 | C2NC-1300-CHEM | Lines | 1 Inch PVC Antifoam Line | [11 empty] | D0-1 | 1_AC30_CH_1300_01 | [10 empty] | Antifoam | PVC | 1 inch |  |  | N
12 Inch Stainless Steel Biogas Line 1310_02 | CNC2-1300-BG-12_AS30_GB_1310_02 | C2NC-1300-BG | Lines | 12 Inch Stainless Steel Biogas Line | [11 empty] | D0-5 | 12_AS30_GB_1310_02 | [10 empty] | Biogas | Stainless Steel | 12 inch |  |  | N
12 Inch Stainless Steel Biogas Line 1310_06 | CNC2-1300-BG-12_AS30_GB_1310_06 | C2NC-1300-BG | Lines | 12 Inch Stainless Steel Biogas Line | [11 empty] | D0-4 | 12_AS30_GB_1310_06 | [10 empty] | Biogas | Stainless Steel | 12 inch |  |  | N
12 Inch Stainless Steel Biogas Line 1310_07 | CNC2-1300-BG-12_AS30_GB_1310_07 | C2NC-1300-BG | Lines | 12 Inch Stainless Steel Biogas Line | [11 empty] | D0-4 | 12_AS30_GB_1310_07 | [10 empty] | Biogas | Stainless Steel | 12 inch |  |  | N
12 Inch Stainless Steel Biogas Line 1320_06 | CNC2-1300-BG-12_AS30_GB_1320_06 | C2NC-1300-BG | Lines | 12 Inch Stainless Steel Biogas Line | [11 empty] | D0-5 | 12_AS30_GB_1320_06 | [10 empty] | Biogas | Stainless Steel | 12 inch |  |  | N
12 Inch Stainless Steel Biogas Line 1320_07 | CNC2-1300-BG-12_AS30_GB_1320_07 | C2NC-1300-BG | Lines | 12 Inch Stainless Steel Biogas Line | [11 empty] | D0-5 | 12_AS30_GB_1320_07 | [10 empty] | Biogas | Stainless Steel | 12 inch |  |  | N
12 Inch Stainless Steel Biogas Line 1330_06 | CNC2-1300-BG-12_AS30_GB_1330_06 | C2NC-1300-BG | Lines | 12 Inch Stainless Steel Biogas Line | [11 empty] | D0-6 | 12_AS30_GB_1330_06 | [10 empty] | Biogas | Stainless Steel | 12 inch |  |  | N
16 Inch Stainless Steel Biogas Line 02 | CNC2-1300-BG-16_AS30_GB_1300_02 | C2NC-1300-BG | Lines | 16 Inch Stainless Steel Biogas Line | [11 empty] | D0-7 | 16_AS30_GB_1300_02 | [10 empty] | Biogas | Stainless Steel | 16 inch |  |  | N
4 Inch PVC Digestate Line 1310_08 | CNC2-1300-DG-4_AC30_ED_1310_08 | C2NC-1300-DG | Lines | 4 Inch PVC Digestate Line | [11 empty] | D0-10 | 4_AC30_ED_1310_08 | [10 empty] | Digestate | PVC | 4 inch |  |  | N
4 Inch PVC Digestate Line 1320_08 | CNC2-1300-DG-4_AC30_ED_1320_08 | C2NC-1300-DG | Lines | 4 Inch PVC Digestate Line | [11 empty] | D0-10 | 4_AC30_ED_1320_08 | [10 empty] | Digestate | PVC | 4 inch |  |  | N
4 Inch PVC Digestate Line 1330_08 | CNC2-1300-DG-4_AC30_ED_1330_08 | C2NC-1300-DG | Lines | 4 Inch PVC Digestate Line | [11 empty] | D0-10 | 4_AC30_ED_1330_08 | [10 empty] | Digestate | PVC | 4 inch |  |  | N
6 Inch PVC Digestate Line 1310_08 | CNC2-1300-DG-6_AC30_ED_1310_08 | C2NC-1300-DG | Lines | 6 Inch PVC Digestate Line | [11 empty] | D0-10 | 6_AC30_ED_1310_08 | [10 empty] | Digestate | PVC | 6 inch |  |  | N
6 Inch PVC Digestate Line 1320_08 | CNC2-1300-DG-6_AC30_ED_1320_08 | C2NC-1300-DG | Lines | 6 Inch PVC Digestate Line | [11 empty] | D0-10 | 6_AC30_ED_1320_08 | [10 empty] | Digestate | PVC | 6 inch |  |  | N
6 Inch PVC Digestate Line 1330_08 | CNC2-1300-DG-6_AC30_ED_1330_08 | C2NC-1300-DG | Lines | 6 Inch PVC Digestate Line | [11 empty] | D0-10 | 6_AC30_ED_1330_08 | [10 empty] | Digestate | PVC | 6 inch |  |  | N
6 Inch Carbon Steel Digestate Line 1310_08 | CNC2-1300-DG-6_AE30RT_ED_1310_08 | C2NC-1300-DG | Lines | 6 Inch Carbon Steel Digestate Line | [11 empty] | D0-4 | 6_AE30RT_ED_1310_08 | [10 empty] | Digestate | Carbon Steel | 6 inch |  |  | N
6 Inch Carbon Steel Digestate Line 1320_08 | CNC2-1300-DG-6_AE30RT_ED_1320_08 | C2NC-1300-DG | Lines | 6 Inch Carbon Steel Digestate Line | [11 empty] | D0-5 | 6_AE30RT_ED_1320_08 | [10 empty] | Digestate | Carbon Steel | 6 inch |  |  | N
6 Inch Carbon Steel Digestate Line 1330_08 | CNC2-1300-DG-6_AE30RT_ED_1330_08 | C2NC-1300-DG | Lines | 6 Inch Carbon Steel Digestate Line | [11 empty] | D0-6 | 6_AE30RT_ED_1330_08 | [10 empty] | Digestate | Carbon Steel | 6 inch |  |  | N
8 Inch PVC Digestate Line 1310_09 | CNC2-1300-DG-8_AC30_ED_1310_09 | C2NC-1300-DG | Lines | 8 Inch PVC Digestate Line | [11 empty] | D0-4 | 8_AC30_ED_1310_09 | [10 empty] | Digestate | PVC | 8 inch |  |  | N
8 Inch PVC Digestate Line 1320_09 | CNC2-1300-DG-8_AC30_ED_1320_09 | C2NC-1300-DG | Lines | 8 Inch PVC Digestate Line | [11 empty] | D0-5 | 8_AC30_ED_1320_09 | [10 empty] | Digestate | PVC | 8 inch |  |  | N
8 Inch PVC Digestate Line 1330_09 | CNC2-1300-DG-8_AC30_ED_1330_09 | C2NC-1300-DG | Lines | 8 Inch PVC Digestate Line | [11 empty] | D0-6 | 8_AC30_ED_1330_09 | [10 empty] | Digestate | PVC | 8 inch |  |  | N
8 Inch Carbon Steel Digestate Line 1310_09 | CNC2-1300-DG-8_AE30RT_ED_1310_09 | C2NC-1300-DG | Lines | 8 Inch Carbon Steel Digestate Line | [11 empty] | D0-4 | 8_AE30RT_ED_1310_09 | [10 empty] | Digestate | Carbon Steel | 8 inch |  |  | N
8 Inch Carbon Steel Digestate Line 1320_09 | CNC2-1300-DG-8_AE30RT_ED_1320_09 | C2NC-1300-DG | Lines | 8 Inch Carbon Steel Digestate Line | [11 empty] | D0-5 | 8_AE30RT_ED_1320_09 | [10 empty] | Digestate | Carbon Steel | 8 inch |  |  | N
8 Inch Carbon Steel Digestate Line 1330_09 | CNC2-1300-DG-8_AE30RT_ED_1330_09 | C2NC-1300-DG | Lines | 8 Inch Carbon Steel Digestate Line | [11 empty] | D0-6 | 8_AE30RT_ED_1330_09 | [10 empty] | Digestate | Carbon Steel | 8 inch |  |  | N
8 Inch Stainless Steel Biogas Line 1310_03 | CNC2-1300-BG-8_AS30_GB_1310_03 | C2NC-1300-BG | Lines | 8 Inch Stainless Steel Biogas Line | [11 empty] | D0-4 | 8_AS30_GB_1310_03 | [10 empty] | Biogas | Stainless Steel | 8 inch |  |  | N
8 Inch Stainless Steel Biogas Line 1310_04 | CNC2-1300-BG-8_AS30_GB_1310_04 | C2NC-1300-BG | Lines | 8 Inch Stainless Steel Biogas Line | [11 empty] | D0-4 | 8_AS30_GB_1310_04 | [10 empty] | Biogas | Stainless Steel | 8 inch |  |  | N
8 Inch Stainless Steel Biogas Line 1310_05 | CNC2-1300-BG-8_AS30_GB_1310_05 | C2NC-1300-BG | Lines | 8 Inch Stainless Steel Biogas Line | [11 empty] | D0-4 | 8_AS30_GB_1310_05 | [10 empty] | Biogas | Stainless Steel | 8 inch |  |  | N
8 Inch Stainless Steel Biogas Line 1320_03 | CNC2-1300-BG-8_AS30_GB_1320_03 | C2NC-1300-BG | Lines | 8 Inch Stainless Steel Biogas Line | [11 empty] | D0-5 | 8_AS30_GB_1320_03 | [10 empty] | Biogas | Stainless Steel | 8 inch |  |  | N
8 Inch Stainless Steel Biogas Line 1320_04 | CNC2-1300-BG-8_AS30_GB_1320_04 | C2NC-1300-BG | Lines | 8 Inch Stainless Steel Biogas Line | [11 empty] | D0-5 | 8_AS30_GB_1320_04 | [10 empty] | Biogas | Stainless Steel | 8 inch |  |  | N
8 Inch Stainless Steel Biogas Line 1320_05 | CNC2-1300-BG-8_AS30_GB_1320_05 | C2NC-1300-BG | Lines | 8 Inch Stainless Steel Biogas Line | [11 empty] | D0-5 | 8_AS30_GB_1320_05 | [10 empty] | Biogas | Stainless Steel | 8 inch |  |  | N
Digester - 1 - Membrane - Blower - Pressure Safety Valve - 01A | C2NC-1300-100-PSV_41201A | C2NC-1300-100 | Valves | Membrane Blower Pressure Regulator Valve | [11 empty] | D-04 | PSV_41201A | [21 empty] | AU |  | 10 |  |  | Manual | Pressure Regulator
8 Inch Stainless Steel Biogas Line 1330_03 | CNC2-1300-BG-8_AS30_GB_1330_03 | C2NC-1300-BG | Lines | 8 Inch Stainless Steel Biogas Line | [11 empty] | D0-6 | 8_AS30_GB_1330_03 | [10 empty] | Biogas | Stainless Steel | 8 inch |  |  | N
8 Inch Stainless Steel Biogas Line 1330_04 | CNC2-1300-BG-8_AS30_GB_1330_04 | C2NC-1300-BG | Lines | 8 Inch Stainless Steel Biogas Line | [11 empty] | D0-6 | 8_AS30_GB_1330_04 | [10 empty] | Biogas | Stainless Steel | 8 inch |  |  | N
8 Inch Stainless Steel Biogas Line 1330_05 | CNC2-1300-BG-8_AS30_GB_1330_05 | C2NC-1300-BG | Lines | 8 Inch Stainless Steel Biogas Line | [11 empty] | D0-6 | 8_AS30_GB_1330_05 | [10 empty] | Biogas | Stainless Steel | 8 inch |  |  | N
Biogas - Piping - Flow - Sensor - 41201 | C2NC-1300-BG-FE_41201 | C2NC-1300-BG | Instruments | Flow sensor associated with condensate trap - Instruments | [7 empty] | Y |  | Analog |  | D-07 | FE_41201 | [42 empty] | BG | 0 |  | Flow Sensor |  | Analog
Biogas - Piping - Flow - Indicating - Transmitter - 41203 | C2NC-1300-BG-FIT_41203 | C2NC-1300-BG | Instruments | FIT associated with condensate trap - Instruments | [7 empty] | Y |  | Analog |  | D-07 | FIT_41203 | [42 empty] | BG | 1/2" GAS-F |  | Flow Indicating Transmitter |  | Analog
FCON - Heating - Flow - Sensor - 44201A | C2NC-1300-100-FE_44201A | C2NC-1300-100 | Instruments | FE on DFS stream prior to FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | FE_44201A | [42 empty] | DFS | 0 |  | Flow Sensor |  | Analog
Digester - Feed - Pumps - Flow - Indicating - Transmitter - 41201A | C2NC-1300-100-FIT_41201A | C2NC-1300-100 | Instruments | Flow transmitter on feed line from FCON to AD - Instruments | [7 empty] | Y |  | Analog |  | D-03 | FIT_41201A | [42 empty] | DFS | 0 |  | Flow Indicating Transmitter |  | Analog
Biogas - Piping - Flow - Indicating - Transmitter - 41202A | C2NC-1300-100-FIT_41202A | C2NC-1300-100 | Instruments | FIT on AD BG line - Instruments | [7 empty] | Y |  | Analog |  | D-07 | FIT_41202A | [42 empty] | BG | 1/4" GAS-F |  | Flow Indicating Transmitter |  | Analog
Digester - Discharge - Pumps - Flow - Indicating - Transmitter - 41204A | C2NC-1300-100-FIT_41204A | C2NC-1300-100 | Instruments | Flow transmitter for discharge from AD - Instruments | [7 empty] | Y |  | Analog |  | D-10 | FIT_41204A | [42 empty] | DGT | 1/4" GAS-F |  | Flow Indicating Transmitter |  | Analog
FCON - Heating - Flow - Indicating - Transmitter - 44201A | C2NC-1300-100-FIT_44201A | C2NC-1300-100 | Instruments | FIT on DFS stream prior to FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | FIT_44201A | [42 empty] | DFS | 0 |  | Flow Indicating Transmitter |  | Analog
FCON - Heating - Flow - Indicating - Transmitter - 44202A | C2NC-1300-100-FIT_44202A | C2NC-1300-100 | Instruments | FIT on DFS stream prior to FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | FIT_44202A | [42 empty] | DFS | 0 |  | Flow Indicating Transmitter |  | Analog
Digester - 1 - Level - Transmitter - 41201A | C2NC-1300-100-LIT_41201A | C2NC-1300-100 | Instruments | LT for AD tank, linked to LE - Instruments | [7 empty] | Y |  | Analog |  | D-04 | LIT_41201A | [42 empty] | DGT | 1/2" GAS-F |  | Level Transmitter |  | Analog
Digester - 1 - Level - Indicating - Transmitter - 41202A | C2NC-1300-100-LIT_41202A | C2NC-1300-100 | Instruments | Level transmitter for AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-04 | LIT_41202A | [42 empty] | DGT | 0 |  | Level Indicating Transmitter |  | Analog
Digester - 1 - Level - Transmitter - 41203A | C2NC-1300-100-LIT_41203A | C2NC-1300-100 | Instruments | Level Transmitter for AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-04 | LIT_41203A | [42 empty] | DGT | 0 |  | Level Transmitter |  | Analog
Digester - 1 - Level - High - High - Switch - 41201A | C2NC-1300-100-LSHH_41201A | C2NC-1300-100 | Instruments | Level switch for AD tank (at top) - Instruments | [7 empty] | Y |  | Digital |  | D-04 | LSHH_41201A | [42 empty] | DGT | 0 |  | Level High High Switch |  | Digital
Digester - Feed - Pumps - Pressure - Indicator - 41201A | C2NC-1300-100-PI_41201A | C2NC-1300-100 | Instruments | PI prior to substrate pump to AD - Instruments | [7 empty] | Y |  | Analog |  | D-03 | PI_41201A | [42 empty] | DFS | 0 |  | Pressure Indicator |  | Analog
Digester - Feed - Pumps - Pressure - Indicator - 41202A | C2NC-1300-100-PI_41202A | C2NC-1300-100 | Instruments | PI on DFS stream exiting substrate pump, going to AD - Instruments | [7 empty] | Y |  | Analog |  | D-03 | PI_41202A | [42 empty] | DFS | 1 1/2" GAS-F |  | Pressure Indicator |  | Analog
Digester - 1 - Pressure - Indicator - 41203A | C2NC-1300-100-PI_41203A | C2NC-1300-100 | Instruments | PI on service box for BG line on AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-04 | PI_41203A | [42 empty] | BG | 0 |  | Pressure Indicator |  | Analog
Digester - 1 - Pressure - Indicator - 41204A | C2NC-1300-100-PI_41204A | C2NC-1300-100 | Instruments | PI on service box for BG line on AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-04 | PI_41204A | [42 empty] | BG | 0 |  | Pressure Indicator |  | Analog
Digester - 1 - Pressure - Indicator - 41205A | C2NC-1300-100-PI_41205A | C2NC-1300-100 | Instruments | PI on service box for BG line on AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-04 | PI_41205A | [42 empty] | BG | 0 |  | Pressure Indicator |  | Analog
Digester - Discharge - Pumps - Pressure - Indicator - 41206A | C2NC-1300-100-PI_41206A | C2NC-1300-100 | Instruments | Pressure indicator prior to digestate waste pump - Instruments | [7 empty] | Y |  | Analog |  | D-10 | PI_41206A | [42 empty] | DGT | 1/2" GAS-F |  | Pressure Indicator |  | Analog
Digester - Discharge - Pumps - Pressure - Indicator - 41207A | C2NC-1300-100-PI_41207A | C2NC-1300-100 | Instruments | Pressure indicator after digestate waste pump - Instruments | [7 empty] | Y |  | Analog |  | D-10 | PI_41207A | [42 empty] | DGT | 1/2" GAS-F |  | Pressure Indicator |  | Analog
FCON - Heating - Pressure - Indicator - 44201A | C2NC-1300-100-PI_44201A | C2NC-1300-100 | Instruments | Pressure indicator prior to FCON HX pump - Instruments | [7 empty] | Y |  | Analog |  | D-02 | PI_44201A | [42 empty] | DFS | 0 |  | Pressure Indicator |  | Analog
FCON - Heating - Pressure - Indicator - 44202A | C2NC-1300-100-PI_44202A | C2NC-1300-100 | Instruments | Pressure indicator after FCON HX pump - Instruments | [7 empty] | Y |  | Analog |  | D-02 | PI_44202A | [42 empty] | DFS | 0 |  | Pressure Indicator |  | Analog
FCON - Heating - Pressure - Indicator - 44203A | C2NC-1300-100-PI_44203A | C2NC-1300-100 | Instruments | Pressure indicator on HW supply for FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | PI_44203A | [42 empty] | HW | 0 |  | Pressure Indicator |  | Analog
FCON - Heating - Pressure - Indicator - 44204A | C2NC-1300-100-PI_44204A | C2NC-1300-100 | Instruments | PI on HW exiting FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | PI_44204A | [42 empty] | HW | 0 |  | Pressure Indicator |  | Analog
FCON - Heating - Pressure - Indicator - 44205A | C2NC-1300-100-PI_44205A | C2NC-1300-100 | Instruments | PI on DFS stream exiting FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | PI_44205A | [42 empty] | DFS | FLANGED DN 50 PN25/40 |  | Pressure Indicator |  | Analog
Digester - 2 - Membrane - Blower - Check Valve - 01B | C2NC-1300-200-CV_41201B | C2NC-1300-200 | Valves | Membrane Blower Check Valve | [11 empty] | D-05 | CV_41201B | [21 empty] | AU |  | 8 |  |  | Manual | Check
Digester - 1 - Pressure - Indicating - Transmitter - 41201A | C2NC-1300-100-PIT_41201A | C2NC-1300-100 | Instruments | PIT on combined BG line from service boxes exiting the AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-04 | PIT_41201A | [42 empty] | BG | 0 |  | Pressure Indicating Transmitter |  | Analog
Digester - 1 - Pressure - Indicating - Transmitter - 41202A | C2NC-1300-100-PIT_41202A | C2NC-1300-100 | Instruments | PIT in intermembrane space - Instruments | [7 empty] | Y |  | Analog |  | D-04 | PIT_41202A | [42 empty] | AU | 0 |  | Pressure Indicating Transmitter |  | Analog
Digester - Feed - Pumps - Pressure - High - Switch - 41201A | C2NC-1300-100-PSH_41201A | C2NC-1300-100 | Instruments | PSH on DFS stream exiting substrate pump, going to AD - Instruments | [7 empty] | Y |  | Digital |  | D-03 | PSH_41201A | [42 empty] | DFS | 0 |  | Pressure High Switch |  | Digital
Digester - Discharge - Pumps - Pressure - High - Switch - 41202A | C2NC-1300-100-PSH_41202A | C2NC-1300-100 | Instruments | Pressure switch after digestate waste pump - Instruments | [7 empty] | Y |  | Digital |  | D-10 | PSH_41202A | [42 empty] | DGT | 1/2" GAS-F |  | Pressure High Switch |  | Digital
FCON - Heating - Pressure - High - Switch - 44201A | C2NC-1300-100-PSH_44201A | C2NC-1300-100 | Instruments | Pressure switch after FCON HX pump - Instruments | [7 empty] | Y |  | Digital |  | D-02 | PSH_44201A | [42 empty] | DFS | 0 |  | Pressure High Switch |  | Digital
FCON - Heating - Temperature - Indicator - 44201A | C2NC-1300-100-TI_44201A | C2NC-1300-100 | Instruments | TI on HW exiting FCON HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-02 | TI_44201A | [42 empty] | HW | E+H |  | Temperature Indicator |  | Analog
Digester - 1 - Temperature - Indicating - Transmitter - 41201A | C2NC-1300-100-TIT_41201A | C2NC-1300-100 | Instruments | TIT for AD tank with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-04 | TIT_41201A | [42 empty] | DGT | 0 |  | Temperature Indicating Transmitter |  | Analog
Digester - 1 - Temperature - Transmitter - 41202A | C2NC-1300-100-TIT_41202A | C2NC-1300-100 | Instruments | TIT for AD tank with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-04 | TIT_41202A | [42 empty] | DGT | 0 |  | Temperature Transmitter |  | Analog
Digester - 2 - Antifoam - 18B | C2NC-1300-200-HV_41218B | C2NC-1300-200 | Valves | Antifoam Ball Valve | [11 empty] | D-05 | HV_41218B | [21 empty] | ADA |  | 1 |  |  | Manual | Ball
Digester - 2 - Service - Water - 19B | C2NC-1300-200-HV_41219B | C2NC-1300-200 | Valves | Service Water Knife Gate Valve | [11 empty] | D-05 | HV_41219B | [21 empty] | WU |  | 3 |  |  | Manual | Knife Gate
Digester - 2 - Sight - Glass - 20B | C2NC-1300-200-HV_41220B | C2NC-1300-200 | Valves | Sight Glass Ball Valve | [11 empty] | D-05 | HV_41220B | [21 empty] | WU |  | 0.5 |  |  | Manual | Ball
Digester - 2 - Feed - Line - 21B | C2NC-1300-200-HV_41221B | C2NC-1300-200 | Valves | Feed Line Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-05 | HV_41221B | [21 empty] | DFS | CF8M | 4 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 2 - Service - Water - 22B | C2NC-1300-200-HV_41222B | C2NC-1300-200 | Valves | Service Water Knife Gate Valve | [11 empty] | D-05 | HV_41222B | [21 empty] | SW |  | 3 |  |  | Manual | Knife Gate
Digester - 2 - Return - from - HX - 23B | C2NC-1300-200-HV_41223B | C2NC-1300-200 | Valves | Return from HX Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-05 | HV_41223B | [21 empty] | DGT | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 2 - Membrane - Blower - 24B | C2NC-1300-200-HV_41224B | C2NC-1300-200 | Valves | Membrane Blower Butterfly Valve | [11 empty] | D-05 | HV_41224B | [21 empty] | AU |  | 8 |  |  | Manual | Butterfly
Digester - 2 - Biogas - Offtake - 25B | C2NC-1300-200-HV_41225B | C2NC-1300-200 | Valves | Biogas Offtake Butterfly Valve | [11 empty] | D-05 | HV_41225B | [21 empty] | BG |  | 8 |  |  | Manual | Butterfly
Digester - 2 - Biogas - Offtake - 28B | C2NC-1300-200-HV_41228B | C2NC-1300-200 | Valves | Biogas Offtake Butterfly Valve | [11 empty] | D-05 | HV_41228B | [21 empty] | BG |  | 8 |  |  | Manual | Butterfly
Digester - 2 - Sight - Glass - 29B | C2NC-1300-200-HV_41229B | C2NC-1300-200 | Valves | Sight Glass Ball Valve Valve | [11 empty] | D-05 | HV_41229B | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Biogas - Offtake - 31B | C2NC-1300-200-HV_41231B | C2NC-1300-200 | Valves | Biogas Offtake Butterfly Valve | [11 empty] | D-05 | HV_41231B | [21 empty] | BG |  | 8 |  |  | Manual | Butterfly
Digester - 2 - Service - Water - 34B | C2NC-1300-200-HV_41234B | C2NC-1300-200 | Valves | Service Water Ball Valve Valve | [11 empty] | D-05 | HV_41234B | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Service - Water - 35B | C2NC-1300-200-HV_41235B | C2NC-1300-200 | Valves | Service Water Ball Valve Valve | [11 empty] | D-05 | HV_41235B | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Service - Water - 36B | C2NC-1300-200-HV_41236B | C2NC-1300-200 | Valves | Service Water Ball Valve Valve | [11 empty] | D-05 | HV_41236B | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Service - Water - 37B | C2NC-1300-200-HV_41237B | C2NC-1300-200 | Valves | Service Water Ball Valve Valve | [11 empty] | D-05 | HV_41237B | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Service - Water - 38B | C2NC-1300-200-HV_41238B | C2NC-1300-200 | Valves | Service Water Ball Valve Valve | [11 empty] | D-05 | HV_41238B | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Instrument - Isolation - 39B | C2NC-1300-200-HV_41239B | C2NC-1300-200 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-05 | HV_41239B | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Drain - 40B | C2NC-1300-200-HV_41240B | C2NC-1300-200 | Valves | Drain Ball Valve Valve | [11 empty] | D-05 | HV_41240B | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Biogas - Offtake - 41B | C2NC-1300-200-HV_41241B | C2NC-1300-200 | Valves | Biogas Offtake Butterfly Valve | [11 empty] | D-05 | HV_41241B | [21 empty] | BG |  | 12 |  |  | Manual | Butterfly
Digester - 2 - Discharge - 42B | C2NC-1300-200-HV_41242B | C2NC-1300-200 | Valves | Discharge Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-05 | HV_41242B | [21 empty] | DGT | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 2 - To - HX - 43B | C2NC-1300-200-HV_41243B | C2NC-1300-200 | Valves | To HX Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-05 | HV_41243B | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 2 - Spare - Nozzle - 44B | C2NC-1300-200-HV_41244B | C2NC-1300-200 | Valves | Spare Nozzle Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-05 | HV_41244B | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 2 - Drain - Valve - 45B | C2NC-1300-200-HV_41245B | C2NC-1300-200 | Valves | Drain Valve Ball Valve | [11 empty] | D-05 | HV_41245B | [21 empty] | DGT |  | 0.5 |  |  | Manual | Ball
Digester - 2 - Instrument - Isolation - 46B | C2NC-1300-200-HV_41246B | C2NC-1300-200 | Valves | Instrument Isolation Ball Valve | Orbinox | BT Series 22 | [9 empty] | D-05 | HV_41246B | [21 empty] | DGT | CF8M | 0.5 |  |  | Manual | Ball |  | ANSI Flange | EPDM
Digester - 2 - Spare - Nozzle - 47B | C2NC-1300-200-HV_41247B | C2NC-1300-200 | Valves | Spare Nozzle Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-05 | HV_41247B | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 2 - Spare - Nozzle - 48B | C2NC-1300-200-HV_41248B | C2NC-1300-200 | Valves | Spare Nozzle Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-05 | HV_41248B | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 2 - Drain - 49B | C2NC-1300-200-HV_41249B | C2NC-1300-200 | Valves | Drain Ball Valve Valve | [11 empty] | D-05 | HV_41249B | [21 empty] | BG |  | 12 |  |  | Manual | Butterfly
Digester - 2 - Drain - 50B | C2NC-1300-200-HV_41250B | C2NC-1300-200 | Valves | Drain Ball Valve Valve | [11 empty] | D-05 | HV_41250B | [21 empty] | DGT |  | 2 |  |  | Manual | Ball Valve
Digester - 2 - Instrument - Isolation - 51B | C2NC-1300-200-HV_41251B | C2NC-1300-200 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-05 | HV_41251B | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - 2 - Instrument - Isolation - 52B | C2NC-1300-200-HV_41252B | C2NC-1300-200 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-05 | HV_41252B | [21 empty] | DGT |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Drain - 53B | C2NC-1300-200-HV_41253B | C2NC-1300-200 | Valves | Drain Ball Valve Valve | [11 empty] | D-05 | HV_41253B | [21 empty] | DGT |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Biogas - from - FCON - 54B | C2NC-1300-200-HV_41254B | C2NC-1300-200 | Valves | Biogas from FCON Butterfly Valve | [11 empty] | D-07 | HV_41254B | [21 empty] | BG |  | 12 |  |  | Manual | Butterfly
Digester - 2 - Instrument - Isolation - 55B | C2NC-1300-200-HV_41255B | C2NC-1300-200 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-05 | HV_41255B | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Drain - 56B | C2NC-1300-200-HV_41256B | C2NC-1300-200 | Valves | Drain Ball Valve Valve | [11 empty] | D-05 | HV_41256B | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Instrument - Isolation - 57B | C2NC-1300-200-HV_41257B | C2NC-1300-200 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-05 | HV_41257B | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Drain - 58B | C2NC-1300-200-HV_41258B | C2NC-1300-200 | Valves | Drain Ball Valve Valve | [11 empty] | D-05 | HV_41258B | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 2 - Drain - 59B | C2NC-1300-200-HV_41259B | C2NC-1300-200 | Valves | Drain Eccentric Plug Valve | Orbinox | BT Series 22 | [9 empty] | D-10 | HV_41259B | [21 empty] | DGT | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 2 - Gas - Recirculation - 63B | C2NC-1300-200-HV_41263B | C2NC-1300-200 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-05 | HV_41263B | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 2 - Gas - Recirculation - 64B | C2NC-1300-200-HV_41264B | C2NC-1300-200 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-05 | HV_41264B | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 2 - Gas - Recirculation - 65B | C2NC-1300-200-HV_41265B | C2NC-1300-200 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-05 | HV_41265B | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 2 - Gas - Recirculation - 66B | C2NC-1300-200-HV_41266B | C2NC-1300-200 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-05 | HV_41266B | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 2 - Gas - Recirculation - 70B | C2NC-1300-200-HV_41270B | C2NC-1300-200 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-05 | HV_41270B | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 2 - Gas - Recirculation - 71B | C2NC-1300-200-HV_41271B | C2NC-1300-200 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-05 | HV_41271B | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 2 - Gas - Recirculation - 72B | C2NC-1300-200-HV_41272B | C2NC-1300-200 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-05 | HV_41272B | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 2 - Gas - Recirculation - 73B | C2NC-1300-200-HV_41273B | C2NC-1300-200 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-05 | HV_41273B | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 2 - Gas - Recirculation - 74B | C2NC-1300-200-HV_41274B | C2NC-1300-200 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-05 | HV_41274B | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
FCON - Heating - Temperature - Indicating - Transmitter - 44201A | C2NC-1300-100-TIT_44201A | C2NC-1300-100 | Instruments | Temp indicator on HW supply for FCON HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-02 | TIT_44201A | [42 empty] | HW | 0 |  | Temperature Indicating Transmitter |  | Analog
FCON - Heating - Temperature - Indicating - Transmitter - 44202A | C2NC-1300-100-TIT_44202A | C2NC-1300-100 | Instruments | TIT on DFS stream prior to FCON HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-02 | TIT_44202A | [42 empty] | DFS | 0 |  | Temperature Indicating Transmitter |  | Analog
FCON - Heating - Temperature - Indicating - Transmitter - 44203A | C2NC-1300-100-TIT_44203A | C2NC-1300-100 | Instruments | TIT on DFS stream exiting FCON HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-02 | TIT_44203A | [42 empty] | DFS | 0 |  | Temperature Indicating Transmitter |  | Analog
Digester - 1 - Temperature - Sensor - 41201A | C2NC-1300-100-TW_41201A | C2NC-1300-100 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-04 | TW_41201A | [42 empty] | DGT | 0 |  | Temperature Sensor |  | Analog
Digester - 1 - Thermowell - 41202A | C2NC-1300-100-TW_41202A | C2NC-1300-100 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-04 | TW_41202A | [42 empty] | DGT | 1 1/2" GAS-F |  | Temperature Transmitter |  | Analog
FCON - Heating - Temperature - Sensor - 44202A | C2NC-1300-100-TW_44202A | C2NC-1300-100 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-02 | TW_44202A | [42 empty] | DFS | 0 |  | Temperature Sensor |  | Analog
FCON - Heating - Temperature - Sensor - 44203A | C2NC-1300-100-TW_44203A | C2NC-1300-100 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-02 | TW_44203A | [42 empty] | DFS | 0 |  | Temperature Sensor |  | Analog
Digester - 1 - Position - Indicating - Transmitter - 41201A | C2NC-1300-100-ZIT_41201A | C2NC-1300-100 | Instruments | ZIT placed on top of AD - Instruments | [7 empty] | Y |  | Analog |  | D-04 | ZIT_41201A | [42 empty] | DGT | 0 |  | Position Indicating Transmitter |  | Analog
FCON - Heating - Flow - Sensor - 44201B | C2NC-1300-200-FE_44201B | C2NC-1300-200 | Instruments | FE on DFS stream prior to FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | FE_44201B | [42 empty] | DFS | 0 |  | Flow Sensor |  | Analog
Digester - Feed - Pumps - Flow - Indicating - Transmitter - 41201B | C2NC-1300-200-FIT_41201B | C2NC-1300-200 | Instruments | Flow transmitter on feed line from FCON to AD - Instruments | [7 empty] | Y |  | Analog |  | D-03 | FIT_41201B | [42 empty] | DFS | 0 |  | Flow Indicating Transmitter |  | Analog
Biogas - Piping - Flow - Indicating - Transmitter - 41202B | C2NC-1300-200-FIT_41202B | C2NC-1300-200 | Instruments | FIT on AD BG line - Instruments | [7 empty] | Y |  | Analog |  | D-07 | FIT_41202B | [42 empty] | BG | 1/2" GAS-F |  | Flow Indicating Transmitter |  | Analog
Digester - Discharge - Pumps - Flow - Indicating - Transmitter - 41204B | C2NC-1300-200-FIT_41204B | C2NC-1300-200 | Instruments | Flow transmitter for discharge from AD - Instruments | [7 empty] | Y |  | Analog |  | D-10 | FIT_41204B | [42 empty] | DGT | 1/4" GAS-F |  | Flow Indicating Transmitter |  | Analog
FCON - Heating - Flow - Indicating - Transmitter - 44201B | C2NC-1300-200-FIT_44201B | C2NC-1300-200 | Instruments | FIT on DFS stream prior to FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | FIT_44201B | [42 empty] | DFS | 0 |  | Flow Indicating Transmitter |  | Analog
FCON - Heating - Flow - Indicating - Transmitter - 44202B | C2NC-1300-200-FIT_44202B | C2NC-1300-200 | Instruments | FIT on DFS stream prior to FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | FIT_44202B | [42 empty] | DFS | 0 |  | Flow Indicating Transmitter |  | Analog
Digester - 2 - Level - Transmitter - 41201B | C2NC-1300-200-LIT_41201B | C2NC-1300-200 | Instruments | LT for AD tank, linked to LE - Instruments | [7 empty] | Y |  | Analog |  | D-05 | LIT_41201B | [42 empty] | DGT | 1/4" GAS-F |  | Level Transmitter |  | Analog
Digester - 2 - Level - Indicating - Transmitter - 41202B | C2NC-1300-200-LIT_41202B | C2NC-1300-200 | Instruments | Level transmitter for AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-05 | LIT_41202B | [42 empty] | DGT | 0 |  | Level Indicating Transmitter |  | Analog
Digester - 2 - Level - Transmitter - 41203B | C2NC-1300-200-LIT_41203B | C2NC-1300-200 | Instruments | Level Transmitter for AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-05 | LIT_41203B | [42 empty] | DGT | 0 |  | Level Transmitter |  | Analog
Digester - 2 - Level - High - High - Switch - 41201B | C2NC-1300-200-LSHH_41201B | C2NC-1300-200 | Instruments | Level switch for AD tank (at top) - Instruments | [7 empty] | Y |  | Digital |  | D-05 | LSHH_41201B | [42 empty] | DGT | 1 1/2" GAS-F |  | Level High High Switch |  | Digital
Digester - Feed - Pumps - Pressure - Indicator - 41201B | C2NC-1300-200-PI_41201B | C2NC-1300-200 | Instruments | PI prior to substrate pump to AD - Instruments | [7 empty] | Y |  | Analog |  | D-03 | PI_41201B | [42 empty] | DFS | 0 |  | Pressure Indicator |  | Analog
Digester - Feed - Pumps - Pressure - Indicator - 41202B | C2NC-1300-200-PI_41202B | C2NC-1300-200 | Instruments | PI on DFS stream exiting substrate pump, going to AD - Instruments | [7 empty] | Y |  | Analog |  | D-03 | PI_41202B | [42 empty] | DFS | 0 |  | Pressure Indicator |  | Analog
Digester - 2 - Pressure - Indicator - 41203B | C2NC-1300-200-PI_41203B | C2NC-1300-200 | Instruments | PI on service box for BG line on AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-05 | PI_41203B | [42 empty] | BG | 0 |  | Pressure Indicator |  | Analog
Digester - 2 - Pressure - Indicator - 41204B | C2NC-1300-200-PI_41204B | C2NC-1300-200 | Instruments | PI on service box for BG line on AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-05 | PI_41204B | [42 empty] | BG | MBA |  | Pressure Indicator |  | Analog
Digester - 2 - Pressure - Indicator - 41205B | C2NC-1300-200-PI_41205B | C2NC-1300-200 | Instruments | PI on service box for BG line on AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-05 | PI_41205B | [42 empty] | BG | 0 |  | Pressure Indicator |  | Analog
Digester - Discharge - Pumps - Pressure - Indicator - 41206B | C2NC-1300-200-PI_41206B | C2NC-1300-200 | Instruments | Pressure indicator prior to digestate waste pump - Instruments | [7 empty] | Y |  | Analog |  | D-10 | PI_41206B | [42 empty] | DGT | 1/2" GAS-F |  | Pressure Indicator |  | Analog
Digester - Discharge - Pumps - Pressure - Indicator - 41207B | C2NC-1300-200-PI_41207B | C2NC-1300-200 | Instruments | Pressure indicator after digestate waste pump - Instruments | [7 empty] | Y |  | Analog |  | D-10 | PI_41207B | [42 empty] | DGT | 1/2" GAS-F |  | Pressure Indicator |  | Analog
FCON - Heating - Pressure - Indicator - 44201B | C2NC-1300-200-PI_44201B | C2NC-1300-200 | Instruments | Pressure indicator prior to FCON HX pump - Instruments | [7 empty] | Y |  | Analog |  | D-02 | PI_44201B | [42 empty] | DFS | 0 |  | Pressure Indicator |  | Analog
FCON - Heating - Pressure - Indicator - 44202B | C2NC-1300-200-PI_44202B | C2NC-1300-200 | Instruments | Pressure indicator after FCON HX pump - Instruments | [7 empty] | Y |  | Analog |  | D-02 | PI_44202B | [42 empty] | DFS | 0 |  | Pressure Indicator |  | Analog
FCON - Heating - Pressure - Indicator - 44203B | C2NC-1300-200-PI_44203B | C2NC-1300-200 | Instruments | Pressure indicator on HW supply for FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | PI_44203B | [42 empty] | HW | 0 |  | Pressure Indicator |  | Analog
FCON - Heating - Pressure - Indicator - 44204B | C2NC-1300-200-PI_44204B | C2NC-1300-200 | Instruments | PI on HW exiting FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | PI_44204B | [42 empty] | HW | 0 |  | Pressure Indicator |  | Analog
FCON - Heating - Pressure - Indicator - 44205B | C2NC-1300-200-PI_44205B | C2NC-1300-200 | Instruments | PI on DFS stream exiting FCON HX - Instruments | [7 empty] | Y |  | Analog |  | D-02 | PI_44205B | [42 empty] | DFS | 1 1/2" GAS-F |  | Pressure Indicator |  | Analog
Digester - 2 - Pressure - Indicating - Transmitter - 41201B | C2NC-1300-200-PIT_41201B | C2NC-1300-200 | Instruments | PIT on combined BG line from service boxes exiting the AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-05 | PIT_41201B | [42 empty] | BG | 0 |  | Pressure Indicating Transmitter |  | Analog
Digester - 2 - Pressure - Indicating - Transmitter - 41202B | C2NC-1300-200-PIT_41202B | C2NC-1300-200 | Instruments | PIT in intermembrane space - Instruments | [7 empty] | Y |  | Analog |  | D-05 | PIT_41202B | [42 empty] | AU | 0 |  | Pressure Indicating Transmitter |  | Analog
Digester - Feed - Pumps - Pressure - High - Switch - 41201B | C2NC-1300-200-PSH_41201B | C2NC-1300-200 | Instruments | PSH on DFS stream exiting substrate pump, going to AD - Instruments | [7 empty] | Y |  | Digital |  | D-03 | PSH_41201B | [42 empty] | DFS | MBA |  | Pressure High Switch |  | Digital
Digester - 2 - Membrane - Blower - Pressure Safety Valve - 01B | C2NC-1300-200-PSV_41201B | C2NC-1300-200 | Valves | Membrane Blower Pressure Regulator Valve | [11 empty] | D-05 | PSV_41201B | [21 empty] | AU |  | 10 |  |  | Manual | Pressure Regulator
Digester - Discharge - Pumps - Pressure - High - Switch - 41202B | C2NC-1300-200-PSH_41202B | C2NC-1300-200 | Instruments | Pressure switch after digestate waste pump - Instruments | [7 empty] | Y |  | Digital |  | D-10 | PSH_41202B | [42 empty] | DGT | 1/2" GAS-F |  | Pressure High Switch |  | Digital
FCON - Heating - Pressure - High - Switch - 44201B | C2NC-1300-200-PSH_44201B | C2NC-1300-200 | Instruments | Pressure switch after FCON HX pump - Instruments | [7 empty] | Y |  | Digital |  | D-02 | PSH_44201B | [42 empty] | DFS | 0 |  | Pressure High Switch |  | Digital
FCON - Heating - Temperature - Indicator - 44201B | C2NC-1300-200-TI_44201B | C2NC-1300-200 | Instruments | TI on HW exiting FCON HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TI_44201B | [42 empty] | HW | 0 |  | Temperature Indicator |  | Analog
Digester - 2 - Temperature - Indicating - Transmitter - 41201B | C2NC-1300-200-TIT_41201B | C2NC-1300-200 | Instruments | TIT for AD tank with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TIT_41201B | [42 empty] | DGT | 0 |  | Temperature Indicating Transmitter |  | Analog
Digester - 2 - Temperature - Transmitter - 41202B | C2NC-1300-200-TIT_41202B | C2NC-1300-200 | Instruments | TIT for AD tank with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TIT_41202B | [42 empty] | DGT | 0 |  | Temperature Transmitter |  | Analog
FCON - Heating - Temperature - Indicating - Transmitter - 44201B | C2NC-1300-200-TIT_44201B | C2NC-1300-200 | Instruments | Temp indicator on HW supply for FCON HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TIT_44201B | [42 empty] | HW | 0 |  | Temperature Indicating Transmitter |  | Analog
FCON - Heating - Temperature - Indicating - Transmitter - 44202B | C2NC-1300-200-TIT_44202B | C2NC-1300-200 | Instruments | TIT on DFS stream prior to FCON HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TIT_44202B | [42 empty] | DFS | E+H |  | Temperature Indicating Transmitter |  | Analog
FCON - Heating - Temperature - Indicating - Transmitter - 44203B | C2NC-1300-200-TIT_44203B | C2NC-1300-200 | Instruments | TIT on DFS stream exiting FCON HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TIT_44203B | [42 empty] | DFS | 0 |  | Temperature Indicating Transmitter |  | Analog
Digester - 2 - Temperature - Sensor - 41201B | C2NC-1300-200-TW_41201B | C2NC-1300-200 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TW_41201B | [42 empty] | DGT | 1 1/2" GAS-F |  | Temperature Sensor |  | Analog
Digester - 2 - Thermowell - 41202B | C2NC-1300-200-TW_41202B | C2NC-1300-200 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TW_41202B | [42 empty] | DGT | 1 1/2" GAS-F |  | Temperature Transmitter |  | Analog
FCON - Heating - Temperature - Sensor - 44202B | C2NC-1300-200-TW_44202B | C2NC-1300-200 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TW_44202B | [42 empty] | DFS | 0 |  | Temperature Sensor |  | Analog
FCON - Heating - Temperature - Sensor - 44203B | C2NC-1300-200-TW_44203B | C2NC-1300-200 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TW_44203B | [42 empty] | DFS | 0 |  | Temperature Sensor |  | Analog
Digester - 2 - Position - Indicating - Transmitter - 41201B | C2NC-1300-200-ZIT_41201B | C2NC-1300-200 | Instruments | ZIT placed on top of AD - Instruments | [7 empty] | Y |  | Analog |  | D-06 | ZIT_41201B | [42 empty] | DGT | BIFFI |  | Position Indicating Transmitter |  | Analog
Digester - Feed - Pumps - Flow - Indicating - Transmitter - 41201C | C2NC-1300-300-FIT_41201C | C2NC-1300-300 | Instruments | Flow transmitter on feed line from FCON to AD - Instruments | [7 empty] | Y |  | Analog |  | D-06 | FIT_41201C | [42 empty] | DFS | 0 |  | Flow Indicating Transmitter |  | Analog
Biogas - Piping - Flow - Indicating - Transmitter - 41202C | C2NC-1300-300-FIT_41202C | C2NC-1300-300 | Instruments | FIT on AD BG line - Instruments | [7 empty] | Y |  | Analog |  | D-06 | FIT_41202C | [42 empty] | BG | 1/4" GAS-F |  | Flow Indicating Transmitter |  | Analog
Digester - Discharge - Pumps - Flow - Indicating - Transmitter - 41204C | C2NC-1300-300-FIT_41204C | C2NC-1300-300 | Instruments | Flow transmitter for discharge from AD - Instruments | [7 empty] | Y |  | Analog |  | D-06 | FIT_41204C | [42 empty] | DGT | 1/2" GAS-F |  | Flow Indicating Transmitter |  | Analog
Digester - 3 - Level - Transmitter - 41201C | C2NC-1300-300-LIT_41201C | C2NC-1300-300 | Instruments | LT for AD tank, linked to LE - Instruments | [7 empty] | Y |  | Analog |  | D-06 | LIT_41201C | [42 empty] | DGT | 1/4" GAS-F |  | Level Transmitter |  | Analog
Digester - 3 - Level - Indicating - Transmitter - 41202C | C2NC-1300-300-LIT_41202C | C2NC-1300-300 | Instruments | Level transmitter for AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-06 | LIT_41202C | [42 empty] | DGT | 0 |  | Level Indicating Transmitter |  | Analog
Digester - 3 - Level - Transmitter - 41203C | C2NC-1300-300-LIT_41203C | C2NC-1300-300 | Instruments | Level Transmitter for AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-06 | LIT_41203C | [42 empty] | DGT | 0 |  | Level Transmitter |  | Analog
Digester - 3 - Level - High - High - Switch - 41201C | C2NC-1300-300-LSHH_41201C | C2NC-1300-300 | Instruments | Level switch for AD tank (at top) - Instruments | [7 empty] | Y |  | Digital |  | D-06 | LSHH_41201C | [42 empty] | DGT | 1 1/2" GAS-F |  | Level High High Switch |  | Digital
Digester - Feed - Pumps - Pressure - Indicator - 41201C | C2NC-1300-300-PI_41201C | C2NC-1300-300 | Instruments | PI prior to substrate pump to AD - Instruments | [7 empty] | Y |  | Analog |  | D-03 | PI_41201C | [42 empty] | DFS | 0 |  | Pressure Indicator |  | Analog
Digester - Feed - Pumps - Pressure - Indicator - 41202C | C2NC-1300-300-PI_41202C | C2NC-1300-300 | Instruments | PI on DFS stream exiting substrate pump, going to AD - Instruments | [7 empty] | Y |  | Analog |  | D-03 | PI_41202C | [42 empty] | DFS | 0 |  | Pressure Indicator |  | Analog
Digester - 3 - Pressure - Indicator - 41203C | C2NC-1300-300-PI_41203C | C2NC-1300-300 | Instruments | PI on service box for BG line on AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-06 | PI_41203C | [42 empty] | BG | 0 |  | Pressure Indicator |  | Analog
Digester - 3 - Pressure - Indicator - 41204C | C2NC-1300-300-PI_41204C | C2NC-1300-300 | Instruments | PI on service box for BG line on AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-06 | PI_41204C | [42 empty] | BG | 0 |  | Pressure Indicator |  | Analog
Digester - 3 - Pressure - Indicator - 41205C | C2NC-1300-300-PI_41205C | C2NC-1300-300 | Instruments | PI on service box for BG line on AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-06 | PI_41205C | [42 empty] | BG | 0 |  | Pressure Indicator |  | Analog
Digester - Discharge - Pumps - Pressure - Indicator - 41206C | C2NC-1300-300-PI_41206C | C2NC-1300-300 | Instruments | Pressure indicator prior to digestate waste pump - Instruments | [7 empty] | Y |  | Analog |  | D-10 | PI_41206C | [42 empty] | DGT | 1" GAS-F |  | Pressure Indicator |  | Analog
Digester - Discharge - Pumps - Pressure - Indicator - 41207C | C2NC-1300-300-PI_41207C | C2NC-1300-300 | Instruments | Pressure indicator after digestate waste pump - Instruments | [7 empty] | Y |  | Analog |  | D-10 | PI_41207C | [42 empty] | DGT | 1/4" GAS-F |  | Pressure Indicator |  | Analog
Digester - 3 - Pressure - Indicating - Transmitter - 41201C | C2NC-1300-300-PIT_41201C | C2NC-1300-300 | Instruments | PIT on combined BG line from service boxes exiting the AD tank - Instruments | [7 empty] | Y |  | Analog |  | D-06 | PIT_41201C | [42 empty] | BG | 0 |  | Pressure Indicating Transmitter |  | Analog
Digester - 3 - Pressure - Indicating - Transmitter - 41202C | C2NC-1300-300-PIT_41202C | C2NC-1300-300 | Instruments | PIT in intermembrane space - Instruments | [7 empty] | Y |  | Analog |  | D-06 | PIT_41202C | [42 empty] | AU | 0 |  | Pressure Indicating Transmitter |  | Analog
Digester - Feed - Pumps - Pressure - High - Switch - 41201C | C2NC-1300-300-PSH_41201C | C2NC-1300-300 | Instruments | PSH on DFS stream exiting substrate pump, going to AD - Instruments | [7 empty] | Y |  | Digital |  | D-03 | PSH_41201C | [42 empty] | DFS | 1 1/2" GAS-F |  | Pressure High Switch |  | Digital
Digester - Discharge - Pumps - Pressure - High - Switch - 41202C | C2NC-1300-300-PSH_41202C | C2NC-1300-300 | Instruments | Pressure switch after digestate waste pump - Instruments | [7 empty] | Y |  | Digital |  | D-10 | PSH_41202C | [42 empty] | DGT | 1/2" GAS-F |  | Pressure High Switch |  | Digital
Digester - 3 - Temperature - Indicating - Transmitter - 41201C | C2NC-1300-300-TIT_41201C | C2NC-1300-300 | Instruments | TIT for AD tank with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TIT_41201C | [42 empty] | DGT | 1 1/2" GAS-F |  | Temperature Indicating Transmitter |  | Analog
Digester - 3 - Temperature - Transmitter - 41202C | C2NC-1300-300-TIT_41202C | C2NC-1300-300 | Instruments | TIT for AD tank with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TIT_41202C | [42 empty] | DGT | 0 |  | Temperature Transmitter |  | Analog
Digester - 3 - Temperature - Sensor - 41201C | C2NC-1300-300-TW_41201C | C2NC-1300-300 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TW_41201C | [42 empty] | DGT | 0 |  | Temperature Sensor |  | Analog
Digester - 3 - Thermowell - 41202C | C2NC-1300-300-TW_41202C | C2NC-1300-300 | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-06 | TW_41202C | [42 empty] | DGT | 1 1/2" GAS-F |  | Temperature Transmitter |  | Analog
Digester - 3 - Membrane - Blower - Check Valve - 01C | C2NC-1300-300-CV_41201C | C2NC-1300-300 | Valves | Membrane Blower Check Valve | [11 empty] | D-06 | CV_41201C | [21 empty] | AU |  | 8 |  |  | Manual | Check
Digester - 3 - Position - Indicating - Transmitter - 41201C | C2NC-1300-300-ZIT_41201C | C2NC-1300-300 | Instruments | ZIT placed on top of AD - Instruments | [7 empty] | Y |  | Analog |  | D-06 | ZIT_41201C | [42 empty] | DGT | 0 |  | Position Indicating Transmitter |  | Analog
Digester - 1 - Position - Switch - Closed - 31201 | C2NC-1300-CHEM-ZSC_31201 | C2NC-1300-CHEM | Instruments | Position switch close for antifoam solenoid - Instruments | [7 empty] | Y |  | Analog |  | D-04 | ZSC_31201 | [42 empty] | AF | 0 |  | Position Switch |  | Analog
Digester - 2 - Position - Switch - Closed - 31202 | C2NC-1300-CHEM-ZSC_31202 | C2NC-1300-CHEM | Instruments | Position switch close for antifoam solenoid - Instruments | [7 empty] | Y |  | Analog |  | D-05 | ZSC_31202 | [42 empty] | DGT | 0 |  | Position Switch |  | Analog
Digester - 3 - Position - Switch - Closed - 31203 | C2NC-1300-CHEM-ZSC_31203 | C2NC-1300-CHEM | Instruments | Position switch close for antifoam solenoid - Instruments | [7 empty] | Y |  | Analog |  | D-06 | ZSC_31203 | [42 empty] | DGT | 0 |  | Position Switch |  | Analog
FCON - Position - Switch - Closed - 31204 | C2NC-1300-CHEM-ZSC_31204 | C2NC-1300-CHEM | Instruments | Position switch close for antifoam solenoid - Instruments | [7 empty] | Y |  | Analog |  | D-01 | ZSC_31204 | [42 empty] | AF | 0 |  | Position Switch |  | Analog
Digester - 3 - Antifoam - 18C | C2NC-1300-300-HV_41218C | C2NC-1300-300 | Valves | Antifoam Ball Valve | [11 empty] | D-06 | HV_41218C | [21 empty] | ADA |  | 1 |  |  | Manual | Ball
Digester - 3 - Drain - 19C | C2NC-1300-300-HV_41219C | C2NC-1300-300 | Valves | Drain Eccentric Plug Valve | [11 empty] | D-06 | HV_41219C | [21 empty] | WU |  | 2 |  |  | Manual | Eccentric Plug
Digester - 3 - Sight - Glass - 20C | C2NC-1300-300-HV_41220C | C2NC-1300-300 | Valves | Sight Glass Ball Valve | [11 empty] | D-06 | HV_41220C | [21 empty] | WU |  | 0.5 |  |  | Manual | Ball
Digester - 3 - Feed - Line - 21C | C2NC-1300-300-HV_41221C | C2NC-1300-300 | Valves | Feed Line Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-06 | HV_41221C | [21 empty] | DFS | CF8M | 4 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 3 - Service - Water - 22C | C2NC-1300-300-HV_41222C | C2NC-1300-300 | Valves | Service Water Knife Gate Valve | [11 empty] | D-06 | HV_41222C | [21 empty] | SW |  | 3 |  |  | Manual | Knife Gate
Digester - 3 - Return - from - HX - 23C | C2NC-1300-300-HV_41223C | C2NC-1300-300 | Valves | Return from HX Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-06 | HV_41223C | [21 empty] | DGT | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 3 - Membrane - Blower - 24C | C2NC-1300-300-HV_41224C | C2NC-1300-300 | Valves | Membrane Blower Butterfly Valve | [11 empty] | D-06 | HV_41224C | [21 empty] | AU |  | 8 |  |  | Manual | Butterfly
Digester - 3 - Biogas - Offtake - 25C | C2NC-1300-300-HV_41225C | C2NC-1300-300 | Valves | Biogas Offtake Butterfly Valve | [11 empty] | D-06 | HV_41225C | [21 empty] | BG |  | 8 |  |  | Manual | Butterfly
Digester - 3 - Biogas - Offtake - 28C | C2NC-1300-300-HV_41228C | C2NC-1300-300 | Valves | Biogas Offtake Butterfly Valve | [11 empty] | D-06 | HV_41228C | [21 empty] | BG |  | 8 |  |  | Manual | Butterfly
Digester - 3 - Sight - Glass - 29C | C2NC-1300-300-HV_41229C | C2NC-1300-300 | Valves | Sight Glass Ball Valve Valve | [11 empty] | D-06 | HV_41229C | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Biogas - Offtake - 31C | C2NC-1300-300-HV_41231C | C2NC-1300-300 | Valves | Biogas Offtake Butterfly Valve | [11 empty] | D-06 | HV_41231C | [21 empty] | BG |  | 8 |  |  | Manual | Butterfly
Digester - 3 - Service - Water - 34C | C2NC-1300-300-HV_41234C | C2NC-1300-300 | Valves | Service Water Ball Valve Valve | [11 empty] | D-06 | HV_41234C | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Service - Water - 35C | C2NC-1300-300-HV_41235C | C2NC-1300-300 | Valves | Service Water Ball Valve Valve | [11 empty] | D-06 | HV_41235C | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Service - Water - 36C | C2NC-1300-300-HV_41236C | C2NC-1300-300 | Valves | Service Water Ball Valve Valve | [11 empty] | D-06 | HV_41236C | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Service - Water - 37C | C2NC-1300-300-HV_41237C | C2NC-1300-300 | Valves | Service Water Ball Valve Valve | [11 empty] | D-06 | HV_41237C | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Service - Water - 38C | C2NC-1300-300-HV_41238C | C2NC-1300-300 | Valves | Service Water Ball Valve Valve | [11 empty] | D-06 | HV_41238C | [21 empty] | SW |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Instrument - Isolation - 39C | C2NC-1300-300-HV_41239C | C2NC-1300-300 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-06 | HV_41239C | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Drain - 40C | C2NC-1300-300-HV_41240C | C2NC-1300-300 | Valves | Drain Ball Valve Valve | [11 empty] | D-06 | HV_41240C | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Discharge - 42C | C2NC-1300-300-HV_41242C | C2NC-1300-300 | Valves | Discharge Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-06 | HV_41242C | [21 empty] | DGT | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 3 - To - HX - 43C | C2NC-1300-300-HV_41243C | C2NC-1300-300 | Valves | To HX Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-06 | HV_41243C | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 3 - Drain - 44C | C2NC-1300-300-HV_41244C | C2NC-1300-300 | Valves | Drain Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-06 | HV_41244C | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 3 - Drain - Valve - 45C | C2NC-1300-300-HV_41245C | C2NC-1300-300 | Valves | Drain Valve Ball Valve | [11 empty] | D-06 | HV_41245C | [21 empty] | DGT |  | 0.5 |  |  | Manual | Ball
Digester - 3 - Instrument - Isolation - 46C | C2NC-1300-300-HV_41246C | C2NC-1300-300 | Valves | Instrument Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-06 | HV_41246C | [21 empty] | DGT | CF8M | 0.5 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 3 - Spare - Nozzle - 47C | C2NC-1300-300-HV_41247C | C2NC-1300-300 | Valves | Spare Nozzle Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-06 | HV_41247C | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 3 - Spare - Nozzle - 48C | C2NC-1300-300-HV_41248C | C2NC-1300-300 | Valves | Spare Nozzle Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-06 | HV_41248C | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - 3 - Biogas - from - AD2 - 49C | C2NC-1300-300-HV_41249C | C2NC-1300-300 | Valves | Biogas from AD2 Butterfly Valve | [11 empty] | D-06 | HV_41249C | [21 empty] | BG |  | 12 |  |  | Manual | Butterfly
Digester - 3 - Drain - 50C | C2NC-1300-300-HV_41250C | C2NC-1300-300 | Valves | Drain Ball Valve Valve | [11 empty] | D-06 | HV_41250C | [21 empty] | DGT |  | 2 |  |  | Manual | Ball Valve
Digester - 3 - Drain - 51C | C2NC-1300-300-HV_41251C | C2NC-1300-300 | Valves | Drain Ball Valve Valve | [11 empty] | D-06 | HV_41251C | [21 empty] | DGT |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Instrument - Isolation - 52C | C2NC-1300-300-HV_41252C | C2NC-1300-300 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-06 | HV_41252C | [21 empty] | DGT |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Drain - 56C | C2NC-1300-300-HV_41256C | C2NC-1300-300 | Valves | Drain Ball Valve Valve | [11 empty] | D-06 | HV_41256C | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Instrument - Isolation - 57C | C2NC-1300-300-HV_41257C | C2NC-1300-300 | Valves | Instrument Isolation Ball Valve Valve | [11 empty] | D-06 | HV_41257C | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Drain - 58C | C2NC-1300-300-HV_41258C | C2NC-1300-300 | Valves | Drain Ball Valve Valve | [11 empty] | D-06 | HV_41258C | [21 empty] | BG |  | 0.5 |  |  | Manual | Ball Valve
Digester - 3 - Gas - Recirculation - 63C | C2NC-1300-300-HV_41263C | C2NC-1300-300 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-06 | HV_41263C | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 3 - Gas - Recirculation - 64C | C2NC-1300-300-HV_41264C | C2NC-1300-300 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-06 | HV_41264C | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 3 - Gas - Recirculation - 65C | C2NC-1300-300-HV_41265C | C2NC-1300-300 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-06 | HV_41265C | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 3 - Gas - Recirculation - 66C | C2NC-1300-300-HV_41266C | C2NC-1300-300 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-06 | HV_41266C | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 3 - Gas - Recirculation - 70C | C2NC-1300-300-HV_41270C | C2NC-1300-300 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-06 | HV_41270C | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 3 - Gas - Recirculation - 71C | C2NC-1300-300-HV_41271C | C2NC-1300-300 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-06 | HV_41271C | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 3 - Gas - Recirculation - 72C | C2NC-1300-300-HV_41272C | C2NC-1300-300 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-06 | HV_41272C | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 3 - Gas - Recirculation - 73C | C2NC-1300-300-HV_41273C | C2NC-1300-300 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-06 | HV_41273C | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 3 - Gas - Recirculation - 74C | C2NC-1300-300-HV_41274C | C2NC-1300-300 | Valves | Gas Recirculation Butterfly Valve | [11 empty] | D-06 | HV_41274C | [21 empty] | BG |  | 6 |  |  | Manual | Butterfly
Digester - 1 - Position - Switch - Open - 31201 | C2NC-1300-CHEM-ZSO_31201 | C2NC-1300-CHEM | Instruments | Position switch open for antifoam solenoid - Instruments | [7 empty] | Y |  | Analog |  | D-04 | ZSO_31201 | [42 empty] | AF | 0 |  | Position Switch |  | Analog
Digester - 2 - Position - Switch - Open - 31202 | C2NC-1300-CHEM-ZSO_31202 | C2NC-1300-CHEM | Instruments | Position switch open for antifoam solenoid - Instruments | [7 empty] | Y |  | Analog |  | D-05 | ZSO_31202 | [42 empty] | DGT | 0 |  | Position Switch |  | Analog
Digester - 3 - Position - Switch - Open - 31203 | C2NC-1300-CHEM-ZSO_31203 | C2NC-1300-CHEM | Instruments | Position switch open for antifoam solenoid - Instruments | [7 empty] | Y |  | Analog |  | D-06 | ZSO_31203 | [42 empty] | DGT | 0 |  | Position Switch |  | Analog
FCON - Position - Switch - Open - 31204 | C2NC-1300-CHEM-ZSO_31204 | C2NC-1300-CHEM | Instruments | Position switch open for antifoam solenoid - Instruments | [7 empty] | Y |  | Analog |  | D-01 | ZSO_31204 | [42 empty] | AF | 0 |  | Position Switch |  | Analog
Digester - Heat - Exchangers - Flow - Sensor - 44101A | C2NC-1300-HTG-FE_44101A | C2NC-1300-HTG | Instruments | Flow sensor on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FE_44101A | [42 empty] | DGT | 1/2" GAS-F |  | Flow Sensor |  | Analog
Digester - Heat - Exchangers - Flow - Sensor - 44101B | C2NC-1300-HTG-FE_44101B | C2NC-1300-HTG | Instruments | Flow sensor on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FE_44101B | [42 empty] | DGT | 1/2" GAS-F |  | Flow Sensor |  | Analog
Digester - Heat - Exchangers - Flow - Sensor - 44101C | C2NC-1300-HTG-FE_44101C | C2NC-1300-HTG | Instruments | Flow sensor on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FE_44101C | [42 empty] | DGT | 1/2" GAS-F |  | Flow Sensor |  | Analog
Digester - Heat - Exchangers - Flow - Sensor - 44102A | C2NC-1300-HTG-FE_44102A | C2NC-1300-HTG | Instruments | Flow sensor on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FE_44102A | [42 empty] | DGT | 0 |  | Flow Sensor |  | Analog
Digester - Heat - Exchangers - Flow - Sensor - 44102B | C2NC-1300-HTG-FE_44102B | C2NC-1300-HTG | Instruments | Flow sensor on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FE_44102B | [42 empty] | DGT | 0 |  | Flow Sensor |  | Analog
Digester - Heat - Exchangers - Flow - Sensor - 44102C | C2NC-1300-HTG-FE_44102C | C2NC-1300-HTG | Instruments | Flow sensor on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FE_44102C | [42 empty] | DGT | 0 |  | Flow Sensor |  | Analog
Digester - Heat - Exchangers - Flow - Indicating - Transmitter - 44101A | C2NC-1300-HTG-FIT_44101A | C2NC-1300-HTG | Instruments | Flow transmitter on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FIT_44101A | [42 empty] | DGT | 0 |  | Flow Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Flow - Indicating - Transmitter - 44101B | C2NC-1300-HTG-FIT_44101B | C2NC-1300-HTG | Instruments | Flow transmitter on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FIT_44101B | [42 empty] | DGT | 1/2" GAS-F |  | Flow Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Flow - Indicating - Transmitter - 44101C | C2NC-1300-HTG-FIT_44101C | C2NC-1300-HTG | Instruments | Flow transmitter on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FIT_44101C | [42 empty] | DGT | 1/2" GAS-F |  | Flow Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Flow - Indicating - Transmitter - 44102A | C2NC-1300-HTG-FIT_44102A | C2NC-1300-HTG | Instruments | Flow transmitter on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FIT_44102A | [42 empty] | DGT | 0 |  | Flow Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Flow - Indicating - Transmitter - 44102B | C2NC-1300-HTG-FIT_44102B | C2NC-1300-HTG | Instruments | Flow transmitter on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FIT_44102B | [42 empty] | DGT | 0 |  | Flow Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Flow - Indicating - Transmitter - 44102C | C2NC-1300-HTG-FIT_44102C | C2NC-1300-HTG | Instruments | Flow transmitter on DGT stream to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | FIT_44102C | [42 empty] | DGT | 0 |  | Flow Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44101A | C2NC-1300-HTG-PI_44101A | C2NC-1300-HTG | Instruments | Pressure indicator prior to AD HX pump - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44101A | [42 empty] | DGT | 1/4" GAS-F |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44101B | C2NC-1300-HTG-PI_44101B | C2NC-1300-HTG | Instruments | Pressure indicator prior to AD HX pump - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44101B | [42 empty] | DGT | 1/4" GAS-F |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44101C | C2NC-1300-HTG-PI_44101C | C2NC-1300-HTG | Instruments | Pressure indicator prior to AD HX pump - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44101C | [42 empty] | DGT | 1/4" GAS-F |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44102A | C2NC-1300-HTG-PI_44102A | C2NC-1300-HTG | Instruments | Pressure indicator after AD HX pump - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44102A | [42 empty] | DGT | 0 |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44102B | C2NC-1300-HTG-PI_44102B | C2NC-1300-HTG | Instruments | Pressure indicator after AD HX pump - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44102B | [42 empty] | DGT | 0 |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44102C | C2NC-1300-HTG-PI_44102C | C2NC-1300-HTG | Instruments | Pressure indicator after AD HX pump - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44102C | [42 empty] | DGT | 0 |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44103A | C2NC-1300-HTG-PI_44103A | C2NC-1300-HTG | Instruments | Pressure transmitter on HW supply to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44103A | [42 empty] | HW | 0 |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44103B | C2NC-1300-HTG-PI_44103B | C2NC-1300-HTG | Instruments | Pressure transmitter on HW supply to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44103B | [42 empty] | HW | 1/2" GAS-F |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44103C | C2NC-1300-HTG-PI_44103C | C2NC-1300-HTG | Instruments | Pressure transmitter on HW supply to AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44103C | [42 empty] | HW | 0 |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44104A | C2NC-1300-HTG-PI_44104A | C2NC-1300-HTG | Instruments | Pressure indicator on HW exiting AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44104A | [42 empty] | HW | 1/2" GAS-F |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44104B | C2NC-1300-HTG-PI_44104B | C2NC-1300-HTG | Instruments | Pressure indicator on HW exiting AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44104B | [42 empty] | HW | 1/2" GAS-F |  | Pressure Indicator |  | Analog
Digester - 3 - Membrane - Blower - Pressure Safety Valve - 01C | C2NC-1300-300-PSV_41201C | C2NC-1300-300 | Valves | Membrane Blower Pressure Regulator Valve | [11 empty] | D-06 | PSV_41201C | [21 empty] | AU |  | 10 |  |  | Manual | Pressure Regulator
Digester - Heat - Exchangers - Pressure - Indicator - 44104C | C2NC-1300-HTG-PI_44104C | C2NC-1300-HTG | Instruments | Pressure indicator on HW exiting AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44104C | [42 empty] | HW | 1/2" GAS-F |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44105A | C2NC-1300-HTG-PI_44105A | C2NC-1300-HTG | Instruments | Pressure indicator on DGT stream exiting AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44105A | [42 empty] | DGT | 1/2" GAS-F |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44105B | C2NC-1300-HTG-PI_44105B | C2NC-1300-HTG | Instruments | Pressure indicator on DGT stream exiting AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44105B | [42 empty] | DGT | 1/2" GAS-F |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - Indicator - 44105C | C2NC-1300-HTG-PI_44105C | C2NC-1300-HTG | Instruments | Pressure indicator on DGT stream exiting AD HX - Instruments | [7 empty] | Y |  | Analog |  | D-09 | PI_44105C | [42 empty] | DGT | 1/2" GAS-F |  | Pressure Indicator |  | Analog
Digester - Heat - Exchangers - Pressure - High - Switch - 44101A | C2NC-1300-HTG-PSH_44101A | C2NC-1300-HTG | Instruments | Pressure switch after AD HX pump - Instruments | [7 empty] | Y |  | Digital |  | D-09 | PSH_44101A | [42 empty] | DGT | 1/2" GAS-F |  | Pressure High Switch |  | Digital
Digester - Heat - Exchangers - Pressure - High - Switch - 44101B | C2NC-1300-HTG-PSH_44101B | C2NC-1300-HTG | Instruments | Pressure switch after AD HX pump - Instruments | [7 empty] | Y |  | Digital |  | D-09 | PSH_44101B | [42 empty] | DGT | 1/4" GAS-F |  | Pressure High Switch |  | Digital
Digester - Heat - Exchangers - Pressure - High - Switch - 44101C | C2NC-1300-HTG-PSH_44101C | C2NC-1300-HTG | Instruments | Pressure switch after AD HX pump - Instruments | [7 empty] | Y |  | Digital |  | D-09 | PSH_44101C | [42 empty] | DGT | 0 |  | Pressure High Switch |  | Digital
Digester - Heat - Exchangers - Temperature - Indicator - 44101A | C2NC-1300-HTG-TI_44101A | C2NC-1300-HTG | Instruments | Temp indicator on HW exiting AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TI_44101A | [42 empty] | HW | 0 |  | Temperature Indicator |  | Analog
Digester - Heat - Exchangers - Temperature - Indicator - 44101B | C2NC-1300-HTG-TI_44101B | C2NC-1300-HTG | Instruments | Temp indicator on HW exiting AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TI_44101B | [42 empty] | HW | 0 |  | Temperature Indicator |  | Analog
Digester - Heat - Exchangers - Temperature - Indicator - 44101C | C2NC-1300-HTG-TI_44101C | C2NC-1300-HTG | Instruments | Temp indicator on HW exiting AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TI_44101C | [42 empty] | HW | 1/2" GAS-F |  | Temperature Indicator |  | Analog
Digester - Heat - Exchangers - Temperature - Indicating - Transmitter - 44101A | C2NC-1300-HTG-TIT_44101A | C2NC-1300-HTG | Instruments | Temperature transmitter on HW supply to AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TIT_44101A | [42 empty] | HW | 1/2" GAS-F |  | Temperature Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Temperature - Indicating - Transmitter - 44101B | C2NC-1300-HTG-TIT_44101B | C2NC-1300-HTG | Instruments | Temperature transmitter on HW supply to AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TIT_44101B | [42 empty] | HW | 1/2" GAS-F |  | Temperature Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Temperature - Indicating - Transmitter - 44101C | C2NC-1300-HTG-TIT_44101C | C2NC-1300-HTG | Instruments | Temperature transmitter on HW supply to AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TIT_44101C | [42 empty] | HW | FLANGED DN 40 PN 10 |  | Temperature Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Temperature - Indicating - Transmitter - 44102A | C2NC-1300-HTG-TIT_44102A | C2NC-1300-HTG | Instruments | Temp transmitter on DGT stream to AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TIT_44102A | [42 empty] | DGT | 1/2" GAS-F |  | Temperature Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Temperature - Indicating - Transmitter - 44102B | C2NC-1300-HTG-TIT_44102B | C2NC-1300-HTG | Instruments | Temp transmitter on DGT stream to AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TIT_44102B | [42 empty] | DGT | 1/2" GAS-F |  | Temperature Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Temperature - Indicating - Transmitter - 44102C | C2NC-1300-HTG-TIT_44102C | C2NC-1300-HTG | Instruments | Temp transmitter on DGT stream to AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TIT_44102C | [42 empty] | DGT | 1/2" GAS-F |  | Temperature Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Temperature - Indicating - Transmitter - 44103A | C2NC-1300-HTG-TIT_44103A | C2NC-1300-HTG | Instruments | Temp transmitter on DGT stream exiting AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TIT_44103A | [42 empty] | DGT | 1/2" GAS-F |  | Temperature Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Temperature - Indicating - Transmitter - 44103B | C2NC-1300-HTG-TIT_44103B | C2NC-1300-HTG | Instruments | Temp transmitter on DGT stream exiting AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TIT_44103B | [42 empty] | DGT | 1/2" GAS-F |  | Temperature Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Temperature - Indicating - Transmitter - 44103C | C2NC-1300-HTG-TIT_44103C | C2NC-1300-HTG | Instruments | Temp transmitter on DGT stream exiting AD HX with thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TIT_44103C | [42 empty] | DGT | 1/2" GAS-F |  | Temperature Indicating Transmitter |  | Analog
Digester - Heat - Exchangers - Thermowell - 44102A | C2NC-1300-HTG-TW_44102A | C2NC-1300-HTG | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TW_44102A | [42 empty] | DGT | 1/2" GAS-F |  | Thermowell |  | Analog
Digester - Heat - Exchangers - Thermowell - 44102B | C2NC-1300-HTG-TW_44102B | C2NC-1300-HTG | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TW_44102B | [42 empty] | DGT | 1/2" GAS-F |  | Thermowell |  | Analog
Digester - Heat - Exchangers - Thermowell - 44102C | C2NC-1300-HTG-TW_44102C | C2NC-1300-HTG | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TW_44102C | [42 empty] | DGT | 0 |  | Thermowell |  | Analog
Digester - Heat - Exchangers - Thermowell - 44103A | C2NC-1300-HTG-TW_44103A | C2NC-1300-HTG | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TW_44103A | [42 empty] | DGT | 1" GAS-F |  | Thermowell |  | Analog
Digester - Heat - Exchangers - Thermowell - 44103B | C2NC-1300-HTG-TW_44103B | C2NC-1300-HTG | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TW_44103B | [42 empty] | DGT | 1" GAS-F |  | Thermowell |  | Analog
Digester - Heat - Exchangers - Thermowell - 44103C | C2NC-1300-HTG-TW_44103C | C2NC-1300-HTG | Instruments | Thermowell - Instruments | [7 empty] | Y |  | Analog |  | D-09 | TW_44103C | [42 empty] | DGT | 1/2" GAS-F |  | Thermowell |  | Analog
Sodium Hydroxide - Check Valve - 01 | C2NC-1300-CHEM-CV_31101 | C2NC-1300-CHEM | Valves | Check Valve | [11 empty] | D-08 | CV_31101 | [21 empty] | ADA |  | 25DN |  |  | Manual | Check
Sodium Hypochlorite - Dosing - Check Valve - 01 | C2NC-1300-CHEM-CV_31201 | C2NC-1300-CHEM | Valves | Antifoam Dosing Check Valve | [11 empty] | D-08 | CV_31201 | [21 empty] | AF |  | 1 |  |  | Manual | Check
Sodium Hydroxide - Ball Valve - 01 | C2NC-1300-CHEM-HV_31101 | C2NC-1300-CHEM | Valves | Ball Valve | [11 empty] | D-08 | HV_31101 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Sodium Hydroxide - Ball Valve - 02 | C2NC-1300-CHEM-HV_31102 | C2NC-1300-CHEM | Valves | Ball Valve | [11 empty] | D-08 | HV_31102 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Sodium Hypochlorite - Ball Valve - 01 | C2NC-1300-CHEM-HV_31201 | C2NC-1300-CHEM | Valves | Ball Valve | [11 empty] | D-08 | HV_31201 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Sodium Hypochlorite - Dosing - Ball Valve - 02 | C2NC-1300-CHEM-HV_31202 | C2NC-1300-CHEM | Valves | Antifoam Dosing Ball Valve | [11 empty] | D-08 | HV_31202 | [21 empty] | AF |  | 1 |  |  | Manual | Ball
Sodium Hypochlorite - Ball Valve - 03 | C2NC-1300-CHEM-HV_31203 | C2NC-1300-CHEM | Valves | Ball Valve | [11 empty] | D-08 | HV_31203 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Sodium Hypochlorite - Ball Valve - 04 | C2NC-1300-CHEM-HV_31204 | C2NC-1300-CHEM | Valves | Ball Valve | [11 empty] | D-08 | HV_31204 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Sodium Hypochlorite - Ball Valve - 05 | C2NC-1300-CHEM-HV_31205 | C2NC-1300-CHEM | Valves | Ball Valve | [11 empty] | D-08 | HV_31205 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Sodium Hypochlorite - Ball Valve - 06 | C2NC-1300-CHEM-HV_31206 | C2NC-1300-CHEM | Valves | Ball Valve | [11 empty] | D-08 | HV_31206 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Digester - Feed - Pumps - Valve - 02 | C2NC-1300-FD-HV_41202 | C2NC-1300-FD | Valves | Knife Gate Valve | [11 empty] | D-03 | HV_41202 | [21 empty] | DFS |  | 150DN |  |  | Manual | Knife Gate
Digester - Feed - Pumps - Pump - Isolation - 03A | C2NC-1300-FD-HV_41203A | C2NC-1300-FD | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-03 | HV_41203A | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Feed - Pumps - Pump - Isolation - 03B | C2NC-1300-FD-HV_41203B | C2NC-1300-FD | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-03 | HV_41203B | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Feed - Pumps - Pump - Isolation - 03C | C2NC-1300-FD-HV_41203C | C2NC-1300-FD | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-03 | HV_41203C | [21 empty] | DFS | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Feed - Pumps - Drain - Valve - 04A | C2NC-1300-FD-HV_41204A | C2NC-1300-FD | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-03 | HV_41204A | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
Digester - Feed - Pumps - Drain - Valve - 04B | C2NC-1300-FD-HV_41204B | C2NC-1300-FD | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-03 | HV_41204B | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
Digester - Feed - Pumps - Drain - Valve - 04C | C2NC-1300-FD-HV_41204C | C2NC-1300-FD | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-03 | HV_41204C | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
Digester - Feed - Pumps - Drain - Valve - 05A | C2NC-1300-FD-HV_41205A | C2NC-1300-FD | Valves | Drain Valve Ball Valve | [11 empty] | D-03 | HV_41205A | [21 empty] | DFS |  | 1 |  |  | Manual | Ball
Digester - Feed - Pumps - Drain - Valve - 05B | C2NC-1300-FD-HV_41205B | C2NC-1300-FD | Valves | Drain Valve Ball Valve | [11 empty] | D-03 | HV_41205B | [21 empty] | DFS |  | 1 |  |  | Manual | Ball
Digester - Feed - Pumps - Drain - Valve - 05C | C2NC-1300-FD-HV_41205C | C2NC-1300-FD | Valves | Drain Valve Ball Valve | [11 empty] | D-03 | HV_41205C | [21 empty] | DFS |  | 1 |  |  | Manual | Ball
Digester - Feed - Pumps - Pump - Isolation - 11A | C2NC-1300-FD-HV_41211A | C2NC-1300-FD | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-03 | HV_41211A | [21 empty] | DFS | CF8M | 4 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Feed - Pumps - Pump - Isolation - 11B | C2NC-1300-FD-HV_41211B | C2NC-1300-FD | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-03 | HV_41211B | [21 empty] | DFS | CF8M | 4 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Feed - Pumps - Pump - Isolation - 11C | C2NC-1300-FD-HV_41211C | C2NC-1300-FD | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-03 | HV_41211C | [21 empty] | DFS | CF8M | 4 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Feed - Pumps - Drain - Valve - 12A | C2NC-1300-FD-HV_41212A | C2NC-1300-FD | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-03 | HV_41212A | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
Digester - Feed - Pumps - Drain - Valve - 12B | C2NC-1300-FD-HV_41212B | C2NC-1300-FD | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-03 | HV_41212B | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
Digester - Feed - Pumps - Drain - Valve - 12C | C2NC-1300-FD-HV_41212C | C2NC-1300-FD | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-03 | HV_41212C | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
Digester - Feed - Pumps - Drain - Valve - 13A | C2NC-1300-FD-HV_41213A | C2NC-1300-FD | Valves | Drain Valve Ball Valve | [11 empty] | D-03 | HV_41213A | [21 empty] | DFS |  | 1 |  |  | Manual | Ball
Digester - Feed - Pumps - Drain - Valve - 13B | C2NC-1300-FD-HV_41213B | C2NC-1300-FD | Valves | Drain Valve Ball Valve | [11 empty] | D-03 | HV_41213B | [21 empty] | DFS |  | 1 |  |  | Manual | Ball
Digester - Feed - Pumps - Drain - Valve - 13C | C2NC-1300-FD-HV_41213C | C2NC-1300-FD | Valves | Drain Valve Ball Valve | [11 empty] | D-03 | HV_41213C | [21 empty] | DFS |  | 1 |  |  | Manual | Ball
Digester - Feed - Pumps - Drain - Valve - 14A | C2NC-1300-FD-HV_41214A | C2NC-1300-FD | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-03 | HV_41214A | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
Digester - Feed - Pumps - Drain - Valve - 14B | C2NC-1300-FD-HV_41214B | C2NC-1300-FD | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-03 | HV_41214B | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
Digester - Feed - Pumps - Drain - Valve - 14C | C2NC-1300-FD-HV_41214C | C2NC-1300-FD | Valves | Drain Valve Eccentric Plug Valve | [11 empty] | D-03 | HV_41214C | [21 empty] | DFS |  | 2 |  |  | Manual | Eccentric Plug
Digester - Feed - Pumps - Valve - 17 | C2NC-1300-FD-HV_41217 | C2NC-1300-FD | Valves | Ball Valve | [11 empty] | D-03 | HV_41217 | [21 empty] | DFS |  | 80DN |  |  | Manual | Ball
Digester - #1 - Blower - #1 | C2NC-1300-100-BL_41201A | C2NC-1300-100 | Equipment | Blower to maintain pressure in gas holder cover | Cincinnati Fan | PB-15A | [5 empty] | P |  |  |  | D-04 | BL_41201A |  | 480 | 15A | 5 HP | Air | CI Frame |  |  | Blower
Digester - #1 - Blower - #2 | C2NC-1300-100-BL_41202A | C2NC-1300-100 | Equipment | Blower to maintain pressure in gas holder cover | Cincinnati Fan | PB-15A | [5 empty] | P |  |  |  | D-04 | BL_41202A |  | 480 | 15A | 5 HP | Air | CI Frame |  |  | Blower
Digester - #1 - Mixer - #1 | C2NC-1300-100-MX_41201A | C2NC-1300-100 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSM_XP 940 | [5 empty] | P |  |  |  | D-04 | MX_41201A |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #1 - Mixer - #2 | C2NC-1300-100-MX_41202A | C2NC-1300-100 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSM_XP 940 | [5 empty] | P |  |  |  | D-04 | MX_41202A |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #1 - Mixer - #3 | C2NC-1300-100-MX_41203A | C2NC-1300-100 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-04 | MX_41203A |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #1 - Mixer - #4 | C2NC-1300-100-MX_41204A | C2NC-1300-100 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-04 | MX_41204A |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #1 - Mixer - #5 | C2NC-1300-100-MX_41205A | C2NC-1300-100 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-04 | MX_41205A |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #1 - Mixer - #6 | C2NC-1300-100-MX_41206A | C2NC-1300-100 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-04 | MX_41206A |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #1 - Mixer - #7 | C2NC-1300-100-MX_41207A | C2NC-1300-100 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-04 | MX_41207A |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - Heat - Exchangers - Nutrient - Check - 04 | C2NC-1300-HTG-CV_31104 | C2NC-1300-HTG | Valves | Nutrient Check Ball Valve | [11 empty] | D-09 | CV_31104 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Digester - Heat - Exchangers - Nutrient - Check - 05 | C2NC-1300-HTG-CV_31105 | C2NC-1300-HTG | Valves | Nutrient Check Ball Valve | [11 empty] | D-09 | CV_31105 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Digester - Heat - Exchangers - Nutrient - Check - 06 | C2NC-1300-HTG-CV_31106 | C2NC-1300-HTG | Valves | Nutrient Check Ball Valve | [11 empty] | D-09 | CV_31106 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Digester - #1 - Mixer - #8 | C2NC-1300-100-MX_41208A | C2NC-1300-100 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-04 | MX_41208A |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #1 - Mixer - #9 | C2NC-1300-100-MX_41209A | C2NC-1300-100 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-04 | MX_41209A |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Substrate - Pump - to - Digester - #1 | C2NC-1300-100-P_41201A | C2NC-1300-100 | Equipment | Pump from FCON to AD #1 | Boerger | CL 260 | [5 empty] | P |  |  |  | D-03 | P_41201A |  | 480 |  | 20 HP |  |  |  |  | Pump
Digestate - Discharge - Pump - #1 | C2NC-1300-100-P_41202A | C2NC-1300-100 | Equipment | Pump to downstream dewatering | Boerger | CL 260 | [5 empty] | P |  |  |  | D-10 | P_41202A |  | 480 |  | 15 HP |  |  |  |  | Pump
Digester - #1 - Mixer - Service - Box - #1 | C2NC-1300-100-SB_41201A | C2NC-1300-100 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-04 | SB_41201A | [8 empty] | Service Box
Digester - #1 - Mixer - Service - Box - #2 | C2NC-1300-100-SB_41202A | C2NC-1300-100 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-04 | SB_41202A | [8 empty] | Service Box
Digester - #1 - Mixer - Service - Box - #3 | C2NC-1300-100-SB_41203A | C2NC-1300-100 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-04 | SB_41203A | [8 empty] | Service Box
Digester - #1 - Mixer - Service - Box - #4 | C2NC-1300-100-SB_41204A | C2NC-1300-100 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-04 | SB_41204A | [8 empty] | Service Box
Digester - #1 - Mixer - Service - Box - #5 | C2NC-1300-100-SB_41205A | C2NC-1300-100 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-04 | SB_41205A | [8 empty] | Service Box
Digester - #1 - Mixer - Service - Box - #6 | C2NC-1300-100-SB_41206A | C2NC-1300-100 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-04 | SB_41206A | [8 empty] | Service Box
Digester - #1 - Mixer - Service - Box - #7 | C2NC-1300-100-SB_41207A | C2NC-1300-100 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-04 | SB_41207A | [8 empty] | Service Box
Digester - #1 - Mixer - Service - Box - #8 | C2NC-1300-100-SB_41208A | C2NC-1300-100 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-04 | SB_41208A | [8 empty] | Service Box
Digester - #1 - Mixer - Service - Box - #9 | C2NC-1300-100-SB_41209A | C2NC-1300-100 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-04 | SB_41209A | [8 empty] | Service Box
Digester - #1 - Mixer - Auto-Positioner - #1 | C2NC-1300-100-SB_M_41201A | C2NC-1300-100 | Equipment | Digester - #1 - Mixer - Auto-Positioner - #1 | AUMA | [6 empty] | Y |  |  |  | D-08 | SB_M_41201A | [8 empty] | Electric Positioner
Digester - #1 - Mixer - Auto-Positioner - #2 | C2NC-1300-100-SB_M_41202A | C2NC-1300-100 | Equipment | Digester - #1 - Mixer - Auto-Positioner - #2 | AUMA | [6 empty] | Y |  |  |  | D-08 | SB_M_41202A | [8 empty] | Electric Positioner
Digester - Heat - Exchangers - Nutrient - Isolation - 04 | C2NC-1300-HTG-HV_31104 | C2NC-1300-HTG | Valves | Nutrient Isolation Ball Valve | [11 empty] | D-09 | HV_31104 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Digester - Heat - Exchangers - Nutrient - Isolation - 05 | C2NC-1300-HTG-HV_31105 | C2NC-1300-HTG | Valves | Nutrient Isolation Ball Valve | [11 empty] | D-09 | HV_31105 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Digester - Heat - Exchangers - Nutrient - Isolation - 06 | C2NC-1300-HTG-HV_31106 | C2NC-1300-HTG | Valves | Nutrient Isolation Ball Valve | [11 empty] | D-09 | HV_31106 | [21 empty] | ADA |  | 25DN |  |  | Manual | Ball
Digester - Heat - Exchangers - Valve - 01 | C2NC-1300-HTG-HV_44101 | C2NC-1300-HTG | Valves | Knife Gate Valve | [11 empty] | D-09 | HV_44101 | [21 empty] | DGT |  | 200DN |  |  | Manual | Knife Gate
Digester - Heat - Exchangers - Valve - 02 | C2NC-1300-HTG-HV_44102 | C2NC-1300-HTG | Valves | Knife Gate Valve | [11 empty] | D-09 | HV_44102 | [21 empty] | DGT |  | 200DN |  |  | Manual | Knife Gate
Digester - Heat - Exchangers - Pump/HX - Isolation - 03A | C2NC-1300-HTG-HV_44103A | C2NC-1300-HTG | Valves | Pump/HX Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-09 | HV_44103A | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Heat - Exchangers - Pump/HX - Isolation - 03B | C2NC-1300-HTG-HV_44103B | C2NC-1300-HTG | Valves | Pump/HX Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-09 | HV_44103B | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Heat - Exchangers - Pump/HX - Isolation - 03C | C2NC-1300-HTG-HV_44103C | C2NC-1300-HTG | Valves | Pump/HX Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-09 | HV_44103C | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Heat - Exchangers - Drain - 04A | C2NC-1300-HTG-HV_44104A | C2NC-1300-HTG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-09 | HV_44104A | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Heat - Exchangers - Drain - 04B | C2NC-1300-HTG-HV_44104B | C2NC-1300-HTG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-09 | HV_44104B | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Heat - Exchangers - Drain - 04C | C2NC-1300-HTG-HV_44104C | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44104C | [21 empty] | DGT |  | 2 |  |  | Manual | Ball
Digester - Heat - Exchangers - Pump/HX - Isolation - 07A | C2NC-1300-HTG-HV_44107A | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44107A | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Pump/HX - Isolation - 07B | C2NC-1300-HTG-HV_44107B | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44107B | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Pump/HX - Isolation - 07C | C2NC-1300-HTG-HV_44107C | C2NC-1300-HTG | Valves | Pump/HX Isolation Ball Valve | [11 empty] | D-09 | HV_44107C | [21 empty] | HW |  | 6 |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 08A | C2NC-1300-HTG-HV_44108A | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44108A | [21 empty] | HW |  |  |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 08B | C2NC-1300-HTG-HV_44108B | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44108B | [21 empty] | HW |  |  |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 08C | C2NC-1300-HTG-HV_44108C | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44108C | [21 empty] | HW |  |  |  |  | Manual | Ball
Digester - Heat - Exchangers - Instrument - Isolation - 10A | C2NC-1300-HTG-HV_44110A | C2NC-1300-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-09 | HV_44110A | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Instrument - Isolation - 10B | C2NC-1300-HTG-HV_44110B | C2NC-1300-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-09 | HV_44110B | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Instrument - Isolation - 10C | C2NC-1300-HTG-HV_44110C | C2NC-1300-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-09 | HV_44110C | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 11A | C2NC-1300-HTG-HV_44111A | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44111A | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 11B | C2NC-1300-HTG-HV_44111B | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44111B | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 11C | C2NC-1300-HTG-HV_44111C | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44111C | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Instrument - Isolation - 12A | C2NC-1300-HTG-HV_44112A | C2NC-1300-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-09 | HV_44112A | [21 empty] | HW |  |  |  |  | Manual | Ball
Digester - Heat - Exchangers - Instrument - Isolation - 12B | C2NC-1300-HTG-HV_44112B | C2NC-1300-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-09 | HV_44112B | [21 empty] | HW |  |  |  |  | Manual | Ball
Digester - Heat - Exchangers - Instrument - Isolation - 12C | C2NC-1300-HTG-HV_44112C | C2NC-1300-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-09 | HV_44112C | [21 empty] | HW |  |  |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 13A | C2NC-1300-HTG-HV_44113A | C2NC-1300-HTG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-09 | HV_44113A | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Heat - Exchangers - Drain - 13B | C2NC-1300-HTG-HV_44113B | C2NC-1300-HTG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-09 | HV_44113B | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Heat - Exchangers - Drain - 13C | C2NC-1300-HTG-HV_44113C | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44113C | [21 empty] | DGT |  | 2 |  |  | Manual | Ball
Digester - Heat - Exchangers - Instrument - Isolation - 14A | C2NC-1300-HTG-HV_44114A | C2NC-1300-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-09 | HV_44114A | [21 empty] | HW |  |  |  |  | Manual | Ball
Digester - Heat - Exchangers - Instrument - Isolation - 14B | C2NC-1300-HTG-HV_44114B | C2NC-1300-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-09 | HV_44114B | [21 empty] | HW |  |  |  |  | Manual | Ball
Digester - Heat - Exchangers - Instrument - Isolation - 14C | C2NC-1300-HTG-HV_44114C | C2NC-1300-HTG | Valves | Instrument Isolation Ball Valve | [11 empty] | D-09 | HV_44114C | [21 empty] | HW |  |  |  |  | Manual | Ball
Digester - Heat - Exchangers - Pump/HX - Isolation - 15A | C2NC-1300-HTG-HV_44115A | C2NC-1300-HTG | Valves | Pump/HX Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-09 | HV_44115A | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Heat - Exchangers - Pump/HX - Isolation - 15B | C2NC-1300-HTG-HV_44115B | C2NC-1300-HTG | Valves | Pump/HX Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-09 | HV_44115B | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Heat - Exchangers - Pump/HX - Isolation - 15C | C2NC-1300-HTG-HV_44115C | C2NC-1300-HTG | Valves | Pump/HX Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-09 | HV_44115C | [21 empty] | DGT | CF8M | 8 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Heat - Exchangers - Pump/HX - Isolation - 17A | C2NC-1300-HTG-HV_44117A | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44117A | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Pump/HX - Isolation - 17B | C2NC-1300-HTG-HV_44117B | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44117B | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Pump/HX - Isolation - 17C | C2NC-1300-HTG-HV_44117C | C2NC-1300-HTG | Valves | Pump/HX Isolation Ball Valve | [11 empty] | D-09 | HV_44117C | [21 empty] | HW |  | 6 |  |  | Manual | Ball
Digester - Heat - Exchangers - Pump/HX - Isolation - 18A | C2NC-1300-HTG-HV_44118A | C2NC-1300-HTG | Valves | Pump/HX Isolation Ball Valve | Orbinox | BT Series 22 | [9 empty] | D-09 | HV_44118A | [21 empty] | DGT | CF8M | 1 |  |  | Manual | Ball |  | ANSI Flange | EPDM
Digester - Heat - Exchangers - Drain - 18B | C2NC-1300-HTG-HV_44118B | C2NC-1300-HTG | Valves | Drain Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-09 | HV_44118B | [21 empty] | DGT | CF8M | 1 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Heat - Exchangers - Drain - 18C | C2NC-1300-HTG-HV_44118C | C2NC-1300-HTG | Valves | Drain Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-09 | HV_44118C | [21 empty] | DGT | CF8M | 1 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Heat - Exchangers - Pump/HX - Isolation - 19A | C2NC-1300-HTG-HV_44119A | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44119A | [21 empty] | DGT |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Pump/HX - Isolation - 19B | C2NC-1300-HTG-HV_44119B | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44119B | [21 empty] | DGT |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Pump/HX - Isolation - 19C | C2NC-1300-HTG-HV_44119C | C2NC-1300-HTG | Valves | Pump/HX Isolation Ball Valve | [11 empty] | D-09 | HV_44119C | [21 empty] | DGT |  | 6 |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 20A | C2NC-1300-HTG-HV_44120A | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44120A | [21 empty] | HW |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 20B | C2NC-1300-HTG-HV_44120B | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44120B | [21 empty] | HW |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 20C | C2NC-1300-HTG-HV_44120C | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44120C | [21 empty] | HW |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Pump/HX - Isolation - 21A | C2NC-1300-HTG-HV_44121A | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44121A | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Pump/HX - Isolation - 21B | C2NC-1300-HTG-HV_44121B | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44121B | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Pump/HX - Isolation - 21C | C2NC-1300-HTG-HV_44121C | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44121C | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Valve - 22 | C2NC-1300-HTG-HV_44122 | C2NC-1300-HTG | Valves | Knife Gate Valve | [11 empty] | D-09 | HV_44122 | [21 empty] | DGT |  | 100DN |  |  | Manual | Knife Gate
Digester - Heat - Exchangers - Pump/HX - Isolation - 22A | C2NC-1300-HTG-HV_44122A | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44122A | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Pump/HX - Isolation - 22B | C2NC-1300-HTG-HV_44122B | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44122B | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Pump/HX - Isolation - 22C | C2NC-1300-HTG-HV_44122C | C2NC-1300-HTG | Valves | Pump/HX Isolation Butterfly Valve | [11 empty] | D-09 | HV_44122C | [21 empty] | HW |  | 6 |  |  | Manual | Butterfly
Digester - Heat - Exchangers - Valve - 23 | C2NC-1300-HTG-HV_44123 | C2NC-1300-HTG | Valves | Knife Gate Valve | [11 empty] | D-09 | HV_44123 | [21 empty] | DGT |  | 100DN |  |  | Manual | Knife Gate
Digester - Heat - Exchangers - Drain - 23A | C2NC-1300-HTG-HV_44123A | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44123A | [21 empty] | HW |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 23B | C2NC-1300-HTG-HV_44123B | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44123B | [21 empty] | HW |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 23C | C2NC-1300-HTG-HV_44123C | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44123C | [21 empty] | HW |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Pump/HX - Isolation - 24A | C2NC-1300-HTG-HV_44124A | C2NC-1300-HTG | Valves | Pump/HX Isolation Knife Gate Valve | [11 empty] | D-09 | HV_44124A | [21 empty] | DGT |  | 8 |  |  | Manual | Knife Gate
Digester - Heat - Exchangers - Pump/HX - Isolation - 24B | C2NC-1300-HTG-HV_44124B | C2NC-1300-HTG | Valves | Pump/HX Isolation Knife Gate Valve | [11 empty] | D-09 | HV_44124B | [21 empty] | DGT |  | 8 |  |  | Manual | Knife Gate
Digester - Heat - Exchangers - Pump/HX - Isolation - 24C | C2NC-1300-HTG-HV_44124C | C2NC-1300-HTG | Valves | Pump/HX Isolation Knife Gate Valve | [11 empty] | D-09 | HV_44124C | [21 empty] | DGT |  | 8 |  |  | Manual | Knife Gate
Digester - Heat - Exchangers - Drain - 25A | C2NC-1300-HTG-HV_44125A | C2NC-1300-HTG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-09 | HV_44125A | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Heat - Exchangers - Drain - 25B | C2NC-1300-HTG-HV_44125B | C2NC-1300-HTG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-09 | HV_44125B | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Heat - Exchangers - Drain - 25C | C2NC-1300-HTG-HV_44125C | C2NC-1300-HTG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-09 | HV_44125C | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Heat - Exchangers - Drain - 26A | C2NC-1300-HTG-HV_44126A | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44126A | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 26B | C2NC-1300-HTG-HV_44126B | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44126B | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Heat - Exchangers - Drain - 26C | C2NC-1300-HTG-HV_44126C | C2NC-1300-HTG | Valves | Drain Ball Valve | [11 empty] | D-09 | HV_44126C | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - #1 - Mixer - Auto-Positioner - #3 | C2NC-1300-100-SB_M_41203A | C2NC-1300-100 | Equipment | Digester - #1 - Mixer - Auto-Positioner - #3 | AUMA | [6 empty] | Y |  |  |  | D-08 | SB_M_41203A | [8 empty] | Electric Positioner
Digester - #1 - Mixer - Auto-Positioner - #4 | C2NC-1300-100-SB_M_41204A | C2NC-1300-100 | Equipment | Digester - #1 - Mixer - Auto-Positioner - #4 | AUMA | [6 empty] | Y |  |  |  | D-08 | SB_M_41204A | [8 empty] | Electric Positioner
Digester - #1 - Mixer - Auto-Positioner - #5 | C2NC-1300-100-SB_M_41205A | C2NC-1300-100 | Equipment | Digester - #1 - Mixer - Auto-Positioner - #5 | AUMA | [6 empty] | Y |  |  |  | D-08 | SB_M_41205A | [8 empty] | Electric Positioner
Digester - #1 - Mixer - Auto-Positioner - #6 | C2NC-1300-100-SB_M_41206A | C2NC-1300-100 | Equipment | Digester - #1 - Mixer - Auto-Positioner - #6 | AUMA | [6 empty] | Y |  |  |  | D-08 | SB_M_41206A | [8 empty] | Electric Positioner
Digester - #1 - Mixer - Auto-Positioner - #7 | C2NC-1300-100-SB_M_41207A | C2NC-1300-100 | Equipment | Digester - #1 - Mixer - Auto-Positioner - #7 | AUMA | [6 empty] | Y |  |  |  | D-08 | SB_M_41207A | [8 empty] | Electric Positioner
Digester - #1 - Mixer - Auto-Positioner - #8 | C2NC-1300-100-SB_M_41208A | C2NC-1300-100 | Equipment | Digester - #1 - Mixer - Auto-Positioner - #8 | AUMA | [6 empty] | Y |  |  |  | D-05 | SB_M_41208A | [8 empty] | Electric Positioner
Digester - #1 - Mixer - Auto-Positioner - #9 | C2NC-1300-100-SB_M_41209A | C2NC-1300-100 | Equipment | Digester - #1 - Mixer - Auto-Positioner - #9 | AUMA | [6 empty] | Y |  |  |  | D-06 | SB_M_41209A | [8 empty] | Electric Positioner
Digester - 1 - Sight - Glass 1 | C2NC-1300-100-SG_41201A | C2NC-1300-100 | Equipment | Digester 1 Sight Glass 1 | [11 empty] | D-05 | SG_41201A
Digester - 1 - Sight - Glass 2 | C2NC-1300-100-SG_41202A | C2NC-1300-100 | Equipment | Digester 1 Sight Glass 2 | [11 empty] | D-05 | SG_41202A | [8 empty] | Sight Glass
Digester - #2 - Blower - #1 | C2NC-1300-200-BL_41201B | C2NC-1300-200 | Equipment | Blower to maintain pressure in gas holder cover | Cincinnati Fan | PB-15A | [5 empty] | P |  |  |  | D-04 | BL_41201B |  | 480 | 15A | 5 HP | Air | CI Frame |  |  | Blower
Digester - #2 - Blower - #2 | C2NC-1300-200-BL_41202B | C2NC-1300-200 | Equipment | Blower to maintain pressure in gas holder cover | Cincinnati Fan | PB-15A | [5 empty] | P |  |  |  | D-04 | BL_41202B |  | 480 | 15A | 5 HP | Air | CI Frame |  |  | Blower
Digester - #2 - Mixer - #1 | C2NC-1300-200-MX_41201B | C2NC-1300-200 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSM_XP 940 | [5 empty] | P |  |  |  | D-05 | MX_41201B |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #2 - Mixer - #2 | C2NC-1300-200-MX_41202B | C2NC-1300-200 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSM_XP 940 | [5 empty] | P |  |  |  | D-03 | MX_41202B |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #2 - Mixer - #3 | C2NC-1300-200-MX_41203B | C2NC-1300-200 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-05 | MX_41203B |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #2 - Mixer - #4 | C2NC-1300-200-MX_41204B | C2NC-1300-200 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-05 | MX_41204B |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #2 - Mixer - #5 | C2NC-1300-200-MX_41205B | C2NC-1300-200 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-05 | MX_41205B |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #2 - Mixer - #6 | C2NC-1300-200-MX_41206B | C2NC-1300-200 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-05 | MX_41206B |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #2 - Mixer - #7 | C2NC-1300-200-MX_41207B | C2NC-1300-200 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-05 | MX_41207B |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #2 - Mixer - #8 | C2NC-1300-200-MX_41208B | C2NC-1300-200 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-05 | MX_41208B |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #2 - Mixer - #9 | C2NC-1300-200-MX_41209B | C2NC-1300-200 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-05 | MX_41209B |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Substrate - Pump - to - Digester - #2 | C2NC-1300-200-P_41201B | C2NC-1300-200 | Equipment | Pump from FCON to AD #2 | Boerger | CL 260 | [5 empty] | P |  |  |  | D-05 | P_41201B |  | 480 |  | 20 HP |  |  |  |  | Pump
Digestate - Discharge - Pump - #2 | C2NC-1300-200-P_41202B | C2NC-1300-200 | Equipment | Pump to downstream dewatering | Boerger | CL 260 | [5 empty] | P |  |  |  | D-05 | P_41202B |  | 480 |  | 15 HP |  |  |  |  | Pump
Digester - #2 - Mixer - Service - Box - #1 | C2NC-1300-200-SB_41201B | C2NC-1300-200 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-03 | SB_41201B | [8 empty] | Service Box
Digester - #2 - Mixer - Service - Box - #2 | C2NC-1300-200-SB_41202B | C2NC-1300-200 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-10 | SB_41202B | [8 empty] | Service Box
Digester - #2 - Mixer - Service - Box - #3 | C2NC-1300-200-SB_41203B | C2NC-1300-200 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-05 | SB_41203B | [8 empty] | Service Box
Digester - #2 - Mixer - Service - Box - #4 | C2NC-1300-200-SB_41204B | C2NC-1300-200 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-05 | SB_41204B | [8 empty] | Service Box
Digester - #2 - Mixer - Service - Box - #5 | C2NC-1300-200-SB_41205B | C2NC-1300-200 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-05 | SB_41205B | [8 empty] | Service Box
Digester - #2 - Mixer - Service - Box - #6 | C2NC-1300-200-SB_41206B | C2NC-1300-200 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-05 | SB_41206B | [8 empty] | Service Box
Digester - #2 - Mixer - Service - Box - #7 | C2NC-1300-200-SB_41207B | C2NC-1300-200 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-05 | SB_41207B | [8 empty] | Service Box
Digester - #2 - Mixer - Service - Box - #8 | C2NC-1300-200-SB_41208B | C2NC-1300-200 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-05 | SB_41208B | [8 empty] | Service Box
Digester - #2 - Mixer - Service - Box - #9 | C2NC-1300-200-SB_41209B | C2NC-1300-200 | Equipment | Service Box Pro for membrane roof | Anaergia Technologies | [6 empty] | Y |  |  |  | D-05 | SB_41209B | [8 empty] | Service Box
Digester - #2 - Mixer - Auto-Positioner - #1 | C2NC-1300-200-SB_M_41201B | C2NC-1300-200 | Equipment | Digester - #2 - Mixer - Auto-Positioner - #1 | AUMA | [6 empty] | Y |  |  |  | D-05 | SB_M_41201B | [8 empty] | Electric Positioner
Digester - #2 - Mixer - Auto-Positioner - #2 | C2NC-1300-200-SB_M_41202B | C2NC-1300-200 | Equipment | Digester - #2 - Mixer - Auto-Positioner - #2 | AUMA | [6 empty] | Y |  |  |  | D-05 | SB_M_41202B | [8 empty] | Electric Positioner
Digester - #2 - Mixer - Auto-Positioner - #3 | C2NC-1300-200-SB_M_41203B | C2NC-1300-200 | Equipment | Digester - #2 - Mixer - Auto-Positioner - #3 | AUMA | [6 empty] | Y |  |  |  | D-05 | SB_M_41203B | [8 empty] | Electric Positioner
Digester - #2 - Mixer - Auto-Positioner - #4 | C2NC-1300-200-SB_M_41204B | C2NC-1300-200 | Equipment | Digester - #2 - Mixer - Auto-Positioner - #4 | AUMA | [6 empty] | Y |  |  |  | D-05 | SB_M_41204B | [8 empty] | Electric Positioner
Digester - #2 - Mixer - Auto-Positioner - #5 | C2NC-1300-200-SB_M_41205B | C2NC-1300-200 | Equipment | Digester - #2 - Mixer - Auto-Positioner - #5 | AUMA | [6 empty] | Y |  |  |  | D-05 | SB_M_41205B | [8 empty] | Electric Positioner
Digester - Discharge - Pumps - Valve - 57 | C2NC-1300-DG-HV_41257 | C2NC-1300-DG | Valves | Knife Gate Valve | [11 empty] | D-05 | HV_41257 | [21 empty] | DGT |  | 150DN |  |  | Manual | Knife Gate
Digester - Discharge - Pumps - Valve - 58 | C2NC-1300-DG-HV_41258 | C2NC-1300-DG | Valves | Knife Gate Valve | [11 empty] | D-05 | HV_41258 | [21 empty] | DGT |  | 150DN |  |  | Manual | Knife Gate
Digester - Discharge - Pumps - Pump - Isolation - 59A | C2NC-1300-DG-HV_41259A | C2NC-1300-DG | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-10 | HV_41259A | [21 empty] | DGT | CF8M | 150DN |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Discharge - Pumps - Pump - Isolation - 59B | C2NC-1300-DG-HV_41259B | C2NC-1300-DG | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-10 | HV_41259B | [21 empty] | DGT | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Discharge - Pumps - Pump - Isolation - 59C | C2NC-1300-DG-HV_41259C | C2NC-1300-DG | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-10 | HV_41259C | [21 empty] | DGT | CF8M | 6 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Discharge - Pumps - Drain - 60A | C2NC-1300-DG-HV_41260A | C2NC-1300-DG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-10 | HV_41260A | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Discharge - Pumps - Drain - 60B | C2NC-1300-DG-HV_41260B | C2NC-1300-DG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-10 | HV_41260B | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Discharge - Pumps - Drain - 60C | C2NC-1300-DG-HV_41260C | C2NC-1300-DG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-10 | HV_41260C | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Discharge - Pumps - Drain - 62A | C2NC-1300-DG-HV_41262A | C2NC-1300-DG | Valves | Drain Ball Valve | [11 empty] | D-10 | HV_41262A | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Discharge - Pumps - Drain - 62B | C2NC-1300-DG-HV_41262B | C2NC-1300-DG | Valves | Drain Ball Valve | [11 empty] | D-10 | HV_41262B | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Discharge - Pumps - Drain - 62C | C2NC-1300-DG-HV_41262C | C2NC-1300-DG | Valves | Drain Ball Valve | [11 empty] | D-10 | HV_41262C | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Discharge - Pumps - Drain - 67A | C2NC-1300-DG-HV_41267A | C2NC-1300-DG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-10 | HV_41267A | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Discharge - Pumps - Drain - 67B | C2NC-1300-DG-HV_41267B | C2NC-1300-DG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-10 | HV_41267B | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Discharge - Pumps - Drain - 67C | C2NC-1300-DG-HV_41267C | C2NC-1300-DG | Valves | Drain Eccentric Plug Valve | [11 empty] | D-10 | HV_41267C | [21 empty] | DGT |  | 2 |  |  | Manual | Eccentric Plug
Digester - Discharge - Pumps - Pump - Isolation - 68A | C2NC-1300-DG-HV_41268A | C2NC-1300-DG | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-10 | HV_41268A | [21 empty] | DGT | CF8M | 4 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Discharge - Pumps - Pump - Isolation - 68B | C2NC-1300-DG-HV_41268B | C2NC-1300-DG | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-10 | HV_41268B | [21 empty] | DGT | CF8M | 4 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Discharge - Pumps - Pump - Isolation - 68C | C2NC-1300-DG-HV_41268C | C2NC-1300-DG | Valves | Pump Isolation Knife Gate Valve | Orbinox | BT Series 22 | [9 empty] | D-10 | HV_41268C | [21 empty] | DGT | CF8M | 4 |  |  | Manual | Knife Gate |  | ANSI Flange | EPDM
Digester - Discharge - Pumps - Drain - 69A | C2NC-1300-DG-HV_41269A | C2NC-1300-DG | Valves | Drain Ball Valve | [11 empty] | D-10 | HV_41269A | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Discharge - Pumps - Drain - 69B | C2NC-1300-DG-HV_41269B | C2NC-1300-DG | Valves | Drain Ball Valve | [11 empty] | D-10 | HV_41269B | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - Discharge - Pumps - Drain - 69C | C2NC-1300-DG-HV_41269C | C2NC-1300-DG | Valves | Drain Ball Valve | [11 empty] | D-10 | HV_41269C | [21 empty] | DGT |  | 1 |  |  | Manual | Ball
Digester - #2 - Mixer - Auto-Positioner - #6 | C2NC-1300-200-SB_M_41206B | C2NC-1300-200 | Equipment | Digester - #2 - Mixer - Auto-Positioner - #6 | AUMA | [6 empty] | Y |  |  |  | D-10 | SB_M_41206B | [8 empty] | Electric Positioner
Digester - #2 - Mixer - Auto-Positioner - #7 | C2NC-1300-200-SB_M_41207B | C2NC-1300-200 | Equipment | Digester - #2 - Mixer - Auto-Positioner - #7 | AUMA | [6 empty] | Y |  |  |  | D-10 | SB_M_41207B | [8 empty] | Electric Positioner
Digester - #2 - Mixer - Auto-Positioner - #8 | C2NC-1300-200-SB_M_41208B | C2NC-1300-200 | Equipment | Digester - #2 - Mixer - Auto-Positioner - #8 | AUMA | [6 empty] | Y |  |  |  | D-05 | SB_M_41208B | [8 empty] | Electric Positioner
Digester - #2 - Mixer - Auto-Positioner - #9 | C2NC-1300-200-SB_M_41209B | C2NC-1300-200 | Equipment | Digester - #2 - Mixer - Auto-Positioner - #9 | AUMA | [6 empty] | Y |  |  |  | D-05 | SB_M_41209B | [8 empty] | Electric Positioner
Digester - 2 - Sight - Glass 1 | C2NC-1300-200-SG_41201B | C2NC-1300-200 | Equipment | Digester 2 Sight Glass 1 | [11 empty] | D-06 | SG_41201B
Digester - 2 - Sight - Glass 2 | C2NC-1300-200-SG_41202B | C2NC-1300-200 | Equipment | Digester 2 Sight Glass 2 | [7 empty] | Y |  |  |  | D-06 | SG_41202B | [8 empty] | Electric Positioner
Digester - #3 - Blower - #1 | C2NC-1300-300-BL_41201C | C2NC-1300-300 | Equipment | Blower to maintain pressure in gas holder cover | Cincinnati Fan | PB-15A | [5 empty] | P |  |  |  | D-05 | BL_41201C |  | 480 | 15A | 5 HP | Air | CI Frame |  |  | Blower
Digester - #3 - Blower - #2 | C2NC-1300-300-BL_41202C | C2NC-1300-300 | Equipment | Blower to maintain pressure in gas holder cover | Cincinnati Fan | PB-15A | [5 empty] | P |  |  |  | D-05 | BL_41202C |  | 480 | 15A | 5 HP | Air | CI Frame |  |  | Blower
Digester - #3 - Mixer - #1 | C2NC-1300-300-MX_41201C | C2NC-1300-300 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSM_XP 940 | [5 empty] | P |  |  |  | D-06 | MX_41201C |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #3 - Mixer - #2 | C2NC-1300-300-MX_41202C | C2NC-1300-300 | Equipment | PSM 940 Mixer | Anaergia Technologies | PSM_XP 940 | [5 empty] | P |  |  |  | D-06 | MX_41202C |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #3 - Mixer - #3 | C2NC-1300-300-MX_41203C | C2NC-1300-300 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-06 | MX_41203C |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #3 - Mixer - #4 | C2NC-1300-300-MX_41204C | C2NC-1300-300 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-06 | MX_41204C |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #3 - Mixer - #5 | C2NC-1300-300-MX_41205C | C2NC-1300-300 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-06 | MX_41205C |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #3 - Mixer - #6 | C2NC-1300-300-MX_41206C | C2NC-1300-300 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-06 | MX_41206C |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #3 - Mixer - #7 | C2NC-1300-300-MX_41207C | C2NC-1300-300 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-06 | MX_41207C |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #3 - Mixer - #8 | C2NC-1300-300-MX_41208C | C2NC-1300-300 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-06 | MX_41208C |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Digester - #3 - Mixer - #9 | C2NC-1300-300-MX_41209C | C2NC-1300-300 | Equipment | PSM 1500 Mixer | Anaergia Technologies | PSM_XP 1500 | [5 empty] | P |  |  |  | D-06 | MX_41209C |  | 480 |  | 16.76275 HP |  |  |  |  | Mixer
Substrate - Pump - to - Digester - #3 | C2NC-1300-300-P_41201C | C2NC-1300-300 | Equipment | Pump from FCON to AD #3 | Boerger | CL 260 | [5 empty] | P |  |  |  | D-06 | P_41201C |  | 480 |  | 20 HP |  |  |  |  | Pump
Digestate - Discharge - Pump - #3 | C2NC-1300-300-P_41202C | C2NC-1300-300 | Equipment | Pump to downstream dewatering | Boerger | CL 260 | [5 empty] | P |  |  |  | D-06 | P_41202C |  | 480 |  | 15 HP |  |  |  |  | Pump
Digester - #3 - Mixer - Service - Box - #1 | C2NC-1300-300-SB_41201C | C2NC-1300-300 | Equipment | Service Box Pro for membrane roof 1 | Anaergia Technologies | [6 empty] | Y |  |  |  | D-03 | SB_41201C | [8 empty] | Service Box
Digester - #3 - Mixer - Service - Box - #2 | C2NC-1300-300-SB_41202C | C2NC-1300-300 | Equipment | Service Box Pro for membrane roof 2 | Anaergia Technologies | [6 empty] | Y |  |  |  | D-10 | SB_41202C | [8 empty] | Service Box
Digester - #3 - Mixer - Service - Box - #3 | C2NC-1300-300-SB_41203C | C2NC-1300-300 | Equipment | Service Box Pro for membrane roof 3 | Anaergia Technologies | [6 empty] | Y |  |  |  | D-06 | SB_41203C | [8 empty] | Service Box
Digester - #3 - Mixer - Service - Box - #4 | C2NC-1300-300-SB_41204C | C2NC-1300-300 | Equipment | Service Box Pro for membrane roof 4 | Anaergia Technologies | [6 empty] | Y |  |  |  | D-06 | SB_41204C | [8 empty] | Service Box
Digester - #3 - Mixer - Service - Box - #5 | C2NC-1300-300-SB_41205C | C2NC-1300-300 | Equipment | Service Box Pro for membrane roof 5 | Anaergia Technologies | [6 empty] | Y |  |  |  | D-06 | SB_41205C | [8 empty] | Service Box
Digester - #3 - Mixer - Service - Box - #6 | C2NC-1300-300-SB_41206C | C2NC-1300-300 | Equipment | Service Box Pro for membrane roof 6 | Anaergia Technologies | [6 empty] | Y |  |  |  | D-06 | SB_41206C | [8 empty] | Service Box
Digester - #3 - Mixer - Service - Box - #7 | C2NC-1300-300-SB_41207C | C2NC-1300-300 | Equipment | Service Box Pro for membrane roof 7 | Anaergia Technologies | [6 empty] | Y |  |  |  | D-06 | SB_41207C | [8 empty] | Service Box
Digester - #3 - Mixer - Service - Box - #8 | C2NC-1300-300-SB_41208C | C2NC-1300-300 | Equipment | Service Box Pro for membrane roof 8 | Anaergia Technologies | [6 empty] | Y |  |  |  | D-06 | SB_41208C | [8 empty] | Service Box
Digester - #3 - Mixer - Service - Box - #9 | C2NC-1300-300-SB_41209C | C2NC-1300-300 | Equipment | Service Box Pro for membrane roof 9 | Anaergia Technologies | [6 empty] | Y |  |  |  | D-06 | SB_41209C | [8 empty] | Service Box
Digester - #3 - Mixer - Auto-Positioner - #1 | C2NC-1300-300-SB_M_41201C | C2NC-1300-300 | Equipment | Digester - #3 - Mixer - Auto-Positioner - #1 | AUMA | [6 empty] | Y |  |  |  | D-06 | SB_M_41201C | [8 empty] | Electric Positioner
Digester - #3 - Mixer - Auto-Positioner - #2 | C2NC-1300-300-SB_M_41202C | C2NC-1300-300 | Equipment | Digester - #3 - Mixer - Auto-Positioner - #2 | AUMA | [6 empty] | Y |  |  |  | D-06 | SB_M_41202C | [8 empty] | Electric Positioner
Digester - #3 - Mixer - Auto-Positioner - #3 | C2NC-1300-300-SB_M_41203C | C2NC-1300-300 | Equipment | Digester - #3 - Mixer - Auto-Positioner - #3 | AUMA | [6 empty] | Y |  |  |  | D-06 | SB_M_41203C | [8 empty] | Electric Positioner
Digester - #3 - Mixer - Auto-Positioner - #4 | C2NC-1300-300-SB_M_41204C | C2NC-1300-300 | Equipment | Digester - #3 - Mixer - Auto-Positioner - #4 | AUMA | [6 empty] | Y |  |  |  | D-06 | SB_M_41204C | [8 empty] | Electric Positioner
Digester - #3 - Mixer - Auto-Positioner - #5 | C2NC-1300-300-SB_M_41205C | C2NC-1300-300 | Equipment | Digester - #3 - Mixer - Auto-Positioner - #5 | AUMA | [6 empty] | Y |  |  |  | D-06 | SB_M_41205C | [8 empty] | Electric Positioner
Digester - #3 - Mixer - Auto-Positioner - #6 | C2NC-1300-300-SB_M_41206C | C2NC-1300-300 | Equipment | Digester - #3 - Mixer - Auto-Positioner - #6 | AUMA | [6 empty] | Y |  |  |  | D-06 | SB_M_41206C | [8 empty] | Electric Positioner
Digester - #3 - Mixer - Auto-Positioner - #7 | C2NC-1300-300-SB_M_41207C | C2NC-1300-300 | Equipment | Digester - #3 - Mixer - Auto-Positioner - #7 | AUMA | [6 empty] | Y |  |  |  | D-06 | SB_M_41207C | [8 empty] | Electric Positioner
Digester - #3 - Mixer - Auto-Positioner - #8 | C2NC-1300-300-SB_M_41208C | C2NC-1300-300 | Equipment | Digester - #3 - Mixer - Auto-Positioner - #8 | AUMA | [6 empty] | Y |  |  |  | D-06 | SB_M_41208C | [8 empty] | Electric Positioner
Digester - #3 - Mixer - Auto-Positioner - #9 | C2NC-1300-300-SB_M_41209C | C2NC-1300-300 | Equipment | Digester - #3 - Mixer - Auto-Positioner - #9 | AUMA | [6 empty] | Y |  |  |  | D-06 | SB_M_41209C | [8 empty] | Electric Positioner
Digester - 3 - Sight - Glass - 1 | C2NC-1300-300-SG_41201C | C2NC-1300-300 | Equipment | Digester 3 Sight Glass 1 | AUMA | [10 empty] | D-07 | SG_41201C
Digester - 3 - Sight - Glass - 2 | C2NC-1300-300-SG_41202C | C2NC-1300-300 | Equipment | Digester 3 Sight Glass 2 | AUMA | [10 empty] | D-07 | SG_41202C
Nutrient - Dosing - Pump A | C2NC-1300-CHEM-P_31101A | C2NC-1300-CHEM | Equipment | Dosing pump for nutrient dosing skid | Seepex | MD 0015-24 | [5 empty] | P |  |  |  | D-06 | P_31101A |  | 120 |  | 1 HP |  |  |  |  | Pump
Nutrient - Dosing - Pump B | C2NC-1300-CHEM-P_31101B | C2NC-1300-CHEM | Equipment | Dosing pump for nutrient dosing skid | Seepex | MD 0015-24 | [5 empty] | P |  |  |  | D-06 | P_31101B |  | 120 |  | 1 HP |  |  |  |  | Pump
Anti-Foam - Dosing - Pump A | C2NC-1300-CHEM-P_31201A | C2NC-1300-CHEM | Equipment | Dosing pump for anti-foam dosing skid | Seepex | MD 003-12 | [5 empty] | P |  |  |  | D-08 | P_31201A |  | 120 |  | 1 HP |  |  |  |  | Pump
Anti-Foam - Dosing - Pump B | C2NC-1300-CHEM-P_31201B | C2NC-1300-CHEM | Equipment | Dosing pump for anti-foam dosing skid | Seepex | MD 003-12 | [5 empty] | P |  |  |  | D-08 | P_31201B |  | 120 |  | 1 HP |  |  |  |  | Pump
Digestate - Heat - Exchanger - #1 | C2NC-1300-HTG-HX_44101A | C2NC-1300-HTG | Equipment | 500kw AD heat exchanger | Lackeby | HSW 100-36 L=3 | [5 empty] | Y |  |  |  | D-08 | HX_44101A | [8 empty] | Heat Exchanger
Digestate - Heat - Exchanger - #2 | C2NC-1300-HTG-HX_44101B | C2NC-1300-HTG | Equipment | 500kw AD heat exchanger | Lackeby | HSW 100-36 L=3 | [5 empty] | Y |  |  |  | D-08 | HX_44101B | [8 empty] | Heat Exchanger
Digestate - Heat - Exchanger - #3 | C2NC-1300-HTG-HX_44101C | C2NC-1300-HTG | Equipment | 500kw AD heat exchanger | Lackeby | HSW 100-36 L=3 | [5 empty] | Y |  |  |  | D-09 | HX_44101C | [8 empty] | Heat Exchanger
Digester - #1 - Heat - Exchanger - Pump | C2NC-1300-HTG-P_44101A | C2NC-1300-HTG | Equipment | Digester - #1 - Heat - Exchanger - Pump | Boerger | EL 1550 | [5 empty] | P |  |  |  | D-09 | P_44101A |  | 480 |  | 60 HP |  |  |  |  | Pump
Digester - #2 - Heat - Exchanger - Pump | C2NC-1300-HTG-P_44101B | C2NC-1300-HTG | Equipment | Digester - #2 - Heat - Exchanger - Pump | Boerger | EL 1550 | [5 empty] | P |  |  |  | D-09 | P_44101B |  | 480 |  | 60 HP |  |  |  |  | Pump
Digester - #3 - Heat - Exchanger - Pump | C2NC-1300-HTG-P_44101C | C2NC-1300-HTG | Equipment | Digester - #3 - Heat - Exchanger - Pump | Boerger | EL 1550 | [5 empty] | P |  |  |  | D-09 | P_44101C |  | 480 |  | 60 HP |  |  |  |  | Pump
Digester - #1 - Hot - Water - Pump | C2NC-1300-HTG-P_44102A | C2NC-1300-HTG | Equipment | Digester - #1 - Hot - Water - Pump | [7 empty] | P |  |  |  | D-09 | P_44102A |  | 460 |  | 10 HP |  |  |  |  | Pump
Digester - #2 - Hot - Water - Pump | C2NC-1300-HTG-P_44102B | C2NC-1300-HTG | Equipment | Digester - #2 - Hot - Water - Pump | [7 empty] | P |  |  |  | D-09 | P_44102B |  | 460 |  | 10 HP |  |  |  |  | Pump
Digester - #3 - Hot - Water - Pump | C2NC-1300-HTG-P_44102C | C2NC-1300-HTG | Equipment | Digester - #3 - Hot - Water - Pump | [7 empty] | P |  |  |  | D-09 | P_44102C |  | 460 |  | 10 HP |  |  |  |  | Pump
Sight Glass
Electric Positioner

## 1400 - Digestate
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Material of Construction | Instrument Diameter | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes
1400 - Dewatering | C2NC-1400 | C2NC | Locations And Facilities | Dewatering
Filtrate Handeling | C2NC-1400-FLT | C2NC-1800 | Locations And Facilities | Filtrate Handeling
6 Inch PVC Filtrate Handeling SSD Filtrate Line 541_03 | C2NC-1400-FLT-6 _ FLT _ 54103 _ PVC | C2NC-1400-FLT | Lines | 6 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 5 | 6 _ FLT _ 54103 _ PVC | [10 empty] | SSD Filtrate | PVC | 6 | SSD Filtrate Sump Pump A | SSD Filtrate Sump Pumps Discharge Header | N | 100 |  | 150 #
6 Inch PVC Filtrate Handeling SSD Filtrate Line 541_04 | C2NC-1400-FLT-6 _ FLT _ 54104 _ PVC | C2NC-1400-FLT | Lines | 6 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 5 | 6 _ FLT _ 54104 _ PVC | [10 empty] | SSD Filtrate | PVC | 6 | SSD Filtrate Sump Pump B | SSD Filtrate Sump Pumps Discharge Header | N | 100 |  | 150 #
6 Inch PVC Filtrate Handeling SSD Filtrate Line 541_06 | C2NC-1400-FLT-6 _ FLT _ 54106 _ PVC | C2NC-1400-FLT | Lines | 6 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 5 | 6 _ FLT _ 54106 _ PVC | [10 empty] | SSD Filtrate | PVC | 6 | SSD Filtrate Below Grade Metering Vault FIT Connection |  | N | 100 |  | 150 #
6 Inch PVC Filtrate Handeling SSD Filtrate Line 541_07 | C2NC-1400-FLT-6 _ FLT _ 54107 _ PVC | C2NC-1400-FLT | Lines | 6 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 5 | 6 _ FLT _ 54107 _ PVC | [10 empty] | SSD Filtrate | PVC | 6 | SSD Filtrate Below Grade Metering Vault FIT Connection |  | N | 100 |  | 150 #
6 Inch PVC Filtrate Handeling SSD Filtrate Line 541_08 | C2NC-1400-FLT-6 _ FLT _ 54108 _ PVC | C2NC-1400-FLT | Lines | 6 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 5 | 6 _ FLT _ 54108 _ PVC | [10 empty] | SSD Filtrate | PVC | 6 | SSD Filtrate Below Grade Metering Vault FIT Bypass |  | N | 100 |  | 150 #
6 Inch PVC Filtrate Handeling SSD Filtrate Line 541_09 | C2NC-1400-FLT-6 _ FLT _ 54109 _ PVC | C2NC-1400-FLT | Lines | 6 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 5 | 6 _ FLT _ 54109 _ PVC | [10 empty] | SSD Filtrate | PVC | 6 | SSD Filtrate Below Grade Metering Vault FIT Bypass |  | N | 100 |  | 150 #
6 Inch Carbon Steel Filtrate Handeling Mixed Liquor Line 541_11 | C2NC-1400-FLT-6 _ ML _ 54111 _ CSA | C2NC-1400-FLT | Lines | 6 Inch Carbon Steel Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 6 | 6 _ ML _ 54111 _ CSA | [10 empty] | Mixed Liquor | Carbon Steel | 6 | Anoxic Tank | Drain/Outlet | N | 100 |  | 150 #
8 Inch PVC Filtrate Handeling SSD Filtrate Line 541_01 | C2NC-1400-FLT-8 _ FLT _ 54101 _ PVC1 | C2NC-1400-FLT | Lines | 8 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 5 | 8 _ FLT _ 54101 _ PVC1 | [10 empty] | SSD Filtrate | PVC | 8 | SSD Filtrate Below Grade Metering Vault | Anoxic Tank | N | 100 |  | 150 #
8 Inch PVC Filtrate Handeling SSD Filtrate Line 541_02 | C2NC-1400-FLT-8 _ FLT _ 54102 _ PVC | C2NC-1400-FLT | Lines | 8 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 6 | 8 _ FLT _ 54102 _ PVC | [10 empty] | SSD Filtrate | PVC | 8 | Anoxic Tank Bypass |  | N | 100 |  | 150 #
8 Inch PVC Filtrate Handeling SSD Filtrate Line 541_05 | C2NC-1400-FLT-8 _ FLT _ 54105 _ PVC | C2NC-1400-FLT | Lines | 8 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 5 | 8 _ FLT _ 54105 _ PVC | [10 empty] | SSD Filtrate | PVC | 8 | SSD Filtrate Sump Pumps Discharge Header | SSD Filtrate Below Grade Metering Vault | N | 100 |  | 150 #
8 Inch PVC Filtrate Handeling SSD Filtrate Line 541_10 | C2NC-1400-FLT-8 _ FLT _ 54110 _ PVC | C2NC-1400-FLT | Lines | 8 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 6 | 8 _ FLT _ 54110 _ PVC | [10 empty] | SSD Filtrate | PVC | 8 | SSD Filtrate Sump Exit - Below Grade | Anoxic Tank & Anoxic Tank Bypass | N | 100 |  | 150 #
8 Inch PVC Filtrate Handeling SSD Filtrate Line 541_13 | C2NC-1400-FLT-8 _ FLT _ 54113 _ PVC | C2NC-1400-FLT | Lines | 8 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 8 | 8 _ FLT _ 54113 _ PVC | [10 empty] | SSD Filtrate | PVC | 8 | Anoxic Tank Bypass | Aerobic Tank B | N | 100 |  | 150 #
8 Inch PVC Filtrate Handeling Mixed Liquor Line 541_12 | C2NC-1400-FLT-8 _ ML _ 54112 _ PVC | C2NC-1400-FLT | Lines | 8 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 7 | 8 _ ML _ 54112 _ PVC | [10 empty] | Mixed Liquor | PVC | 8 | Anoxic Tank Bypass | Aerobic Tank A | N | 100 |  | 150 #
Filtrate Handeling - Swing Check Valve - 00 | C2NC-1400-FLT-CV_54100 | C2NC-1400-FLT | Valves | Filtrate Handeling Check Valve - 6" 150# FLGD PVC SWING CHECK VALVE HAYWARD SW1600E |  | 85HAY600SW1600ESCV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 5 | CV_54100 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B | 6 |  |  | Manual | Swing Check Valve | N.A | Flanged
Filtrate Handeling - Swing Check Valve - 01 | C2NC-1400-FLT-CV_54101 | C2NC-1400-FLT | Valves | Filtrate Handeling Check Valve - 6" 150# FLGD PVC SWING CHECK VALVE HAYWARD SW1600E |  | 85HAY600SW1600ESCV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 5 | CV_54101 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B | 6 |  |  | Manual | Swing Check Valve | N.A | Flanged
Filtrate Handeling - Flow Indicator Transmitter - FIT_54100 | C2NC-1400-FLT-FIT_54100 | C2NC-1400-FLT | Instruments | Flow Indicator Transmitter within the Filtrate Handeling system - FIT on SSD filtrate from sump (SUMP-54100) to Anoxic tank (TK-63100) | Endress and Hauser | Promag W10 5WBB1F-AAEAEBJA0DUA1KGAA1+Z1 |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 5 | FIT_54100 | [42 empty] | FLT |  |  |  | Flow Meter w/ indicator |  | Analog | In Line 6" ANSI 150#
Filtrate Handeling - Level Switch High - LSH_54100 | C2NC-1400-FLT-LSH_54100 | C2NC-1400-FLT | Instruments | Level Switch High within the Filtrate Handeling system - Level Switch for Sump (SUMP-54100) | Endress and Hauser | Micropilot FMR50 (FMR50-AAACCDBMRGF+NFZ1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 5 | LSH_54100 | [42 empty] | FLT |  |  |  | Level Switch High |  | Digital | Insertion 1/2" NPT
Filtrate Handeling - Level Switch Low - LSL_54100 | C2NC-1400-FLT-LSL_54100 | C2NC-1400-FLT | Instruments | Level Switch Low within the Filtrate Handeling system - Level Switch for Sump (SUMP-54100) | Endress and Hauser | Liquifloat T FTS20 AC/DC PP/PUR, 20m 71035521 |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 5 | LSL_54100 | [42 empty] | FLT |  |  |  | Level Switch Low |  | Digital | Float
Filtrate Handeling - Level Transmitter - LT_54100 | C2NC-1400-FLT-LT_54100 | C2NC-1400-FLT | Instruments | Level Transmitter within the Filtrate Handeling system - Level Transmitter for Sump (SUMP-54100) | Endress and Hauser | Liquifloat T FTS20 AC/DC PP/PUR, 20m 71035521 |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 5 | LT_54100 | [42 empty] | FLT |  |  |  | Level Transmitter |  | Analog | Float
Filtrate Handeling - Knife-Gate Valve - 00 | C2NC-1400-FLT-MV_54100 | C2NC-1400-FLT | Valves | Filtrate Handeling Manual Valve - 6 ORBlNOX LUG SOFT SEAT KNIFE GATE VALVE SS BODY EPDM SEAT SERIES 20-3636R-HW |  | 600203636RKGV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 5 | MV_54100 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Filtrate Handeling - Knife-Gate Valve - 01 | C2NC-1400-FLT-MV_54101 | C2NC-1400-FLT | Valves | Filtrate Handeling Manual Valve - 6 ORBlNOX LUG SOFT SEAT KNIFE GATE VALVE SS BODY EPDM SEAT SERIES 20-3636R-HW |  | 600203636RKGV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 5 | MV_54101 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Filtrate Handeling - Knife-Gate Valve - 02 | C2NC-1400-FLT-MV_54102 | C2NC-1400-FLT | Valves | Filtrate Handeling Manual Valve - 6 ORBlNOX LUG SOFT SEAT KNIFE GATE VALVE SS BODY EPDM SEAT SERIES 20-3636R-HW |  | 600203636RKGV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 5 | MV_54102 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Filtrate Handeling - Knife-Gate Valve - 03 | C2NC-1400-FLT-MV_54103 | C2NC-1400-FLT | Valves | Filtrate Handeling Manual Valve - 6 ORBlNOX LUG SOFT SEAT KNIFE GATE VALVE SS BODY EPDM SEAT SERIES 20-3636R-HW |  | 600203636RKGV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 5 | MV_54103 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Filtrate Handeling - Knife-Gate Valve - 04 | C2NC-1400-FLT-MV_54104 | C2NC-1400-FLT | Valves | Filtrate Handeling Manual Valve - 6 ORBlNOX LUG SOFT SEAT KNIFE GATE VALVE SS BODY EPDM SEAT SERIES 20-3636R-HW |  | 600203636RKGV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 5 | MV_54104 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Filtrate Handeling - SSD filtrate sump pump A | C2NC-1400-FLT-P_54100A | C2NC-1400-FLT | Equipment | SSD filtrate sump pump A | [9 empty] | AN-0119 A01-01 | 5 | P_54100A | [8 empty] | Pump
Filtrate Handeling - SSD filtrate sump pump B | C2NC-1400-FLT-P_54100B | C2NC-1400-FLT | Equipment | SSD filtrate sump pump B | [9 empty] | AN-0119 A01-01 | 5 | P_54100B | [8 empty] | Pump
Filtrate Handeling - SSD filtrate sump | C2NC-1400-FLT-SUMP_54100 | C2NC-1400-FLT | Equipment | SSD filtrate sump | [9 empty] | AN-0119 A01-01 | 5 | SUMP_54100 | [8 empty] | Sump
SSD1 | C2NC-1400-SSDA | C2NC-1400 | Locations And Facilities | SSD1
6 Inch HDPE SSD 1 Digestate Line 511_02 | C2NC-1400-SSDA-6 _ DSA _ 51102 _ HDPE | C2NC-1400-SSDA | Lines | 6 Inch HDPE Digestate Line | [9 empty] | AN-1156 A01 01 | 1 | 6 _ DSA _ 51102 _ HDPE | [10 empty] | Digestate | HDPE | 6 | Digestate Pumps | SSD A | N | 100 |  | 150 #
6 Inch HDPE SSD 1 Digestate Line 511_03 | C2NC-1400-SSDA-6 _ DSA _ 51103 _ HDPE | C2NC-1400-SSDA | Lines | 6 Inch HDPE Digestate Line | [9 empty] | AN-1156 A01 01 | 18 | 6 _ DSA _ 51103 _ HDPE | [10 empty] | Digestate | HDPE | 6 | Digestate Pumps A/C Crossover |  | N | 100 |  | 150 #
6 Inch HDPE SSD 1 Digestate Line 511_04 | C2NC-1400-SSDA-6 _ DSA _ 51104 _ HDPE | C2NC-1400-SSDA | Lines | 6 Inch HDPE Digestate Line | [9 empty] | AN-1156 A01 01 | 18 | 6 _ DSA _ 51104 _ HDPE | [10 empty] | Digestate | HDPE | 6 | Digestate Pumps A/B Crossover |  | N | 100 |  | 150 #
6 Inch HDPE SSD 1 Digestate Line 511_05 | C2NC-1400-SSDA-6 _ DSA _ 51105 _ HDPE | C2NC-1400-SSDA | Lines | 6 Inch HDPE Digestate Line | [9 empty] | AN-1156 A01 01 | 18 | 6 _ DSA _ 51105 _ HDPE | [10 empty] | Digestate | HDPE | 6 | Digestate Pumps B/C Crossover |  | N | 100 |  | 150 #
8 Inch PVC SSD 1 SSD Filtrate Line 511_01 | C2NC-1400-SSDA-8 _ FLT _ 51101 _ PVC | C2NC-1400-SSDA | Lines | 8 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 1 | 8 _ FLT _ 51101 _ PVC | [10 empty] | SSD Filtrate | PVC | 8 | SSD A | SSD Filtrate Sump | N | 100 |  | 150 #
SSD 1 - Swing Check Valve - 00 | C2NC-1400-SSDA-CV_51100 | C2NC-1400-SSDA | Valves | SSD 1 Check Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | CV_51100 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B | 2 |  |  | Manual | Swing Check Valve | N.A | Flanged
SSD 1 - Knife-Gate Valve - 00 | C2NC-1400-SSDA-FV_51100 | C2NC-1400-SSDA | Valves | SSD 1 Pneumatic Valve - Kinfe gate valve birdirectional with pneumatic double acting fail last position actuator. ASCO Numatics Solenoid EF8342Ga, 120V, 4-way |  | 22-363R-06.0-DA-PROX-SOL |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 18 | FV_51100 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
SSD 1 - Knife-Gate Valve - 03 | C2NC-1400-SSDA-FV_51103 | C2NC-1400-SSDA | Valves | SSD 1 Pneumatic Valve |  | "STAFSIO" or similar | [7 empty] | AN-1156 A01 01 | 1 | FV_51103 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
SSD 1 - Ball Valve - 00 | C2NC-1400-SSDA-MV_51100 | C2NC-1400-SSDA | Valves | SSD 1 Manual Valve - SIMTECH TBB1016020 2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016020 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 1 | MV_51100 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | Flanged
SSD 1 - Knife-Gate Valve - 01 | C2NC-1400-SSDA-MV_51101 | C2NC-1400-SSDA | Valves | SSD 1 Manual Valve |  | "STAFSIO" or similar | [7 empty] | AN-1156 A01 01 | 1 | MV_51101 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Manual | Knife-Gate Valve | Manual | LUG
SSD 1 - Ball Valve - 02 | C2NC-1400-SSDA-MV_51102 | C2NC-1400-SSDA | Valves | SSD 1 Manual Valve |  | "EBRO" or similar |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 1 | MV_51102 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 2 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 1 - Ball Valve - 03 | C2NC-1400-SSDA-MV_51103 | C2NC-1400-SSDA | Valves | SSD 1 Manual Valve |  | "EBRO" or similar |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 1 | MV_51103 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 2 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 1 - Ball Valve - 04 | C2NC-1400-SSDA-MV_51104 | C2NC-1400-SSDA | Valves | SSD 1 Manual Valve |  | "EBRO" or similar |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 1 | MV_51104 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 2 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 1 - 5/3 Way Manual Valve - 05 | C2NC-1400-SSDA-MV_51105 | C2NC-1400-SSDA | Valves | SSD 1 Manual Valve | [5 empty] | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 1 | MV_51105 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Manual | 5/3 Way Manual Valve | Manual
SSD 1 - Ball Valve - 06 | C2NC-1400-SSDA-MV_51106 | C2NC-1400-SSDA | Valves | SSD 1 Manual Valve |  | "EBRO" or similar |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 1 | MV_51106 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.75 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 1 - Ball Valve - 07 | C2NC-1400-SSDA-MV_51107 | C2NC-1400-SSDA | Valves | SSD 1 Manual Valve |  | "EBRO" or similar |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 1 | MV_51107 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD A - Inline Mixer for Digestate Dewatering | C2NC-1400-SSDA-MX_51101 | C2NC-1400-SSDA | Equipment | Inline Mixer for Digestate Dewatering | UTS Products | [8 empty] | AN-0119 A01-01 | 1 | MX_51101 | [8 empty] | Mixer | [25 empty] | 5.9x6.6 | 8.23
SSD A - Mixer for Flocculation Tank | C2NC-1400-SSDA-MX_51102 | C2NC-1400-SSDA | Equipment | Mixer for Flocculation Tank | UTS Products | [8 empty] | AN-0119 A01-01 | 1 | MX_51102 | [8 empty] | Mixer | [25 empty] | 5.9x6.6 | 8.23
SSD 1 - Pressure Indicator Transmitter - PIT_51102 | C2NC-1400-SSDA-PIT_51102 | C2NC-1400-SSDA | Instruments | Pressure Indicator Transmitter within the SSD 1 system - PIT on top of Flocculation tank (TK-51102) | IFM | PG2797 |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 1 | PIT_51102 | [42 empty] | DSA |  |  |  | Pressure Transmitter w/ indicator |  | Analog
SSD 1 - Pressure Control Valve - 00 | C2NC-1400-SSDA-PRV_51100 | C2NC-1400-SSDA | Valves | SSD 1 Pressure Relief Valve |  | Multifix BG1-G1/4 2xIG |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 1 | PRV_51100 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Manual | Pressure Control Valve | Manual | THRD-F NPT
SSD 1 - Pressure Control Valve - 01 | C2NC-1400-SSDA-PRV_51101 | C2NC-1400-SSDA | Valves | SSD 1 Pressure Relief Valve |  | Multifix BG1-G1/4 2xIG |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 1 | PRV_51101 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Manual | Pressure Control Valve | Manual | THRD-F NPT
SSD A - Digestate Dewatering | C2NC-1400-SSDA-SSD_51100 | C2NC-1400-SSDA | Equipment | Digestate Dewatering | UTS Products | [8 empty] | AN-0119 A01-01 | 1 | SSD_51100 | [8 empty] | Solids Seperator Dewaterer | [25 empty] | 21.96 x 5.80 | 5.87
SSD 1 - Solenoid Valve - 00 | C2NC-1400-SSDA-SV_51100 | C2NC-1400-SSDA | Valves | SSD 1 Solenoid Valve |  | Buschjost-GmbH 8274600-9151-02400 |  |  |  | Buschjost |  |  |  | AN-1156 A01 01 | 1 | SV_51100 | [11 empty] | SSA1 | [11 empty] | 2 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD 1 - Solenoid Valve - 01 | C2NC-1400-SSDA-SV_51101 | C2NC-1400-SSDA | Valves | SSD 1 Solenoid Valve |  | Buschjost-GmbH 8274600-9151-02400 |  |  |  | Buschjost |  |  |  | AN-1156 A01 01 | 1 | SV_51101 | [11 empty] | SSA1 | [11 empty] | 2 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD 1 - Solenoid Valve - 02 | C2NC-1400-SSDA-SV_51102 | C2NC-1400-SSDA | Valves | SSD 1 Solenoid Valve |  | FESTO AG VUVS-L25-M52-MD-G14-F8-1B2 |  |  |  | Festo |  |  |  | AN-1156 A01 01 | 1 | SV_51102 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD 1 - Solenoid Valve - 03 | C2NC-1400-SSDA-SV_51103 | C2NC-1400-SSDA | Valves | SSD 1 Solenoid Valve |  | FESTO AG VUVS-L25-M52-MD-G14-F8-1B2 |  |  |  | Festo |  |  |  | AN-1156 A01 01 | 1 | SV_51103 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD A - Flocculation Tank | C2NC-1400-SSDA-TK_51102 | C2NC-1400-SSDA | Tanks | Flocculation Tank | UTS Products | [8 empty] | AN-0119 A01-01 | 1 | TK_51102 | [8 empty] | Tank | [25 empty] | 5.9x6.6 | 8.23
SSD2 | C2NC-1400-SSDB | C2NC-1400 | Locations And Facilities | SSD2
6 Inch HDPE SSD 2 Digestate Line 512_02 | C2NC-1400-SSDB-6 _ DSA _ 51202 _ HDPE | C2NC-1400-SSDB | Lines | 6 Inch HDPE Digestate Line | [9 empty] | AN-1156 A01 01 | 2 | 6 _ DSA _ 51202 _ HDPE | [10 empty] | Digestate | HDPE | 6 | Digestate Pumps | SSD B | N | 100 |  | 150 #
8 Inch PVC SSD 2 SSD Filtrate Line 512_01 | C2NC-1400-SSDB-8 _ FLT _ 51201 _ PVC | C2NC-1400-SSDB | Lines | 8 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 2 | 8 _ FLT _ 51201 _ PVC | [10 empty] | SSD Filtrate | PVC | 8 | SSD B | SSD Filtrate Sump | N | 100 |  | 150 #
SSD 2 - Swing Check Valve - 00 | C2NC-1400-SSDB-CV_51200 | C2NC-1400-SSDB | Valves | SSD 2 Check Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | CV_51200 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B | 2 |  |  | Manual | Swing Check Valve | N.A | Flanged
SSD 2 - Knife-Gate Valve - 00 | C2NC-1400-SSDB-FV_51200 | C2NC-1400-SSDB | Valves | SSD 2 Pneumatic Valve - Kinfe gate valve birdirectional with pneumatic double acting fail last position actuator. ASCO Numatics Solenoid EF8342Ga, 120V, 4-way |  | 22-363R-06.0-DA-PROX-SOL |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 18 | FV_51200 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
SSD 2 - Knife-Gate Valve - 03 | C2NC-1400-SSDB-FV_51203 | C2NC-1400-SSDB | Valves | SSD 2 Pneumatic Valve |  | "STAFSIO" or similar | [7 empty] | AN-1156 A01 01 | 2 | FV_51203 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
SSD 2 - Ball Valve - 00 | C2NC-1400-SSDB-MV_51200 | C2NC-1400-SSDB | Valves | SSD 2 Manual Valve - SIMTECH TBB1016020 2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016020 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 2 | MV_51200 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | Flanged
SSD 2 - Knife-Gate Valve - 01 | C2NC-1400-SSDB-MV_51201 | C2NC-1400-SSDB | Valves | SSD 2 Manual Valve |  | "STAFSIO" or similar | [7 empty] | AN-1156 A01 01 | 2 | MV_51201 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Manual | Knife-Gate Valve | Manual | LUG
SSD 2 - Ball Valve - 02 | C2NC-1400-SSDB-MV_51202 | C2NC-1400-SSDB | Valves | SSD 2 Manual Valve |  | "EBRO" or similar | [7 empty] | AN-1156 A01 01 | 2 | MV_51202 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 2 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 2 - Ball Valve - 03 | C2NC-1400-SSDB-MV_51203 | C2NC-1400-SSDB | Valves | SSD 2 Manual Valve |  | "EBRO" or similar |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 2 | MV_51203 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.75 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 2 - Ball Valve - 04 | C2NC-1400-SSDB-MV_51204 | C2NC-1400-SSDB | Valves | SSD 2 Manual Valve |  | "EBRO" or similar |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 2 | MV_51204 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 2 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 2 - Ball Valve - 04 | C2NC-1400-SSDB-MV_51204 | C2NC-1400-SSDB | Valves | SSD 2 Manual Valve |  | "EBRO" or similar |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 3 | MV_51204 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 2 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 2 - 5/3 Way Manual Valve - 05 | C2NC-1400-SSDB-MV_51205 | C2NC-1400-SSDB | Valves | SSD 2 Manual Valve | [5 empty] | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 2 | MV_51205 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Manual | 5/3 Way Manual Valve | Manual
SSD 2 - 5/3 Way Manual Valve - 05 | C2NC-1400-SSDB-MV_51205 | C2NC-1400-SSDB | Valves | SSD 2 Manual Valve | [5 empty] | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 3 | MV_51205 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Manual | 5/3 Way Manual Valve | Manual
SSD 2 - Ball Valve - 06 | C2NC-1400-SSDB-MV_51206 | C2NC-1400-SSDB | Valves | SSD 2 Manual Valve |  | "EBRO" or similar |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 2 | MV_51206 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 2 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 2 - Ball Valve - 06 | C2NC-1400-SSDB-MV_51206 | C2NC-1400-SSDB | Valves | SSD 2 Manual Valve |  | "EBRO" or similar |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 3 | MV_51206 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 2 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 2 - Ball Valve - 07 | C2NC-1400-SSDB-MV_51207 | C2NC-1400-SSDB | Valves | SSD 2 Manual Valve |  | "EBRO" or similar | [7 empty] | AN-1156 A01 01 | 2 | MV_51207 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD B - Inline Mixer for Digestate Dewatering | C2NC-1400-SSDB-MX_51201 | C2NC-1400-SSDB | Equipment | Inline Mixer for Digestate Dewatering | UTS Products | [8 empty] | AN-0119 A01-01 | 2 | MX_51201 | [8 empty] | Mixer | [25 empty] | 5.9x6.6 | 8.23
SSD B - Mixer for Flocculation Tank | C2NC-1400-SSDB-MX_51202 | C2NC-1400-SSDB | Equipment | Mixer for Flocculation Tank | UTS Products | [8 empty] | AN-0119 A01-01 | 2 | MX_51202 | [8 empty] | Mixer | [25 empty] | 5.9x6.6 | 8.23
SSD 2 - Pressure Indicator Transmitter - PIT_51202 | C2NC-1400-SSDB-PIT_51202 | C2NC-1400-SSDB | Instruments | Pressure Indicator Transmitter within the SSD 2 system - PIT on top of Flocculation tank (TK-51202) | IFM | PG2797 |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 2 | PIT_51202 | [42 empty] | DSA |  |  |  | Pressure Transmitter w/ indicator |  | Analog
SSD 2 - Pressure Control Valve - 00 | C2NC-1400-SSDB-PRV_51200 | C2NC-1400-SSDB | Valves | SSD 2 Pressure Relief Valve |  | Multifix BG1-G1/4 2xIG |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 2 | PRV_51200 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Manual | Pressure Control Valve | Manual | THRD-F NPT
SSD 2 - Pressure Control Valve - 01 | C2NC-1400-SSDB-PRV_51201 | C2NC-1400-SSDB | Valves | SSD 2 Pressure Relief Valve |  | Multifix BG1-G1/4 2xIG |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 2 | PRV_51201 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Manual | Pressure Control Valve | Manual | THRD-F NPT
SSD B - Digestate Dewatering | C2NC-1400-SSDB-SSD_51200 | C2NC-1400-SSDB | Equipment | Digestate Dewatering | UTS Products | [8 empty] | AN-0119 A01-01 | 2 | SSD_51200 | [8 empty] | Solids Seperator Dewaterer | [25 empty] | 21.96 x 5.80 | 5.87
SSD 2 - Solenoid Valve - 00 | C2NC-1400-SSDB-SV_51200 | C2NC-1400-SSDB | Valves | SSD 2 Solenoid Valve |  | Buschjost-GmbH 8274600-9151-02400 |  |  |  | Buschjost |  |  |  | AN-1156 A01 01 | 2 | SV_51200 | [11 empty] | SSA1 | [11 empty] | 2 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD 2 - Solenoid Valve - 01 | C2NC-1400-SSDB-SV_51201 | C2NC-1400-SSDB | Valves | SSD 2 Solenoid Valve |  | Buschjost-GmbH 8274600-9151-02400 |  |  |  | Buschjost |  |  |  | AN-1156 A01 01 | 2 | SV_51201 | [11 empty] | SSA1 | [11 empty] | 2 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD 2 - Solenoid Valve - 02 | C2NC-1400-SSDB-SV_51202 | C2NC-1400-SSDB | Valves | SSD 2 Solenoid Valve |  | FESTO AG VUVS-L25-M52-MD-G14-F8-1B2 |  |  |  | Festo |  |  |  | AN-1156 A01 01 | 2 | SV_51202 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD 2 - Solenoid Valve - 03 | C2NC-1400-SSDB-SV_51203 | C2NC-1400-SSDB | Valves | SSD 2 Solenoid Valve |  | FESTO AG VUVS-L25-M52-MD-G14-F8-1B2 |  |  |  | Festo |  |  |  | AN-1156 A01 01 | 2 | SV_51203 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD B - Flocculation Tank | C2NC-1400-SSDB-TK_51202 | C2NC-1400-SSDB | Tanks | Flocculation Tank | UTS Products | [8 empty] | AN-0119 A01-01 | 2 | TK_51202 | [8 empty] | Tank | [25 empty] | 5.9x6.6 | 8.23
SSD3 | C2NC-1400-SSDC | C2NC-1400 | Locations And Facilities | SSD3
6 Inch HDPE SSD 3 Digestate Line 513_02 | C2NC-1400-SSDC-6 _ DSA _ 51302 _ HDPE | C2NC-1400-SSDC | Lines | 6 Inch HDPE Digestate Line | [9 empty] | AN-1156 A01 01 | 3 | 6 _ DSA _ 51302 _ HDPE | [10 empty] | Digestate | HDPE | 6 | Digestate Pumps | SSD C | N | 100 |  | 150 #
8 Inch PVC SSD 3 SSD Filtrate Line 513_01 | C2NC-1400-SSDC-8 _ FLT _ 51301 _ PVC | C2NC-1400-SSDC | Lines | 8 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 3 | 8 _ FLT _ 51301 _ PVC | [10 empty] | SSD Filtrate | PVC | 8 | SSD C | SSD Filtrate Sump | N | 100 |  | 150 #
SSD 3 - Swing Check Valve - 00 | C2NC-1400-SSDC-CV_51300 | C2NC-1400-SSDC | Valves | SSD 3 Check Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | CV_51300 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B | 2 |  |  | Manual | Swing Check Valve | N.A | Flanged
SSD 3 - Knife-Gate Valve - 00 | C2NC-1400-SSDC-FV_51300 | C2NC-1400-SSDC | Valves | SSD 3 Pneumatic Valve - Kinfe gate valve birdirectional with pneumatic double acting fail last position actuator. ASCO Numatics Solenoid EF8342Ga, 120V, 4-way |  | 22-363R-06.0-DA-PROX-SOL |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 18 | FV_51300 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
SSD 3 - Knife-Gate Valve - 03 | C2NC-1400-SSDC-FV_51303 | C2NC-1400-SSDC | Valves | SSD 3 Pneumatic Valve |  | "STAFSIO" or similar | [7 empty] | AN-1156 A01 01 | 3 | FV_51303 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
SSD 3 - Ball Valve - 00 | C2NC-1400-SSDC-MV_51300 | C2NC-1400-SSDC | Valves | SSD 3 Manual Valve - SIMTECH TBB1016020 2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016020 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 3 | MV_51300 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | Flanged
SSD 3 - Knife-Gate Valve - 01 | C2NC-1400-SSDC-MV_51301 | C2NC-1400-SSDC | Valves | SSD 3 Manual Valve |  | "STAFSIO" or similar | [7 empty] | AN-1156 A01 01 | 3 | MV_51301 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Manual | Knife-Gate Valve | Manual | LUG
SSD 3 - Ball Valve - 02 | C2NC-1400-SSDC-MV_51302 | C2NC-1400-SSDC | Valves | SSD 3 Manual Valve |  | "EBRO" or similar | [7 empty] | AN-1156 A01 01 | 3 | MV_51302 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 2 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 3 - Ball Valve - 03 | C2NC-1400-SSDC-MV_51303 | C2NC-1400-SSDC | Valves | SSD 3 Manual Valve |  | "EBRO" or similar |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 3 | MV_51303 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.75 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD 3 - Ball Valve - 07 | C2NC-1400-SSDC-MV_51307 | C2NC-1400-SSDC | Valves | SSD 3 Manual Valve |  | "EBRO" or similar | [7 empty] | AN-1156 A01 01 | 3 | MV_51307 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
SSD C - Inline Mixer for Digestate Dewatering | C2NC-1400-SSDC-MX_51301 | C2NC-1400-SSDC | Equipment | Inline Mixer for Digestate Dewatering | UTS Products | [8 empty] | AN-0119 A01-01 | 3 | MX_51301 | [8 empty] | Mixer | [25 empty] | 5.9x6.6 | 8.23
SSD C - Mixer for Flocculation Tank | C2NC-1400-SSDC-MX_51302 | C2NC-1400-SSDC | Equipment | Mixer for Flocculation Tank | UTS Products | [8 empty] | AN-0119 A01-01 | 3 | MX_51302 | [8 empty] | Mixer | [25 empty] | 5.9x6.6 | 8.23
SSD 3 - Pressure Indicator Transmitter - PIT_51302 | C2NC-1400-SSDC-PIT_51302 | C2NC-1400-SSDC | Instruments | Pressure Indicator Transmitter within the SSD 3 system - PIT on top of Flocculation tank (TK-51302) | IFM | PG2797 |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 3 | PIT_51302 | [42 empty] | DSA |  |  |  | Pressure Transmitter w/ indicator |  | Analog
SSD 3 - Pressure Control Valve - 00 | C2NC-1400-SSDC-PRV_51300 | C2NC-1400-SSDC | Valves | SSD 3 Pressure Relief Valve |  | Multifix BG1-G1/4 2xIG |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 3 | PRV_51300 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Manual | Pressure Control Valve | Manual | THRD-F NPT
SSD 3 - Pressure Control Valve - 01 | C2NC-1400-SSDC-PRV_51301 | C2NC-1400-SSDC | Valves | SSD 3 Pressure Relief Valve |  | Multifix BG1-G1/4 2xIG |  |  |  | UTS Bioenergy |  |  |  | AN-1156 A01 01 | 3 | PRV_51301 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Manual | Pressure Control Valve | Manual | THRD-F NPT
SSD C - Digestate Dewatering | C2NC-1400-SSDC-SSD_51300 | C2NC-1400-SSDC | Equipment | Digestate Dewatering | UTS Products | [8 empty] | AN-0119 A01-01 | 3 | SSD_51300 | [8 empty] | Solids Seperator Dewaterer | [25 empty] | 21.96 x 5.80 | 5.87
SSD 3 - Solenoid Valve - 00 | C2NC-1400-SSDC-SV_51300 | C2NC-1400-SSDC | Valves | SSD 3 Solenoid Valve |  | Buschjost-GmbH 8274600-9151-02400 |  |  |  | Buschjost |  |  |  | AN-1156 A01 01 | 3 | SV_51300 | [11 empty] | SSA1 | [11 empty] | 2 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD 3 - Solenoid Valve - 01 | C2NC-1400-SSDC-SV_51301 | C2NC-1400-SSDC | Valves | SSD 3 Solenoid Valve |  | Buschjost-GmbH 8274600-9151-02400 |  |  |  | Buschjost |  |  |  | AN-1156 A01 01 | 3 | SV_51301 | [11 empty] | SSA1 | [11 empty] | 2 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD 3 - Solenoid Valve - 02 | C2NC-1400-SSDC-SV_51302 | C2NC-1400-SSDC | Valves | SSD 3 Solenoid Valve |  | FESTO AG VUVS-L25-M52-MD-G14-F8-1B2 |  |  |  | Festo |  |  |  | AN-1156 A01 01 | 3 | SV_51302 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD 3 - Solenoid Valve - 03 | C2NC-1400-SSDC-SV_51303 | C2NC-1400-SSDC | Valves | SSD 3 Solenoid Valve |  | FESTO AG VUVS-L25-M52-MD-G14-F8-1B2 |  |  |  | Festo |  |  |  | AN-1156 A01 01 | 3 | SV_51303 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
SSD C - SSD C Flocculation Tank | C2NC-1400-SSDC-TK_51302 | C2NC-1400-SSDC | Tanks | SSD C Flocculation Tank | UTS Products | [8 empty] | AN-0119 A01-01 | 3 | TK_51302 | [8 empty] | Tank | [25 empty] | 5.9x6.6 | 8.23
Emusion Polymer SSD | C2NC-1400-SSDPOLY | C2NC-1400 | Locations And Facilities | Emusion Polymer SSD
1 Inch PVC Emusion Polymer SSD Polymer Line 351_15 | C2NC-1400-SSDPOLY-1 _ POL _ 35115 _ PVC | C2NC-1400-SSDPOLY | Lines | 1 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 1 _ POL _ 35115 _ PVC | [10 empty] | Polymer | PVC | 1 | SSD Emulsion Polymer Storage Tank | SSD Emulsion Polymer Makeup Unit | N | 100 |  | 150 #
1.5 Inch PVC Emusion Polymer SSD Polymer Line 351_19 | C2NC-1400-SSDPOLY-1.5 _ POL _ 35119 _ PVC | C2NC-1400-SSDPOLY | Lines | 1.5 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 1.5 _ POL _ 35119 _ PVC | [10 empty] | Polymer | PVC | 1.5 | SSD Polymer Pump A | SSD Polymer Pump A Expander | N | 100 |  | 150 #
1.5 Inch PVC Emusion Polymer SSD Polymer Line 351_21 | C2NC-1400-SSDPOLY-1.5 _ POL _ 35121 _ PVC | C2NC-1400-SSDPOLY | Lines | 1.5 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 1.5 _ POL _ 35121 _ PVC | [10 empty] | Polymer | PVC | 1.5 | SSD Polymer Pump B | SSD Polymer Pump B Expander | N | 100 |  | 150 #
1.5 Inch PVC Emusion Polymer SSD Polymer Line 351_22 | C2NC-1400-SSDPOLY-1.5 _ POL _ 35122 _ PVC | C2NC-1400-SSDPOLY | Lines | 1.5 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 1.5 _ POL _ 35122 _ PVC | [10 empty] | Polymer | PVC | 1.5 | SSD Polymer Pump C | SSD Polymer Pump C Expander | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_02 | C2NC-1400-SSDPOLY-2 _ POL _ 35102 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ POL _ 35102 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Recirculation Polymer Pump | SSD Emulsion Polymer Storage Tank | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_03 | C2NC-1400-SSDPOLY-2 _ POL _ 35103 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ POL _ 35103 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Polymer Pumps Header | SSD Polymer Pump A | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_04 | C2NC-1400-SSDPOLY-2 _ POL _ 35104 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ POL _ 35104 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Polymer Pumps Header | SSD Polymer Pump B | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_05 | C2NC-1400-SSDPOLY-2 _ POL _ 35105 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ POL _ 35105 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Polymer Pumps Header | SSD Polymer Pump C | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_06 | C2NC-1400-SSDPOLY-2 _ POL _ 35106 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 1 | 2 _ POL _ 35106 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Polymer System | SSD A | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_07 | C2NC-1400-SSDPOLY-2 _ POL _ 35107 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 2 | 2 _ POL _ 35107 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Polymer System | SSD B | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_08 | C2NC-1400-SSDPOLY-2 _ POL _ 35108 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 3 | 2 _ POL _ 35108 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Polymer System | SSD C | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_11 | C2NC-1400-SSDPOLY-2 _ POL _ 35111 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ POL _ 35111 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Polymer Aging Tank | SSD Polymer Pumps Header | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_16 | C2NC-1400-SSDPOLY-2 _ POL _ 35116 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ POL _ 35116 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Emulsion Polymer Makeup Unit | SSD Polymer Aging Tank | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_17 | C2NC-1400-SSDPOLY-2 _ POL _ 35117 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ POL _ 35117 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Polymer Recirc Pump Outlet PRV | SSD Polymer Recirc Pump Inlet | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_20 | C2NC-1400-SSDPOLY-2 _ POL _ 35120 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ POL _ 35120 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Polymer Pump A Expander | SSD Polymer Pump A Mixing Unit | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_23 | C2NC-1400-SSDPOLY-2 _ POL _ 35123 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ POL _ 35123 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Polymer Pump B Expander | SSD Polymer Pump B Mixing Unit | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Polymer Line 351_24 | C2NC-1400-SSDPOLY-2 _ POL _ 35124 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ POL _ 35124 _ PVC | [10 empty] | Polymer | PVC | 2 | SSD Polymer Pump C Expander | SSD Polymer Pump C Mixing Unit | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Potable Water Line 351_09 | C2NC-1400-SSDPOLY-2 _ PW _ 35109 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Potable Water Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ PW _ 35109 _ PVC | [10 empty] | Potable Water | PVC | 2 | Potable Water Inlet | SSD Polymer Make-Up Unit | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Potable Water Line 351_12 | C2NC-1400-SSDPOLY-2 _ PW _ 35112 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Potable Water Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ PW _ 35112 _ PVC | [10 empty] | Potable Water | PVC | 2 | Potable Water Inlet | SSD Polymer Pump C Mixing Unit | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Potable Water Line 351_13 | C2NC-1400-SSDPOLY-2 _ PW _ 35113 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Potable Water Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ PW _ 35113 _ PVC | [10 empty] | Potable Water | PVC | 2 | Potable Water Inlet | SSD Polymer Pump B Mixing Unit | N | 100 |  | 150 #
2 Inch PVC Emusion Polymer SSD Potable Water Line 351_14 | C2NC-1400-SSDPOLY-2 _ PW _ 35114 _ PVC | C2NC-1400-SSDPOLY | Lines | 2 Inch PVC Potable Water Line | [9 empty] | AN-1156 A01 01 | 4 | 2 _ PW _ 35114 _ PVC | [10 empty] | Potable Water | PVC | 2 | Potable Water Inlet | SSD Polymer Pump A Mixing Unit | N | 100 |  | 150 #
2.5 Inch PVC Emusion Polymer SSD Polymer Line 351_01 | C2NC-1400-SSDPOLY-25 _ POL _ 35101 _ PVC | C2NC-1400-SSDPOLY | Lines | 2.5 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 25 _ POL _ 35101 _ PVC | [10 empty] | Polymer | PVC | 2.5 | SSD Emulsion Polymer Storage Tank | SSD Recirculation Polymer Pump | N | 100 |  | 150 #
3 Inch PVC Emusion Polymer SSD Polymer Line 351_18 | C2NC-1400-SSDPOLY-3 _ POL _ 35118 _ PVC | C2NC-1400-SSDPOLY | Lines | 3 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 4 | 3 _ POL _ 35118 _ PVC | [10 empty] | Polymer | PVC | 3 | SSD Emulsion Polymer Storage Tank | Drain/Outlet | N | 100 |  | 150 #
Emusion Polymer SSD - Swing Check Valve - 00 | C2NC-1400-SSDPOLY-CV_35100 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Check Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | CV_35100 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B | 2 |  |  | Manual | Swing Check Valve | N.A | Flanged
Emusion Polymer SSD - Swing Check Valve - 01 | C2NC-1400-SSDPOLY-CV_35101 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Check Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | CV_35101 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B | 2 |  |  | Manual | Swing Check Valve | N.A | Flanged
Emusion Polymer SSD - Swing Check Valve - 02 | C2NC-1400-SSDPOLY-CV_35102 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Check Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | CV_35102 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B | 2 |  |  | Manual | Swing Check Valve | N.A | Flanged
Emusion Polymer SSD - Flow Indicator Transmitter - FIT_35100 | C2NC-1400-SSDPOLY-FIT_35100 | C2NC-1400-SSDPOLY | Instruments | Flow Indicator Transmitter within the Emusion Polymer SSD system - FIT on potable water feed line to activation mixing chamber (PHU-35100) | IFM | SID10ADBFKOW/LS-100-IRF |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | FIT_35100 | [42 empty] | POL |  |  |  | Flow Meter w/ indicator |  | Analog
Emusion Polymer SSD - Flow Indicator Transmitter - FIT_35101 | C2NC-1400-SSDPOLY-FIT_35101 | C2NC-1400-SSDPOLY | Instruments | Flow Indicator Transmitter within the Emusion Polymer SSD system - FIT on polymer feed line from aging tank to inline mixer (MX-51101) | Endress and Hauser | 5W4C50-AAALNM0DUA1KGA |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | FIT_35101 | [42 empty] | POL |  |  |  | Flow Meter w/ indicator |  | Analog
Emusion Polymer SSD - Flow Indicator Transmitter - FIT_35102 | C2NC-1400-SSDPOLY-FIT_35102 | C2NC-1400-SSDPOLY | Instruments | Flow Indicator Transmitter within the Emusion Polymer SSD system - FIT on polymer feed line from aging tank to inline mixer (MX-51201) | Endress and Hauser | 5W4C50-AAALNM0DUA1KGA |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | FIT_35102 | [42 empty] | POL |  |  |  | Flow Meter w/ indicator |  | Analog
Emusion Polymer SSD - Flow Indicator Transmitter - FIT_35103 | C2NC-1400-SSDPOLY-FIT_35103 | C2NC-1400-SSDPOLY | Instruments | Flow Indicator Transmitter within the Emusion Polymer SSD system - FIT on polymer feed line from aging tank to inline mixer (MX-51301) | Endress and Hauser | 5W4C50-AAALNM0DUA1KGA |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | FIT_35103 | [42 empty] | POL |  |  |  | Flow Meter w/ indicator |  | Analog
Emusion Polymer SSD - Level Indicator Transmitter - LIT_35100 | C2NC-1400-SSDPOLY-LIT_35100 | C2NC-1400-SSDPOLY | Instruments | Level Indicator Transmitter within the Emusion Polymer SSD system - LIT for Emulsion polymer storage tank (TK-35100) | Sitrans | Probe LU |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | LIT_35100 | [42 empty] | POL |  |  |  | Level Transmitter w/ indicator |  | Analog
Emusion Polymer SSD - Level Switch High - LSH_35101 | C2NC-1400-SSDPOLY-LSH_35101 | C2NC-1400-SSDPOLY | Instruments | Level Switch High within the Emusion Polymer SSD system - Level Switch for Aging tank (TK-35101) | McMaster-Carr | 4646K11 |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | LSH_35101 | [42 empty] | POL |  |  |  | Level Switch High |  | Digital
Emusion Polymer SSD - Level Transmitter - LT_35101 | C2NC-1400-SSDPOLY-LT_35101 | C2NC-1400-SSDPOLY | Instruments | Level Transmitter within the Emusion Polymer SSD system - LT for polymer aging tank (TK-35101) | IFM | pm-,25brea01-e-zvg/us |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | LT_35101 | [42 empty] | POL |  |  |  | Level Transmitter |  | Analog
Emusion Polymer SSD - SSD A Polymer Secondary Dilution Mixer | C2NC-1400-SSDPOLY-MIX_35102 | C2NC-1400-SSDPOLY | Equipment | SSD A Polymer Secondary Dilution Mixer | [9 empty] | AN-0119 A01-01 | 4 | MIX_35102 | [8 empty] | Static Mixer
Emusion Polymer SSD - SSD B Polymer Secondary Dilution Mixer | C2NC-1400-SSDPOLY-MIX_35103 | C2NC-1400-SSDPOLY | Equipment | SSD B Polymer Secondary Dilution Mixer | [9 empty] | AN-0119 A01-01 | 4 | MIX_35103 | [8 empty] | Static Mixer
Emusion Polymer SSD - SSD C Polymer Secondary Dilution Mixer | C2NC-1400-SSDPOLY-MIX_35104 | C2NC-1400-SSDPOLY | Equipment | SSD C Polymer Secondary Dilution Mixer | [9 empty] | AN-0119 A01-01 | 4 | MIX_35104 | [8 empty] | Static Mixer
Emusion Polymer SSD - Ball Valve - 00 | C2NC-1400-SSDPOLY-MV_35100 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve - SIMTECH TBB1016010 1" PVC/EPDM TU Ball Valve, Flange |  | TBB1016010 |  |  |  | FCX |  |  |  | AN-1156 A01 01 | 4 | MV_35100 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 01 | C2NC-1400-SSDPOLY-MV_35101 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35101 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 02 | C2NC-1400-SSDPOLY-MV_35102 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35102 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 03 | C2NC-1400-SSDPOLY-MV_35103 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35103 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 04 | C2NC-1400-SSDPOLY-MV_35104 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35104 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 05 | C2NC-1400-SSDPOLY-MV_35105 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35105 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 06 | C2NC-1400-SSDPOLY-MV_35106 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve - SIMTECH TBB1016020 2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016020 |  |  |  | FCX |  |  |  | AN-1156 A01 01 | 4 | MV_35106 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Gate Valve - 15 | C2NC-1400-SSDPOLY-MV_35115 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve | [5 empty] | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35115 | [11 empty] | PVC | [11 empty] | 2 |  |  | Manual | Gate Valve | Manual | Flanged
Emusion Polymer SSD - Gate Valve - 16 | C2NC-1400-SSDPOLY-MV_35116 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve | [5 empty] | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35116 | [11 empty] | PVC | [11 empty] | 2 |  |  | Manual | Gate Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 17 | C2NC-1400-SSDPOLY-MV_35117 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve - SIMTECH TBB1016030 3" PVC/EPDM TU Ball Valve, Flange |  | TBB1016030 |  |  |  | FCX |  |  |  | AN-1156 A01 01 | 4 | MV_35117 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 3 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 18 | C2NC-1400-SSDPOLY-MV_35118 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve - SIMTECH TBB1016025 2.5" PVC/EPDM TU Ball Valve, Flange |  | TBB1016025 |  |  |  | FCX |  |  |  | AN-1156 A01 01 | 4 | MV_35118 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2.5 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 21 | C2NC-1400-SSDPOLY-MV_35121 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35121 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 22 | C2NC-1400-SSDPOLY-MV_35122 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve |  | TBD |  |  |  | FCX |  |  |  | AN-1156 A01 01 | 4 | MV_35122 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Knife-Gate Valve - 23 | C2NC-1400-SSDPOLY-MV_35123 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve - 2" 20-3636R-02.0-HW SERIES 20 KNIFE GATE VALVEBODY AND GATE 316SS SEAT EPDM MANUAL HAND WHEEL |  | 495ORB200203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 4 | MV_35123 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 2 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Emusion Polymer SSD - Ball Valve - 24 | C2NC-1400-SSDPOLY-MV_35124 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35124 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 25 | C2NC-1400-SSDPOLY-MV_35125 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35125 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 27 | C2NC-1400-SSDPOLY-MV_35127 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve |  | TBD |  |  |  | FCX |  |  |  | AN-1156 A01 01 | 4 | MV_35127 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | Flanged
Emusion Polymer SSD - Ball Valve - 29 | C2NC-1400-SSDPOLY-MV_35129 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35129 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | TBD
Emusion Polymer SSD - Gate Valve - 31 | C2NC-1400-SSDPOLY-MV_35131 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Manual Valve | [5 empty] | Velodyne |  |  |  | AN-1156 A01 01 | 4 | MV_35131 | [11 empty] | PVC | [11 empty] | 2 |  |  | Manual | Gate Valve | Manual | Flanged
Emusion Polymer SSD - Mixer for SSD Polmyer System Aging Tank | C2NC-1400-SSDPOLY-MX_35101 | C2NC-1400-SSDPOLY | Equipment | Mixer for SSD Polmyer System Aging Tank | [9 empty] | AN-0119 A01-01 | 4 | MX_35101 | [8 empty] | Mixer
Emusion Polymer SSD - Recirculation pump for SSD Emulsion Polymer Storage Tank | C2NC-1400-SSDPOLY-P_35100 | C2NC-1400-SSDPOLY | Equipment | Recirculation pump for SSD Emulsion Polymer Storage Tank | [9 empty] | AN-0119 A01-01 | 4 | P_35100 | [8 empty] | Pump
Emusion Polymer SSD - Polymer Feed Pump for SSD A | C2NC-1400-SSDPOLY-P_35102 | C2NC-1400-SSDPOLY | Equipment | Polymer Feed Pump for SSD A | [9 empty] | AN-0119 A01-01 | 4 | P_35102 | [8 empty] | Pump
Emusion Polymer SSD - Polymer Feed Pump for SSD B | C2NC-1400-SSDPOLY-P_35103 | C2NC-1400-SSDPOLY | Equipment | Polymer Feed Pump for SSD B | [9 empty] | AN-0119 A01-01 | 4 | P_35103 | [8 empty] | Pump
Emusion Polymer SSD - Polymer Feed Pump for SSD C | C2NC-1400-SSDPOLY-P_35104 | C2NC-1400-SSDPOLY | Equipment | Polymer Feed Pump for SSD C | [9 empty] | AN-0119 A01-01 | 4 | P_35104 | [8 empty] | Pump
Emusion Polymer SSD - Emulsion Polymer Make-up unit for SSDs | C2NC-1400-SSDPOLY-PHU_35100 | C2NC-1400-SSDPOLY | Equipment | Emulsion Polymer Make-up unit for SSDs | [9 empty] | AN-0119 A01-01 | 4 | PHU_35100 | [8 empty] | Polymer Makeup Unit
Emusion Polymer SSD - Pressure Indicator - PI_35100 | C2NC-1400-SSDPOLY-PI_35100 | C2NC-1400-SSDPOLY | Instruments | Pressure Indicator within the Emusion Polymer SSD system - Pressure indicator for polymer storage recirculation pump (P-35100) | Ashcroft | 1008AL 61-1008AL-02b 160# |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | PI_35100 | [42 empty] | POL |  |  |  | Pressure Indicator
Emusion Polymer SSD - Pressure Indicator - PI_35101 | C2NC-1400-SSDPOLY-PI_35101 | C2NC-1400-SSDPOLY | Instruments | Pressure Indicator within the Emusion Polymer SSD system - Pressure indicator for potable water line to polymer activation chamber (PHU-85100) | Ashcroft | 1008AL 61-1008AL-02b 160# |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | PI_35101 | [42 empty] | PW |  |  |  | Pressure Indicator
Emusion Polymer SSD - Pressure Indicator - PI_35102 | C2NC-1400-SSDPOLY-PI_35102 | C2NC-1400-SSDPOLY | Instruments | Pressure Indicator within the Emusion Polymer SSD system - Pressure indicator for potable water prior to (MIX-35102) | Ashcroft | 1008AL 61-1008AL-02b 160# |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | PI_35102 | [42 empty] | PW |  |  |  | Pressure Indicator
Emusion Polymer SSD - Pressure Indicator - PI_35103 | C2NC-1400-SSDPOLY-PI_35103 | C2NC-1400-SSDPOLY | Instruments | Pressure Indicator within the Emusion Polymer SSD system - Pressure indicator for potable water prior to (MIX-35103) | Ashcroft | 1008AL 61-1008AL-02b 160# |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | PI_35103 | [42 empty] | PW |  |  |  | Pressure Indicator
Emusion Polymer SSD - Pressure Indicator - PI_35104 | C2NC-1400-SSDPOLY-PI_35104 | C2NC-1400-SSDPOLY | Instruments | Pressure Indicator within the Emusion Polymer SSD system - Pressure indicator for potable water prior to (MIX-35104) | Ashcroft | 1008AL 61-1008AL-02b 160# |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | PI_35104 | [42 empty] | PW |  |  |  | Pressure Indicator
Emusion Polymer SSD - Pressure Indicator - PI_35105 | C2NC-1400-SSDPOLY-PI_35105 | C2NC-1400-SSDPOLY | Instruments | Pressure Indicator within the Emusion Polymer SSD system - Pressure indicator for potable water prior to MIX-35103) | [5 empty] | Velodyne |  |  |  | AN-1156 A01 01 | 4 | PI_35105 | [42 empty] | PW |  |  |  | Pressure Indicator
Emusion Polymer SSD - Pressure Indicator - PI_35106 | C2NC-1400-SSDPOLY-PI_35106 | C2NC-1400-SSDPOLY | Instruments | Pressure Indicator within the Emusion Polymer SSD system - Pressure indicator for potable water prior to MIX-35102) | [9 empty] | AN-1156 A01 01 | 4 | PI_35106 | [42 empty] | PW |  |  |  | Pressure Indicator
Emusion Polymer SSD - Pressure Indicator - PI_35107 | C2NC-1400-SSDPOLY-PI_35107 | C2NC-1400-SSDPOLY | Instruments | Pressure Indicator within the Emusion Polymer SSD system - Pressure indicator for polymer from activation chamber to aging tank (TK-35101) | Ashcroft | 1008AL 61-1008AL-02b 160# |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | PI_35107 | [42 empty] | POL |  |  |  | Pressure Indicator
Emusion Polymer SSD - Pressure Relief Valve - 00 | C2NC-1400-SSDPOLY-PRV_35100 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Pressure Relief Valve | [5 empty] | Velodyne |  |  |  | AN-1156 A01 01 | 4 | PRV_35100 | [11 empty] | PVC | [11 empty] | 2 |  |  | Manual | Pressure Relief Valve | TBD | TBD
Emusion Polymer SSD - Pressure Switch High - PSH_35100 | C2NC-1400-SSDPOLY-PSH_35100 | C2NC-1400-SSDPOLY | Instruments | Pressure Switch High within the Emusion Polymer SSD system - Pressure switch high after SSD recirculation polymer pump (P-35100) | Ashcroft | Type 400 B series, B424B 100psi |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | PSH_35100 | [42 empty] | POL |  |  |  | Pressure Switch High |  | Digital
Emusion Polymer SSD - Solenoid Valve - 00 | C2NC-1400-SSDPOLY-SV_35100 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Solenoid Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | SV_35100 | [11 empty] | PVC | [10 empty] | TBD | 2 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
Emusion Polymer SSD - Solenoid Valve - 02 | C2NC-1400-SSDPOLY-SV_35102 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Solenoid Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | SV_35102 | [11 empty] | PVC | [10 empty] | TBD | 2 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
Emusion Polymer SSD - Solenoid Valve - 03 | C2NC-1400-SSDPOLY-SV_35103 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Solenoid Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | SV_35103 | [11 empty] | PVC | [10 empty] | TBD | 2 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
Emusion Polymer SSD - Solenoid Valve - 04 | C2NC-1400-SSDPOLY-SV_35104 | C2NC-1400-SSDPOLY | Valves | Emusion Polymer SSD Solenoid Valve |  | TBD |  |  |  | Velodyne |  |  |  | AN-1156 A01 01 | 4 | SV_35104 | [11 empty] | PVC | [10 empty] | TBD | 2 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
Emusion Polymer SSD - Emulsion polymer storage tank for SSD polymer system | C2NC-1400-SSDPOLY-TK_35100 | C2NC-1400-SSDPOLY | Tanks | Emulsion polymer storage tank for SSD polymer system | [9 empty] | AN-0119 A01-01 | 4 | TK_35100 | [8 empty] | Tank
Emusion Polymer SSD - Aging tank for SSD polymer system | C2NC-1400-SSDPOLY-TK_35101 | C2NC-1400-SSDPOLY | Tanks | Aging tank for SSD polymer system | [9 empty] | AN-0119 A01-01 | 4 | TK_35101 | [8 empty] | Tank

## 1500 - Gas Plant
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual RQD | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | horsepower | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Connection Type | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | *Any Custom Fields* | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes
1500 - GAS PLANT | C2NC-1500 | C2NC | Locations and Facilities | GAS PLANT
Gas Plant Active Carbon Vessels | C2NC-1500-ACV | C2NC-1500 | Locations and Facilities | Gas Plant Active Carbon Vessels
Gas Plant Bioreactor and Aeration | C2NC-1500-BR | C2NC-1500 | Locations and Facilities | Gas Plant Bioreactor and Aeration
Gas Plant Compressed Gas Treatment | C2NC-1500-CGT | C2NC-1500 | Locations and Facilities | Gas Plant Compressed Gas Treatment
Gas Plant Chemical Dosing | C2NC-1500-CHEM | C2NC-1500 | Locations and Facilities | Gas Plant Chemical Dosing
Gas Plant Circulation | C2NC-1500-CIRC | C2NC-1500 | Locations and Facilities | Gas Plant Circulation
Gas Plant Cooling | C2NC-1500-CLG | C2NC-1500 | Locations and Facilities | Gas Plant Cooling
Gas Plant Caustic Scrubber | C2NC-1500-CS | C2NC-1500 | Locations and Facilities | Gas Plant Caustic Scrubber
Gas Plant Container Unit | C2NC-1500-CU | C2NC-1500 | Locations and Facilities | Gas Plant Container Unit
Gas Plant Dilution Water | C2NC-1500-DIL | C2NC-1500 | Locations and Facilities | Gas Plant Dilution Water
Gas Plant Feed Gas Compressor | C2NC-1500-FGC | C2NC-1500 | Locations and Facilities | Gas Plant Feed Gas Compressor
Gas Plant Gas Analyzer | C2NC-1500-GA | C2NC-1500 | Locations and Facilities | Gas Plant Gas Analyzer
Gas Plant Gas Compressor | C2NC-1500-GC | C2NC-1500 | Locations and Facilities | Gas Plant Gas Compressor
Gas Plant Membranes | C2NC-1500-MBR | C2NC-1500 | Locations and Facilities | Gas Plant Membranes
Gas Plant Measurement Loop | C2NC-1500-MEAS | C2NC-1500 | Locations and Facilities | Gas Plant Measurement Loop
Gas Plant Non-Hazardous Process Room | C2NC-1500-NHPR | C2NC-1500 | Locations and Facilities | Gas Plant Non-Hazardous Process Room
Gas Plant Pre-Processing | C2NC-1500-PRE | C2NC-1500 | Locations and Facilities | Gas Plant Pre-Processing
Gas Plant Settler and Sludge Removal | C2NC-1500-SLG | C2NC-1500 | Locations and Facilities | Gas Plant Settler and Sludge Removal
Caustic scrubber Butterfly valve V100 | C2NC-1500-CS-V_100 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Blow flow at gas inlet | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263 | 2A | BR-A-V100 | [5 empty] | Raw biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Raw biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  |  |  | Butterfly valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Butterfly valve |  |  | V | V | Valves
Caustic scrubber Ball valve V101 | C2NC-1500-CS-V_101 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V101 | [5 empty] | Raw biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Raw biogas | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Ball valve |  |  | V | DV | Valves
Caustic scrubber Ball valve V102 | C2NC-1500-CS-V_102 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V102 | [5 empty] | Raw biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Raw biogas | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Ball valve |  |  | V | BV | Valves
Circulation pumps Butterfly valve AV315 | C2NC-1500-CIRC-AV_315 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block flow to discharge | Apollo | 215L-04SSP8TA0 150# 316SS Lug Butterfly Valve with Spring return Rack & Pinion Actuator Fail Close | [8 empty] | 9263 | 2B | BR-A-AV315 | [5 empty] | Cooling water (50% propylene glycol) | AISI 316 / RTFM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Cooling water (50% propylene glycol) | AISI 316 / RTFM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Butterfly valve |  |  | AV | AV | Valves
Caustic scrubber Ball valve V103 | C2NC-1500-CS-V_103 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Block pressure transmitter | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V103 | [5 empty] | Raw biogas | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Raw biogas | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Ball valve |  |  | V | PCV | Valves
Circulation pumps Pneumatic actuator AV315 | C2NC-1500-CIRC-AV_315 | C2NC-1500-CIRC | Valves | Circulation pumps Pneumatic actuator. Function: Deliver instrument air | Air Con | Included AV315 | [8 empty] | 9263 | 2B | BR-A-AV315 | [6 empty] | Composition of materials |  |  | Pneumatic actuator | [13 empty] | Composition of materials |  |  |  |  | Pneumatic actuator | [17 empty] | Pneumatic actuator |  |  | AV | OPS | Valves
Circulation pumps Solenoid valve AV315 | C2NC-1500-CIRC-AV_315 | C2NC-1500-CIRC | Valves | Circulation pumps Solenoid valve. Function: Switch instrument air to BR-A-AV315 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2B | BR-A-AV315 |  | 24 VDC | < 0,5 |  |  | Instrument Air | Composition of materials |  |  | Solenoid valve | [11 empty] | 24 VDC | Instrument Air | Composition of materials |  |  |  |  | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | UPSO | Valves
Caustic scrubber Ball valve V105 | C2NC-1500-CS-V_105 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V105 | [5 empty] | Raw biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Raw biogas | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Ball valve |  |  | V | OPSO | Valves
Caustic scrubber Biogas Feed Pipe BFP200 | C2NC-1500-CS-BFP_200 | C2NC-1500-CS | Lines | Caustic scrubber Biogas Feed Pipe. Function: 0 |  | design by MTE | [8 empty] | 9263 | 2A | BR-A-BFP200 | [12 empty] | FRP
Caustic scrubber Scrubber S200 | C2NC-1500-CS-S_200 | C2NC-1500-CS | Equipment | Caustic scrubber Scrubber. Function: Removal of H2S | Midwestern Fabricators | According drawing DMT | [8 empty] | 9263 | 2A | BR-A-S200 | [5 empty] | Raw biogas | FRP | Ø2743mm h=13200mm |  | Scrubber |  |  | AISI 316 | 1" NPT / 2"
Caustic scrubber Spraying Nozzle SN200 | C2NC-1500-CS-SN_200 | C2NC-1500-CS | Equipment | Caustic scrubber Spraying Nozzle. Function: Foam removal | Bete | TFXP Full cone spiral spray nozzle TF40 | [8 empty] | 9263 | 2A | BR-A-SN200 | [5 empty] | Process water | AISI 316 | 1" NPT |  | Spraying Nozzle |  |  | PP
Caustic scrubber Spray nozzle feed pipe SFP200 | C2NC-1500-CS-SFP_200 | C2NC-1500-CS | Lines | Caustic scrubber Spray nozzle feed pipe. Function: mounting of spray nozzle | DMT | according 9263-8019 | [8 empty] | 9263 | 2A | BR-A-SFP200 | [12 empty] | AISI 316 | 1" NPT / 2"
Caustic scrubber Support plate SP200 | C2NC-1500-CS-SP_200 | C2NC-1500-CS | Equipment | Caustic scrubber Support plate. Function: support packing | MTE | MSP43 support plate | [8 empty] | 9263 | 2A | BR-A-SP200 | [5 empty] | Raw biogas | PP | Ø = 2700mm |  | Support plate
Caustic scrubber Packing material PM200 | C2NC-1500-CS-PM_200 | C2NC-1500-CS | Equipment | Caustic scrubber Packing material. Function: Increase contact area | RVT | 1,5" (38mm) Raflux Ring 38-8 Tower Packing | [8 empty] | 9263 | 2A | BR-A-PM200 | [5 empty] | Raw biogas | PP | Ø = 2700mm |  | Packing material
Caustic scrubber Packing grid PG200 | C2NC-1500-CS-PG_200 | C2NC-1500-CS | Equipment | Caustic scrubber Packing grid. Function: 0 | MTE | [9 empty] | 9263 | 2A | BR-A-PG200 | [6 empty] | PP |  |  | Packing grid
Caustic scrubber Liquid distributor LD200 | C2NC-1500-CS-LD_200 | C2NC-1500-CS | Equipment | Caustic scrubber Liquid distributor. Function: Water distribution | MTE | Trough type liquid distributor, type MLD 131 | [8 empty] | 9263 | 2A | BR-A-LD200 | [5 empty] | Raw biogas | PP | Ø = 2700mm |  | Liquid distributor
Caustic scrubber Liquid feed pipe LFP200 | C2NC-1500-CS-LFP_200 | C2NC-1500-CS | Lines | Caustic scrubber Liquid feed pipe. Function: 0 | MTE | [9 empty] | 9263 | 2A | BR-A-LFP200 | [12 empty] | PP
Caustic scrubber Demister DM200 | C2NC-1500-CS-DM_200 | C2NC-1500-CS | Equipment | Caustic scrubber Demister. Function: Gas liquid separation | MTE | Vane type demister | [8 empty] | 9263 | 2A | BR-A-DM200 | [5 empty] | Raw biogas | PP | Ø700*150 mm |  | Demister |  |  |  | 1" NPT / 2"
Caustic scrubber Pressure safety valve PZV200 | C2NC-1500-CS-PZV_200 | C2NC-1500-CS | Valves | Caustic scrubber Pressure safety valve. Function: Guard column against high pressure scenarios | Rampini | High pressure relief valve dwg. 9 A | [8 empty] | 9263 | 2A | BR-A-PZV200 | [5 empty] | Clean biogas | AISI316L / PTFE | 10" 150# |  | Pressure safety valve | [12 empty] | Clean biogas | AISI316L / PTFE | 10" 150# |  |  |  | Pressure safety valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Pressure safety valve |  |  | PZV | FS | Instruments
Caustic scrubber Ball valve V107 | C2NC-1500-CS-V_107 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V107 | [5 empty] | Clean biogas | AISI 316 / PTFE | 2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | AISI 316 / PTFE | 2" NPT |  |  |  | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | FIS | Instruments
Caustic scrubber Ball valve V108 | C2NC-1500-CS-V_108 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Block pressure transmitter | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V108 | [5 empty] | Clean biogas | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | TT | Instruments
Circulation pumps Butterfly valve AV316 | C2NC-1500-CIRC-AV_316 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Bypass heat exchanger | Apollo | 215L-04SSP8TA0 150# 316SS Lug Butterfly Valve with Spring return Rack & Pinion Actuator Fail Open | [8 empty] | 9263 | 2B | BR-A-AV316 | [5 empty] | Cooling water (50% propylene glycol) | AISI 316 / RTFM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Cooling water (50% propylene glycol) | AISI 316 / RTFM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Butterfly valve |  |  | AV | TIT | Instruments
Circulation pumps Pneumatic actuator AV316 | C2NC-1500-CIRC-AV_316 | C2NC-1500-CIRC | Valves | Circulation pumps Pneumatic actuator. Function: Deliver instrument air | Air Con | Included AV316 | [8 empty] | 9263 | 2B | BR-A-AV316 | [6 empty] | Composition of materials |  |  | Pneumatic actuator | [13 empty] | Composition of materials |  |  |  |  | Pneumatic actuator | [17 empty] | Pneumatic actuator |  |  | AV | PT | Instruments
Caustic scrubber Butterfly valve V106 | C2NC-1500-CS-V_106 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Block flow scrubber bypass | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263 | 2A | BR-A-V106 | [5 empty] | Clean biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Clean biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  |  |  | Butterfly valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Butterfly valve |  |  | V | PIT | Instruments
Caustic scrubber Ball valve V110 | C2NC-1500-CS-V_110 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V110 | [5 empty] | Clean biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | FT | Instruments
Circulation pumps Solenoid valve AV316 | C2NC-1500-CIRC-AV_316 | C2NC-1500-CIRC | Valves | Circulation pumps Solenoid valve. Function: Switch instrument air to BR-A-AV316 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2B | BR-A-AV316 |  | 24 VDC | < 0,5 |  |  | Instrument Air | Composition of materials |  |  | Solenoid valve | [11 empty] | 24 VDC | Instrument Air | Composition of materials |  |  |  |  | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | FIT | Instruments
Caustic scrubber Ball valve V111 | C2NC-1500-CS-V_111 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V111 | [5 empty] | Clean biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | QT | Instruments
Caustic scrubber Ball valve V112 | C2NC-1500-CS-V_112 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V112 | [5 empty] | Clean biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | LT | Instruments
Caustic scrubber Butterfly valve V113 | C2NC-1500-CS-V_113 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Block flow after scrubber | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263 | 2A | BR-A-V113 | [5 empty] | Clean biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Clean biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  |  |  | Butterfly valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Butterfly valve |  |  | V | LEL | Instruments
Caustic scrubber Spectacle flange SF100 | C2NC-1500-CS-SF_100 | C2NC-1500-CS | Equipment | Caustic scrubber Spectacle flange. Function: Block gas flow | Eriks | Spectacle flanges AISI 316 ANSI P265-GH 150 16" 25 | [8 empty] | 9263 | 2A | BR-A-SF100 | [5 empty] | Clean biogas | AISI 316 | 16" 150# |  | Spectacle flange
Caustic scrubber Ball valve V114 | C2NC-1500-CS-V_114 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V114 | [5 empty] | Clean biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | FIR | Instruments
Caustic scrubber Butterfly valve V115 | C2NC-1500-CS-V_115 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Block flow to flare | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263 | 2A | BR-A-V115 | [5 empty] | Clean biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Clean biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  |  |  | Butterfly valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Butterfly valve |  |  | V | QITA | Instruments
Circulation pumps Ball valve AV330 | C2NC-1500-CIRC-AV_330 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block flow to discharge | Flotite | 1" 320-SS-2-FFF-025-CDA52-PERP Fail Close | [8 empty] | 9263 | 2B | BR-A-AV330 | [5 empty] | Process water | AISI 316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | AISI 316 / PTFE | 1" |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | AV | FT | Instruments
Circulation pumps Pneumatic actuator AV330 | C2NC-1500-CIRC-AV_330 | C2NC-1500-CIRC | Valves | Circulation pumps Pneumatic actuator. Function: Deliver instrument air to AV330 | Air Con | Included AV330 | [8 empty] | 9263 | 2B | BR-A-AV330 | [6 empty] | Composition of materials |  |  | Pneumatic actuator | [13 empty] | Composition of materials |  |  |  |  | Pneumatic actuator | [17 empty] | Pneumatic actuator |  |  | AV | FIT | Instruments
Circulation pumps Solenoid valve AV330 | C2NC-1500-CIRC-AV_330 | C2NC-1500-CIRC | Valves | Circulation pumps Solenoid valve. Function: Switch instrument air to BR-A-AV330 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2B | BR-A-AV330 |  | 24 VDC | < 0,5 |  |  | Instrument Air | Composition of materials |  |  | Solenoid valve | [11 empty] | 24 VDC | Instrument Air | Composition of materials |  |  |  |  | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | SL | Instruments
Measurement loop and GQA Ball valve AV360 | C2NC-1500-MEAS-AV_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Ball valve. Function: Block flow to analysis | Flotite | 1" 320-SS-2-FFF-025-CDA52-PERP Fail Close | [8 empty] | 9263 | 2G | BR-A-AV360 | [5 empty] | Process water | AISI 316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | AISI 316 / PTFE | 1" |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | AV | ES | Instruments
Measurement loop and GQA Pneumatic actuator AV360 | C2NC-1500-MEAS-AV_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Pneumatic actuator. Function: Deliver instrument air to AV360 | Air Con | Included AV360 | [8 empty] | 9263 | 2G | BR-A-AV360 | [5 empty] | - | Composition of materials | - |  | Pneumatic actuator | [12 empty] | - | Composition of materials | - |  |  |  | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | SI | Instruments
Measurement loop and GQA Solenoid valve AV360 | C2NC-1500-MEAS-AV_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Solenoid valve. Function: Switch instrument air to BR-A-AV360 | Asco | Included AV360 | [8 empty] | 9263 | 2G | BR-A-AV360 |  | 24 VDC | < 0,5 |  |  | Instrument Air | Composition of materials |  |  | Solenoid valve | [11 empty] | 24 VDC | Instrument Air | Composition of materials |  |  |  |  | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | P | Equipment
Circulation pumps Check valve CV721 | C2NC-1500-CIRC-CV_721 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow | Georg Fischer | Type 562 | [8 empty] | 9263 | 2B | BR-A-CV721 | [5 empty] | Nutrients | PP/ EPDM | 1/2" |  | Check valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Nutrients | PP/ EPDM | 1/2" |  |  |  | Check valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Check valve |  |  | CV | GC | Equipment
Circulation pumps Check valve CV731 | C2NC-1500-CIRC-CV_731 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow | Georg Fischer | Type 562 | [8 empty] | 9263 | 2B | BR-A-CV731 | [5 empty] | Antifoam | PP/ EPDM | 1/2" |  | Check valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Antifoam | PP/ EPDM | 1/2" |  |  |  | Check valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Check valve |  |  | CV | FB | Equipment
Circulation pumps Check valve CV701 | C2NC-1500-CIRC-CV_701 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Keep pressure in supply line | Georg Fischer | Type 562 | [8 empty] | 9263 | 2B | BR-A-CV701 | [5 empty] | Caustic | PP/ EPDM | 1/2" |  | Check valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Caustic | PP/ EPDM | 1/2" |  |  |  | Check valve |  |  |  |  | Caustic | [9 empty] | Caustic |  |  | Check valve |  |  | CV | VB | Equipment
Circulation pumps Ball valve V701 | C2NC-1500-CIRC-V_701 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block caustic flow | Georg Fischer | Type 546 | [8 empty] | 9263 | 2B | BR-A-V701 | [5 empty] | Caustic | PP/ EPDM | 1/2" |  | Ball valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Caustic | PP/ EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Caustic | [9 empty] | Caustic |  |  | Ball valve |  |  | V | M | Equipment
Circulation pumps Ball valve V726 | C2NC-1500-CIRC-V_726 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block li ne | Georg Fischer | Type 546 | [8 empty] | 9263 | 2B | BR-A-V726 | [5 empty] | Nutrients | PP/ EPDM | 1/2" |  | Ball valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Nutrients | PP/ EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V | S | Equipment
Circulation pumps Ball valve V736 | C2NC-1500-CIRC-V_736 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block li ne | Georg Fischer | Type 546 | [8 empty] | 9263 | 2B | BR-A-V736 | [5 empty] | Antifoam | PP/ EPDM | 1/2" |  | Ball valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Antifoam | PP/ EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V | FB | Equipment
Measurement loop and GQA Ball valve AV361 | C2NC-1500-MEAS-AV_361 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Ball valve. Function: Open/close rinsing water to sensors | Flotite | 1" 320-SS-2-FFF-025-CDA52-PERP Fail Close | [8 empty] | 9263 | 2G | BR-A-AV361 | [5 empty] | Process water | AISI 316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | AISI 316 / PTFE | 1" |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | AV | MX.X.XX | Equipment
Measurement loop and GQA Pneumatic actuator AV361 | C2NC-1500-MEAS-AV_361 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Pneumatic actuator. Function: Deliver instrument air to AV361 | Air Con | Included AV361 | [8 empty] | 9263 | 2G | BR-A-AV361 | [5 empty] | - | Composition of materials | - |  | Pneumatic actuator | [12 empty] | - | Composition of materials | - |  |  |  | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | HE | Equipment
Circulation pumps Pump P301 | C2NC-1500-CIRC-P_301 | C2NC-1500-CIRC | Equipment | Circulation pumps Pump. Function: Circulation Pump | Verder | MCP3 centrifugal pump | [8 empty] | 9263 | 2B | BR-A-P301 | [5 empty] | Process water | composition | 6" inlet / 5" outlet |  | Pump
Circulation pumps Motor P301_M | C2NC-1500-CIRC-P_301_M | C2NC-1500-CIRC | Equipment | Circulation pumps Motor. Function: Drive P301 | Verder | MCP3 centrifugal pump | [8 empty] | 9263 | 2B | BR-A-P301_M |  | 48 VAC | 31,1 |  | 29,5 | - | composition | - |  | Motor
Measurement loop and GQA Solenoid valve AV361 | C2NC-1500-MEAS-AV_361 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Solenoid valve. Function: Switch instrument air to BR-A-AV361 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2G | BR-A-AV361 |  | 24 VDC | < 0,5 |  |  | Instrument Air | Composition of materials |  |  | Solenoid valve | [11 empty] | 24 VDC | Instrument Air | Composition of materials |  |  |  |  | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | HE | Equipment
Settler and sludge pump Butterfly valve AV451 | C2NC-1500-SLG-AV_451 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Open/close sulphur sludge recycling | Apollo | 2 Apollo 215L-02SSP8TA0 150# 316SS Lug Butterfly Valve with Spring return Rack & Pinion Actuator Fail Close | [8 empty] | 9263 | 2D | BR-A-AV451 | [5 empty] | Sludge | AISI 316 / RTFM | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Sludge | AISI 316 / RTFM | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Butterfly valve |  |  | AV | FA | Equipment
Settler and sludge pump Pneumatic actuator AV451 | C2NC-1500-SLG-AV_451 | C2NC-1500-SLG | Valves | Settler and sludge pump Pneumatic actuator. Function: Deliver instrument air to AV451 | Air Con | Included AV451 | [8 empty] | 9263 | 2D | BR-A-AV451 | [5 empty] | - | Composition of materials | - |  | Pneumatic actuator | [12 empty] | - | Composition of materials | - |  |  |  | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | GR | Equipment
Settler and sludge pump Solenoid valve AV451 | C2NC-1500-SLG-AV_451 | C2NC-1500-SLG | Valves | Settler and sludge pump Solenoid valve. Function: Switch instrument air to BR-A-AV451 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2D | BR-A-AV451 |  | 24 VDC | < 0,5 |  |  | Instrument Air | Composition of materials |  |  | Solenoid valve | [11 empty] | 24 VDC | Instrument Air | Composition of materials |  |  |  |  | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | V | Equipment
Settler and sludge pump Butterfly valve AV452 | C2NC-1500-SLG-AV_452 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Open/close sulphur discharge downstream pump | Apollo | 2 Apollo 215L-02SSP8TA0 150# 316SS Lug Butterfly Valve with Spring return Rack & Pinion Actuator Fail Open | [8 empty] | 9263 | 2D | BR-A-AV452 | [5 empty] | Sludge | AISI 316 / RTFM | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Sludge | AISI 316 / RTFM | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Butterfly valve |  |  | AV | BV | Tanks
Settler and sludge pump Pneumatic actuator AV452 | C2NC-1500-SLG-AV_452 | C2NC-1500-SLG | Valves | Settler and sludge pump Pneumatic actuator. Function: Deliver instrument air to AV452 | Air Con | Included AV452 | [8 empty] | 9263 | 2D | BR-A-AV452 | [5 empty] | - | Composition of materials | - |  | Pneumatic actuator | [12 empty] | - | Composition of materials | - |  |  |  | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | CF | Tanks
Settler and sludge pump Solenoid valve AV452 | C2NC-1500-SLG-AV_452 | C2NC-1500-SLG | Valves | Settler and sludge pump Solenoid valve. Function: Switch instrument air to BR-A-AV452 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2D | BR-A-AV452 |  | 24 VDC | < 0,5 |  |  | Instrument Air | Composition of materials |  |  | Solenoid valve | [11 empty] | 24 VDC | Instrument Air | Composition of materials |  |  |  |  | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | DAV | Equipment
Dilution water Ball valve AV610 | C2NC-1500-DIL-AV_610 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Open close dilution water to settler | Flotite | 1" 320-SS-2-FFF-025-CDA52-PERP Fail Close | [8 empty] | 9263 | 2E | BR-A-AV610 | [5 empty] | Water | AISI 316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Water | AISI 316 / PTFE | 1" |  |  |  | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | AV | F | Equipment
Circulation pumps Pump P310 | C2NC-1500-CIRC-P_310 | C2NC-1500-CIRC | Equipment | Circulation pumps Pump. Function: Circulation Pump | Verder | MCP3 centrifugal pump | [8 empty] | 9263 | 2B | BR-A-P310 | [5 empty] | Process water | composition | 6" inlet / 5" outlet |  | Pump
Circulation pumps Motor P310_M | C2NC-1500-CIRC-P_310_M | C2NC-1500-CIRC | Equipment | Circulation pumps Motor. Function: Drive P310 | Verder | MCP3 centrifugal pump | [8 empty] | 9263 | 2B | BR-A-P310_M |  | 48 VAC | 31,1 |  | 29,5 | - | composition | - |  | Motor
Dilution water Pneumatic actuator AV610 | C2NC-1500-DIL-AV_610 | C2NC-1500-DIL | Valves | Dilution water Pneumatic actuator. Function: Deliver instrument air to AV610 | Air Con | Included AV610 | [8 empty] | 9263 | 2E | BR-A-AV610 | [5 empty] | - | Composition of materials | - |  | Pneumatic actuator | [12 empty] | - | Composition of materials | - |  |  |  | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | SM | Equipment
Dilution water Solenoid valve AV610 | C2NC-1500-DIL-AV_610 | C2NC-1500-DIL | Valves | Dilution water Solenoid valve. Function: Switch instrument air to BR-A-AV610 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2E | BR-A-AV610 |  | 24 VDC | < 0,5 |  |  | Instrument Air | Composition of materials |  |  | Solenoid valve | [11 empty] | 24 VDC | Instrument Air | Composition of materials |  |  |  |  | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | ST | Equipment
Dilution water Ball valve AV620 | C2NC-1500-DIL-AV_620 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Open close dilution water to sulphur discharge | Flotite | 1" 320-SS-2-FFF-025-CDA52-PERP Fail Close | [8 empty] | 9263 | 2E | BR-A-AV620 | [5 empty] | Water | AISI 316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Water | AISI 316 / PTFE | 1" |  |  |  | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | AV | OF | Equipment
Dilution water Pneumatic actuator AV620 | C2NC-1500-DIL-AV_620 | C2NC-1500-DIL | Valves | Dilution water Pneumatic actuator. Function: Deliver instrument air to AV620 | Air Con | Included AV620 | [8 empty] | 9263 | 2E | BR-A-AV620 | [5 empty] | - | Composition of materials | - |  | Pneumatic actuator | [12 empty] | - | Composition of materials | - |  |  |  | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | SN | Equipment
Dilution water Solenoid valve AV620 | C2NC-1500-DIL-AV_620 | C2NC-1500-DIL | Valves | Dilution water Solenoid valve. Function: Switch instrument air to BR-A-AV620 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2E | BR-A-AV620 |  | 24 VDC | < 0,5 |  |  | Instrument Air | Composition of materials |  |  | Solenoid valve | [11 empty] | 24 VDC | Instrument Air | Composition of materials |  |  |  |  | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | FA | Equipment
Circulation pumps Check valve CV301 | C2NC-1500-CIRC-CV_301 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow over stand-by pump | Titan | CV12-SS | [8 empty] | 9263 | 2B | BR-A-CV301 | [5 empty] | Process water | AISI316 / PTFE | 16" 150# |  | Check valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 16" 150# |  |  |  | Check valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Check valve |  |  | CV | BFP | Lines
Circulation pumps Check valve CV311 | C2NC-1500-CIRC-CV_311 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow over stand-by pump | Titan | CV12-SS | [8 empty] | 9263 | 2B | BR-A-CV311 | [5 empty] | Process water | AISI316 / PTFE | 16" 150# |  | Check valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 16" 150# |  |  |  | Check valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Check valve |  |  | CV | LFP | Lines
Measurement loop and GQA Check valve CV360 | C2NC-1500-MEAS-CV_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Check valve. Function: Prevent backflow of water | Swagelok | CH Series | [8 empty] | 9263 | 2G | BR-A-CV360 | [5 empty] | Process water | AISI 316 / PTFE | 1" |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | Process water | AISI 316 / PTFE | 1" |  |  |  | Check valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Check valve |  |  | CV | SFP | Lines
Settler and sludge pump Diaphragm valve CV450 | C2NC-1500-SLG-CV_450 | C2NC-1500-SLG | Valves | Settler and sludge pump Diaphragm valve. Function: Adjust circulation flow to settler | Saunders | 3/4 Saunders 020-3306-A-11T-DE 150# 316SS Weir Body Diaphragm Valve with PTFE Diaphragm | [8 empty] | 9263 | 2D | BR-A-CV450 | [5 empty] | Process water | AISI316 | 3/4" ANSI 150# |  | Diaphragm valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Process water | AISI316 | 3/4" ANSI 150# |  |  |  | Diaphragm valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Diaphragm valve |  |  | CV | SP | Equipment
Bioreactor and aeration Check valve CV510 | C2NC-1500-BR-CV_510 | C2NC-1500-BR | Valves | Bioreactor and aeration Check valve. Function: Prevent backflow | Titan | CV12-SS | [8 empty] | 9263 | 2C | BR-A-CV510 | [5 empty] | Air | AISI316 / PTFE | 3" 150# |  | Check valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | AISI316 / PTFE | 3" 150# |  |  |  | Check valve |  |  |  |  | Air | [9 empty] | Air |  |  | Check valve |  |  | CV | PM | Equipment
Bioreactor and aeration Check valve CV520 | C2NC-1500-BR-CV_520 | C2NC-1500-BR | Valves | Bioreactor and aeration Check valve. Function: Prevent backflow | Titan | CV12-SS | [8 empty] | 9263 | 2C | BR-A-CV520 | [5 empty] | Air | AISI316 / PTFE | 3" 150# |  | Check valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | AISI316 / PTFE | 3" 150# |  |  |  | Check valve |  |  |  |  | Air | [9 empty] | Air |  |  | Check valve |  |  | CV | PG | Equipment
Circulation pumps Check valve CV601 | C2NC-1500-CIRC-CV_601 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow | Swagelok | C Series | [8 empty] | 9263 | 2B | BR-A-CV601 | [5 empty] | Water | AISI 316L / FKM | 1/2" SWAGELOK |  | Check valve | [7 empty] | 3000 PSIG @ 100°F |  |  |  |  | Water | AISI 316L / FKM | 1/2" SWAGELOK |  |  |  | Check valve |  |  |  |  | Water | [9 empty] | Water |  |  | Check valve |  |  | CV | DM | Equipment
Circulation pumps Check valve CV611 | C2NC-1500-CIRC-CV_611 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow | Swagelok | C Series | [8 empty] | 9263 | 2B | BR-A-CV611 | [5 empty] | Water | AISI 316L / FKM | 1/2" SWAGELOK |  | Check valve | [7 empty] | 3000 PSIG @ 100°F |  |  |  |  | Water | AISI 316L / FKM | 1/2" SWAGELOK |  |  |  | Check valve |  |  |  |  | Water | [9 empty] | Water |  |  | Check valve |  |  | CV | SFP | Equipment
Circulation pumps Check valve CV630 | C2NC-1500-CIRC-CV_630 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow | Titan | CV12-SS | [8 empty] | 9263 | 2B | BR-A-CV630 | [5 empty] | Water | AISI316 / PTFE | 2" 150# |  | Check valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Water | AISI316 / PTFE | 2" 150# |  |  |  | Check valve |  |  |  |  | Water | [9 empty] | Water |  |  | Check valve |  |  | CV | WS | Equipment
Dilution water Check valve CV650 | C2NC-1500-DIL-CV_650 | C2NC-1500-DIL | Valves | Dilution water Check valve. Function: Prevent backlfow | Swagelok | C Series | [8 empty] | 9263 | 2E | BR-A-CV650 | [5 empty] | Water | AISI 316L / FKM | 1/2" SWAGELOK |  | Check valve | [7 empty] | 3000 PSIG @ 100°F |  |  |  |  | Water | AISI 316L / FKM | 1/2" SWAGELOK |  |  |  | Check valve |  |  |  |  | Water | [9 empty] | Water |  |  | Check valve |  |  | CV | SNP | Lines
Measurement loop and GQA Flow-through armature DC360 | C2NC-1500-MEAS-DC_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Flow-through armature. Function: Armature for pH and redox sensors | Endress & Hauser | Flowfit-W | [8 empty] | 9263 | 2G | BR-A-DC360 | [5 empty] | Process water | PP / PAL SS316 | G1" |  | Flow-through armature | [12 empty] | Process water | PP / PAL SS316 | G1" |  |  |  | Flow-through armature |  |  |  |  | Process water | [9 empty] | Process water |  |  | Flow-through armature |  |  | DC
Measurement loop and GQA Flow-through armature DC362 | C2NC-1500-MEAS-DC_362 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Flow-through armature. Function: Armature for conductivity sensor | Endress & Hauser | flow through armature conductivity CTSP | [8 empty] | 9263 | 2G | BR-A-DC362 | [5 empty] | Process water | PVC | G3/4" |  | Flow-through armature | [12 empty] | Process water | PVC | G3/4" |  |  |  | Flow-through armature |  |  |  |  | Process water | [9 empty] | Process water |  |  | Flow-through armature |  |  | DC
Measurement loop and GQA Diaphragm valve DV360 | C2NC-1500-MEAS-DV_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Diaphragm valve. Function: Adjust flow to analysis | Saunders | 3/4" Saunders 020-3306-A-11T-DE 150# 316ss | [8 empty] | 9263 | 2G | BR-A-DV360 | [5 empty] | Process water | AISI316 | 3/4" ANSI 150# |  | Diaphragm valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Process water | AISI316 | 3/4" ANSI 150# |  |  |  | Diaphragm valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Diaphragm valve |  |  | DV | SF | Equipment
Dilution water Diaphragm valve DV610 | C2NC-1500-DIL-DV_610 | C2NC-1500-DIL | Valves | Dilution water Diaphragm valve. Function: Adjust flow water to settler | Saunders | 1 Saunders 025-3306-A-11T-PE 150# 316SS Weir Body Diaphragm Valve with PTFE Diaphragm | [8 empty] | 9263 | 2E | BR-A-DV610 | [5 empty] | Water | AISI316 | 1" ANSI 150# |  | Diaphragm valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Water | AISI316 | 1" ANSI 150# |  |  |  | Diaphragm valve |  |  |  |  | Water | [9 empty] | Water |  |  | Diaphragm valve |  |  | DV | LD | Equipment
Dilution water Diaphragm valve DV620 | C2NC-1500-DIL-DV_620 | C2NC-1500-DIL | Valves | Dilution water Diaphragm valve. Function: Adjust flow dilution water to sulphur discharge | Saunders | 1 Saunders 025-3306-A-11T-PE 150# 316SS Weir Body Diaphragm Valve with PTFE Diaphragm | [8 empty] | 9263 | 2E | BR-A-DV620 | [5 empty] | Water | AISI316 | 1" ANSI 150# |  | Diaphragm valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Water | AISI316 | 1" ANSI 150# |  |  |  | Diaphragm valve |  |  |  |  | Water | [9 empty] | Water |  |  | Diaphragm valve |  |  | DV | CH | Equipment
Dilution water Diaphragm valve DV640 | C2NC-1500-DIL-DV_640 | C2NC-1500-DIL | Valves | Dilution water Diaphragm valve. Function: Adjust dilution water to measurement loop | Saunders | 1/2 Saunders 015-3306-A-11T-PE 150# 316SS Weir Body Diaphragm Valve with PTFE Diaphragm | [8 empty] | 9263 | 2E | BR-A-DV640 | [5 empty] | Water | AISI316 | 1/2" ANSI 150# |  | Diaphragm valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Water | AISI316 | 1/2" ANSI 150# |  |  |  | Diaphragm valve |  |  |  |  | Water | [9 empty] | Water |  |  | Diaphragm valve |  |  | DV | GQA | Instruments
Non hazardous proces room Emergency stop indoor ES900 | C2NC-1500-NHPR-ES_900 | C2NC-1500-NHPR | Instruments | Non hazardous proces room Emergency stop indoor. Function: Stop installation | Schneider | 9001SK | [8 empty] | 9263 | 2H | BR-A-ES900 |  | 24 VDC |  |  |  |  | - | - |  | Emergency stop indoor | [11 empty] | 24 VDC |  | - | - |  |  |  | Emergency stop indoor | [13 empty] | 24 VDC |  |  |  | Emergency stop indoor |  |  | ES
Non hazardous proces room Emergency stop outdoor ES901 | C2NC-1500-NHPR-ES_901 | C2NC-1500-NHPR | Instruments | Non hazardous proces room Emergency stop outdoor. Function: Stop installation | Schneider | 9001SK | [8 empty] | 9263 | 2H | BR-A-ES901 |  | 24 VDC |  |  |  |  | - | - |  | Emergency stop outdoor | [11 empty] | 24 VDC |  | - | - |  |  |  | Emergency stop outdoor | [13 empty] | 24 VDC |  |  |  | Emergency stop outdoor |  |  | ES
Dilution water Filter F600 | C2NC-1500-DIL-F_600 | C2NC-1500-DIL | Equipment | Dilution water Filter. Function: Filtering water | Titan | YS61-SS | [8 empty] | 9263 | 2E | BR-A-F600 | [5 empty] | Water | AISI 316 | 2" |  | Filter
Non hazardous proces room Fan FA910 | C2NC-1500-NHPR-FA_910 | C2NC-1500-NHPR | Equipment | Non hazardous proces room Fan. Function: refreshment process room | J&D Manufacturing | VES201C | [8 empty] | 9263 | 2H | BR-A-FA910 |  | 12 VAC |  |  |  | Ambient air | Composition of materials | 20" |  | Fan
Dilution water Flow indicator FI650 | C2NC-1500-DIL-FI_650 | C2NC-1500-DIL | Instruments | Dilution water Flow indicator. Function: indicate water flow | Kytola instruments | Flowmeter A Range 8M (0,1-1,1 L/min) | [8 empty] | 9263 | 2E | BR-A-FI650 | [5 empty] | Water | PMMA | 3/8" BSP |  | Flow indicator | [7 empty] | 20 barg |  |  |  |  | Water | PMMA | 3/8" BSP |  |  |  | Flow indicator |  |  |  |  | Water | [9 empty] | Water |  |  | Flow indicator |  |  | FI
Dilution water Flow indicator recorder (Totalizer) FIR650 | C2NC-1500-DIL-FIR_650 | C2NC-1500-DIL | Instruments | Dilution water Flow indicator recorder (Totalizer). Function: record water flow | MCM | MCM 4041K61 | [8 empty] | 9263 | 2E | BR-A-FIR650 | [5 empty] | Water | Composition of materials | 1/2" |  | Flow indicator recorder (Totalizer) | [12 empty] | Water | Composition of materials | 1/2" |  |  |  | Flow indicator recorder (Totalizer) |  |  |  |  | Water | [9 empty] | Water |  |  | Flow indicator recorder (Totalizer) |  |  | FIR
Circulation pumps Ball valve V310 | C2NC-1500-CIRC-V_310 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block deaeration valve | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2B | BR-A-V310 | [5 empty] | Cooling water (50% propylene glycol) | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Cooling water (50% propylene glycol) | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Ball valve |  |  | V
Circulation pumps Deaeration valve DAV310 | C2NC-1500-CIRC-DAV_310 | C2NC-1500-CIRC | Equipment | Circulation pumps Deaeration valve. Function: Deaerate system | Flamco | FLEXVENT PRO NPT | [8 empty] | 9263 | 2B | BR-A-DAV310 | [5 empty] | Cooling water (50% propylene glycol) | Brass | 1/2" FNPT |  | Deaeration valve
Caustic scrubber Flow switch FIS200 | C2NC-1500-CS-FIS_200 | C2NC-1500-CS | Instruments | Caustic scrubber Flow switch. Function: validate flowrate | Ameritrol | FX – 0750 – XD | [8 empty] | 9263 | 2A | BR-A-FIS200 |  | 24 DC | 0.15 |  |  | Process water | AISI 316L | 3/4" MNPT |  | Flow switch | [7 empty] | Vacuum to 4000 PSIG (275 Bar) |  |  |  | 24 DC | Process water | AISI 316L | 3/4" MNPT |  |  |  | Flow switch |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow switch |  | Digital | FIS
Circulation pumps Flow indicator SWITCH FIS300 | C2NC-1500-CIRC-FIS_300 | C2NC-1500-CIRC | Instruments | Circulation pumps Flow indicator SWITCH. Function: Flow indication | IFM | SI5000 | [8 empty] | 9263 | 2B | BR-A-FIS300 |  | 24 DC | 0,25 / 0,06 |  |  | Process water | AISI 316L / FKM | M18 x 1,5 |  | Flow indicator SWITCH | [7 empty] | 435 PSIG (30 BARG) |  |  |  | 24 DC | Process water | AISI 316L / FKM | M18 x 1,5 |  |  |  | Flow indicator SWITCH |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow indicator SWITCH |  | Digital | FIS
Circulation pumps Flow indicator SWITCH FIS320 | C2NC-1500-CIRC-FIS_320 | C2NC-1500-CIRC | Instruments | Circulation pumps Flow indicator SWITCH. Function: Flow indication | IFM | SI5000 | [8 empty] | 9263 | 2B | BR-A-FIS320 |  | 24 DC | 0,25 / 0,06 |  |  | Process water | AISI 316L / FKM | M18 x 1,5 |  | Flow indicator SWITCH | [7 empty] | 435 PSIG (30 BARG) |  |  |  | 24 DC | Process water | AISI 316L / FKM | M18 x 1,5 |  |  |  | Flow indicator SWITCH |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow indicator SWITCH |  | Digital | FIS
Circulation pumps Butterfly valve V331 | C2NC-1500-CIRC-V_331 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Switch between heating / cooling | Emerson | Keystone Figure 322 trim 112 Resilient seated butterfly valve | [8 empty] | 9263 | 2B | BR-A-V331 | [5 empty] | Cooling water (50% propylene glycol) | AISI 316 / EPDM | 4" Multi drill PN 6/10/16, ASME 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Cooling water (50% propylene glycol) | AISI 316 / EPDM | 4" Multi drill PN 6/10/16, ASME 150# |  |  |  | Butterfly valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Butterfly valve |  |  | V
Circulation pumps Butterfly valve V332 | C2NC-1500-CIRC-V_332 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Switch between heating / cooling | Emerson | Keystone Figure 322 trim 112 Resilient seated butterfly valve | [8 empty] | 9263 | 2B | BR-A-V332 | [5 empty] | Cooling water (50% propylene glycol) | AISI 316 / EPDM | 4" Multi drill PN 6/10/16, ASME 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Cooling water (50% propylene glycol) | AISI 316 / EPDM | 4" Multi drill PN 6/10/16, ASME 150# |  |  |  | Butterfly valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Biologial reactor R400 | C2NC-1500-BR-R_400 | C2NC-1500-BR | Equipment | Bioreactor and aeration Biologial reactor. Function: Caustic recovery and formation of sulphur | Midwestern Fabricators | BR350 | [8 empty] | 9263 | 2C | BR-A-R400 | [5 empty] | Process water | FRP | 3048 x 6000 mm (10ft x 19ft 14") |  | Biologial reactor
Bioreactor and aeration Air diffuser SN501_524 | C2NC-1500-BR-SN_501_524 | C2NC-1500-BR | Equipment | Bioreactor and aeration Air diffuser. Function: Air distribution | Mooers | 3/4"NPT Mooers Flexcap Diffuser | [8 empty] | 9263 | 2C | BR-A-SN501-524 | [5 empty] | Ambient air / Process water | PP/EPDM | 3/4" NPT |  | Air diffuser
Bioreactor and aeration Spray nozzle pipe SNP400 | C2NC-1500-BR-SNP_400 | C2NC-1500-BR | Lines | Bioreactor and aeration Spray nozzle pipe. Function: mounting of spray nozzle | DMT | according 9263-8022 | [8 empty] | 9263 | 2C | BR-A-SNP400 | [12 empty] | AISI 316 | 1" NPT / 2"
Bioreactor and aeration Spraying Nozzle SN401 | C2NC-1500-BR-SN_401 | C2NC-1500-BR | Equipment | Bioreactor and aeration Spraying Nozzle. Function: Foam removal | Bete | TFXP Full cone spiral spray nozzle TF48 | [8 empty] | 9263 | 2C | BR-A-SN401 | [5 empty] | Process water | AISI 316 | 1" NPT |  | Spraying Nozzle
Circulation pumps Flow indicator SWITCH FIS330 | C2NC-1500-CIRC-FIS_330 | C2NC-1500-CIRC | Instruments | Circulation pumps Flow indicator SWITCH. Function: validate flowrate | IFM | SI5000 | [8 empty] | 9263 | 2B | BR-A-FIS330 |  | 24 DC | 0,25 / 0,06 |  |  | Process water | AISI 316L / FKM | M18 x 1,5 |  | Flow indicator SWITCH | [7 empty] | 435 PSIG (30 BARG) |  |  |  | 24 DC | Process water | AISI 316L / FKM | M18 x 1,5 |  |  |  | Flow indicator SWITCH |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow indicator SWITCH |  | Digital | FIS
Measurement loop and GQA Flow indicator SWITCH FIS360 | C2NC-1500-MEAS-FIS_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Flow indicator SWITCH. Function: Flow indication measurement loop | IFM | SI5000 | [8 empty] | 9263 | 2G | BR-A-FIS360 |  | 24 DC | 0,25 / 0,06 |  |  | Process water | AISI 316L / FKM | M18 x 1,5 |  | Flow indicator SWITCH | [7 empty] | 435 PSIG (30 BARG) |  |  |  | 24 DC | Process water | AISI 316L / FKM | M18 x 1,5 |  |  |  | Flow indicator SWITCH |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow indicator SWITCH |  | Digital | FIS
Dosing skids Flow indicator SWITCH FIS700 | C2NC-1500-CHEM-FIS_700 | C2NC-1500-CHEM | Instruments | Dosing skids Flow indicator SWITCH. Function: validate flowrate | IFM | SI5000 | [8 empty] | 9263 | 2F | BR-A-FIS700 |  | 24 DC | 0,25 / 0,06 |  |  | Process water | AISI 316L / FKM | M18 x 1,5 |  | Flow indicator SWITCH | [7 empty] | 435 PSIG (30 BARG) |  |  |  | 24 DC | Process water | AISI 316L / FKM | M18 x 1,5 |  |  |  | Flow indicator SWITCH |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow indicator SWITCH |  | Digital | FIS
Circulation pumps Flow indicator transmitter FIT340 | C2NC-1500-CIRC-FIT_340 | C2NC-1500-CIRC | Instruments | Circulation pumps Flow indicator transmitter. Function: Flow indication circulation flow to scrubber | Endress & Hauser | Promag W 400, 5W4C2F, DN250 10" | [8 empty] | 9263 | 2B | BR-A-FIT340 |  | 12 VAC | 0.15 |  |  | Process water | CS / ALU / ALLOY / PTFE | 10" 150# |  | Flow indicator transmitter | [7 empty] | 73-101 psi |  |  |  | 12 VAC | Process water | CS / ALU / ALLOY / PTFE | 10" 150# |  |  |  | Flow indicator transmitter |  |  |  |  | Process water | [8 empty] | 12 VAC | Process water |  |  | Flow indicator transmitter |  | Analog | FIT
Bioreactor and aeration Flow indicator transmitter FIT510 | C2NC-1500-BR-FIT_510 | C2NC-1500-BR | Instruments | Bioreactor and aeration Flow indicator transmitter. Function: Flow indication air injection | Endress & Hauser | T-mass B 150, 6BABL1, 235mm 9" | [8 empty] | 9263 | 2C | BR-A-FIT510 |  | 24 VDC | 0.35 |  |  | Air | SS316 / PEEK | 3/4" NPT |  | Flow indicator transmitter | [7 empty] | -7,25 - 290 psig |  |  |  | 24 VDC | Air | SS316 / PEEK | 3/4" NPT |  |  |  | Flow indicator transmitter |  |  |  |  | Air | [8 empty] | 24 VDC | Air |  |  | Flow indicator transmitter |  | Analog | FIT
Dilution water Flow indicator transmitter FIT610 | C2NC-1500-DIL-FIT_610 | C2NC-1500-DIL | Instruments | Dilution water Flow indicator transmitter. Function: Water consumption totalizer | Endress & Hauser | Promag W 400, 5W4C25, DN25 1" | [8 empty] | 9263 | 2E | BR-A-FIT610 |  | 12 VAC | 0.15 |  |  | Water | Composition of materials | 1" |  | Flow indicator transmitter | [7 empty] | 73-101 psi |  |  |  | 12 VAC | Water | Composition of materials | 1" |  |  |  | Flow indicator transmitter |  |  |  |  | Water | [8 empty] | 12 VAC | Water |  |  | Flow indicator transmitter |  | Analog | FIT
Non hazardous proces room Grid GR910 | C2NC-1500-NHPR-GR_910 | C2NC-1500-NHPR | Equipment | Non hazardous proces room Grid. Function: Inlet air | Grainger | [9 empty] | 9263 | 2H | BR-A-GR910 | [5 empty] | Ambient air | Aluminium | 400x400mm |  | Grid
Non hazardous proces room Grid GR911 | C2NC-1500-NHPR-GR_911 | C2NC-1500-NHPR | Equipment | Non hazardous proces room Grid. Function: Inlet air | Grainger | [9 empty] | 9263 | 2H | BR-A-GR911 | [5 empty] | Ambient air | Aluminium | 500x500mm |  | Grid
Non hazardous proces room Grid GR912 | C2NC-1500-NHPR-GR_912 | C2NC-1500-NHPR | Equipment | Non hazardous proces room Grid. Function: Inlet air | Grainger | [9 empty] | 9263 | 2H | BR-A-GR912 | [5 empty] | Ambient air | Aluminium | 500x500mm |  | Grid
Circulation pumps Pipe cooler HE310 | C2NC-1500-CIRC-HE_310 | C2NC-1500-CIRC | Equipment | Circulation pumps Pipe cooler. Function: Heat transfer from hot water to proces medium | DMT | According drawing DMT | [8 empty] | 9263 | 2B | BR-A-HE310 | [5 empty] | Process water | AISI304 / NBR | 12" 150# |  | Pipe cooler
Non hazardous proces room Heater HE900 | C2NC-1500-NHPR-HE_900 | C2NC-1500-NHPR | Equipment | Non hazardous proces room Heater. Function: Heating | McMaster-Carr | Ceiling-&Wall-Mount Large-Space Electric Heater | [8 empty] | 9263 | 2H | BR-A-HE900 |  | 48 VAC |  | 5 |  | Ambient air | Steel |  |  | Heater
Caustic scrubber Level switch LS200 | C2NC-1500-CS-LS_200 | C2NC-1500-CS | Instruments | Caustic scrubber Level switch. Function: Protection of pumps from dry running | Endress & Hauser | Liquiphant M FTL51 | [8 empty] | 9263 | 2A | BR-A-LS200 |  | 24 VDC | 0.085 |  |  | Process water | AISI 316 | 2" 150# RF |  | Level switch | [11 empty] | 24 VDC | Process water | AISI 316 | 2" 150# RF |  |  |  | Level switch |  |  |  |  | Process water | [8 empty] | 24 VDC | Process water |  |  | Level switch |  | Analog | LS
Bioreactor and aeration Filter F510 | C2NC-1500-BR-F_510 | C2NC-1500-BR | Equipment | Bioreactor and aeration Filter. Function: Filter ingoing air | Aertzen | [9 empty] | 9263 | 2C | BR-A-F510 | [5 empty] | Air | AISI 316 / paper | G5" |  | Filter
Bioreactor and aeration Feed blower FB510 | C2NC-1500-BR-FB_510 | C2NC-1500-BR | Equipment | Bioreactor and aeration Feed blower. Function: Increase pressure of air for bioreactor aeration | Aertzen | AERZEN draaizuigerblower GM 10 S | [8 empty] | 9263 | 2C | BR-A-FB510 | [5 empty] | Air | Composition | 3" |  | Feed blower
Bioreactor and aeration Motor FB510_M | C2NC-1500-BR-FB_510_M | C2NC-1500-BR | Equipment | Bioreactor and aeration Motor. Function: Drive FB510 | Aertzen | [9 empty] | 9263 | 2C | BR-A-FB510_M |  | 48 VAC | 15,6 |  | 14,8 | - | Composition |  |  | Motor
Bioreactor and aeration Pressure safety valve PZV510 | C2NC-1500-BR-PZV_510 | C2NC-1500-BR | Valves | Bioreactor and aeration Pressure safety valve. Function: protection of overpressure | Aertzen | [9 empty] | 9263 | 2C | BR-A-PZV510 | [5 empty] | Air |  |  |  | Pressure safety valve | [12 empty] | Air | [5 empty] | Pressure safety valve |  |  |  |  | Air | [9 empty] | Air |  |  | Pressure safety valve |  |  | PZV
Bioreactor and aeration Compensator BL510 | C2NC-1500-BR-BL_510 | C2NC-1500-BR | Equipment | Bioreactor and aeration Compensator. Function: Absorb shrinking and expanding of piping | Aertzen | [9 empty] | 9263 | 2C | BR-A-BL510 | [5 empty] | Air | AISI 316 | 3" |  | Compensator
Bioreactor and aeration Level switch LS400 | C2NC-1500-BR-LS_400 | C2NC-1500-BR | Instruments | Bioreactor and aeration Level switch. Function: Protection of pumps from dry running | Endress & Hauser | Liquiphant M FTL51 | [8 empty] | 9263 | 2C | BR-A-LS400 |  | 24 VDC | 0.085 |  |  | Process water | AISI 316 | 2" 150# RF |  | Level switch | [11 empty] | 24 VDC | Process water | AISI 316 | 2" 150# RF |  |  |  | Level switch |  |  |  |  | Process water | [8 empty] | 24 VDC | Process water |  |  | Level switch |  | Analog | LS
Settler and sludge pump Level switch LS451 | C2NC-1500-SLG-LS_451 | C2NC-1500-SLG | Instruments | Settler and sludge pump Level switch. Function: Protection of pumps from dry running | Endress & Hauser | Liquiphant M FTL51 | [8 empty] | 9263 | 2D | BR-A-LS451 |  | 24 VDC | 0.085 |  |  | Process water | AISI 316 | 2" 150# RF |  | Level switch | [11 empty] | 24 VDC | Process water | AISI 316 | 2" 150# RF |  |  |  | Level switch |  |  |  |  | Process water | [8 empty] | 24 VDC | Process water |  |  | Level switch |  | Analog | LS
Circulation pumps Needle valve NV603 | C2NC-1500-CIRC-NV_603 | C2NC-1500-CIRC | Valves | Circulation pumps Needle valve. Function: block water line | Swagelok | Stainless Steel Integral Bonnet Needle Valve, 0.73 Cv, 1/2 in. Swagelok Tube Fitting, Regulating Stem | [8 empty] | 9263 | 2B | BR-A-NV603 | [5 empty] | Water | AISI 316 | 1/2" |  | Needle valve | [7 empty] | 3435 PSIG |  |  |  |  | Water | AISI 316 | 1/2" |  |  |  | Needle valve |  |  |  |  | Water | [9 empty] | Water |  |  | Needle valve |  |  | NV
Circulation pumps Needle valve NV613 | C2NC-1500-CIRC-NV_613 | C2NC-1500-CIRC | Valves | Circulation pumps Needle valve. Function: block water line | Swagelok | Stainless Steel Integral Bonnet Needle Valve, 0.73 Cv, 1/2 in. Swagelok Tube Fitting, Regulating Stem | [8 empty] | 9263 | 2B | BR-A-NV613 | [5 empty] | Water | AISI 316 | 1/2" |  | Needle valve | [7 empty] | 3435 PSIG |  |  |  |  | Water | AISI 316 | 1/2" |  |  |  | Needle valve |  |  |  |  | Water | [9 empty] | Water |  |  | Needle valve |  |  | NV
Dilution water Needle valve NV650 | C2NC-1500-DIL-NV_650 | C2NC-1500-DIL | Valves | Dilution water Needle valve. Function: Control water flow | Swagelok | Stainless Steel Integral Bonnet Needle Valve, 0.73 Cv, 1/2 in. Swagelok Tube Fitting, Regulating Stem | [8 empty] | 9263 | 2E | BR-A-NV650 | [5 empty] | Water | AISI 316 | 1/2" |  | Needle valve | [7 empty] | 3435 PSIG |  |  |  |  | Water | AISI 316 | 1/2" |  |  |  | Needle valve |  |  |  |  | Water | [9 empty] | Water |  |  | Needle valve |  |  | NV
Bioreactor and aeration Filter F520 | C2NC-1500-BR-F_520 | C2NC-1500-BR | Equipment | Bioreactor and aeration Filter. Function: Filter ingoing air | Aertzen | [9 empty] | 9263 | 2C | BR-A-F520 | [5 empty] | Air | AISI 316 / paper | G5" |  | Filter
Bioreactor and aeration Feed blower FB520 | C2NC-1500-BR-FB_520 | C2NC-1500-BR | Equipment | Bioreactor and aeration Feed blower. Function: Increase pressure of air for bioreactor aeration | Aertzen | AERZEN draaizuigerblower GM 10 S | [8 empty] | 9263 | 2C | BR-A-FB520 | [5 empty] | Air | Composition | 3" |  | Feed blower
Bioreactor and aeration Motor FB520_M | C2NC-1500-BR-FB_520_M | C2NC-1500-BR | Equipment | Bioreactor and aeration Motor. Function: Drive FB510 | Aertzen | [9 empty] | 9263 | 2C | BR-A-FB520_M |  | 48 VAC | 15,6 |  | 14,8 | - | Composition |  |  | Motor
Bioreactor and aeration Pressure safety valve PZV520 | C2NC-1500-BR-PZV_520 | C2NC-1500-BR | Valves | Bioreactor and aeration Pressure safety valve. Function: protection of overpressure | Aertzen | [9 empty] | 9263 | 2C | BR-A-PZV520 | [5 empty] | Air |  |  |  | Pressure safety valve | [12 empty] | Air | [5 empty] | Pressure safety valve |  |  |  |  | Air | [9 empty] | Air |  |  | Pressure safety valve |  |  | PZV
Bioreactor and aeration Compensator BL520 | C2NC-1500-BR-BL_520 | C2NC-1500-BR | Equipment | Bioreactor and aeration Compensator. Function: Absorb shrinking and expanding of piping | Aertzen | [9 empty] | 9263 | 2C | BR-A-BL520 | [5 empty] | Air | AISI 316 | 3" |  | Compensator
Dilution water Pressure control valve PCV600 | C2NC-1500-DIL-PCV_600 | C2NC-1500-DIL | Valves | Dilution water Pressure control valve . Function: Prevent high pressure water line | Eriks | Rvs reduceer type Eriks fig 1536 | [8 empty] | 9263 | 2E | BR-A-PCV600 | [5 empty] | Water | AISI 316 | 2" 150# |  | Pressure control valve | [12 empty] | Water | AISI 316 | 2" 150# |  |  |  | Pressure control valve |  |  |  |  | Water | [9 empty] | Water |  |  | Pressure control valve |  |  | PCV
Dilution water Pressure control valve PCV650 | C2NC-1500-DIL-PCV_650 | C2NC-1500-DIL | Valves | Dilution water Pressure control valve . Function: Prevent high pressure water line | Eriks | Rvs reduceer type Eriks fig 1535 | [8 empty] | 9263 | 2E | BR-A-PCV650 | [5 empty] | Water | AISI 316 | 1/2" NPT |  | Pressure control valve | [12 empty] | Water | AISI 316 | 1/2" NPT |  |  |  | Pressure control valve |  |  |  |  | Water | [9 empty] | Water |  |  | Pressure control valve |  |  | PCV
Non hazardous proces room Pressure reducing valve PCV900 | C2NC-1500-NHPR-PCV_900 | C2NC-1500-NHPR | Valves | Non hazardous proces room Pressure reducing valve. Function: Adjust air supply pressure | Festo | MS6-LFR | [8 empty] | 9263 | 2H | BR-A-PCV900 | [5 empty] | Instrument Air | composition | 1" |  | Pressure reducing valve | [7 empty] | 0,8 - 20 bar |  |  |  |  | Instrument Air | composition | 1" |  |  |  | Pressure reducing valve |  |  |  |  | Instrument Air | [9 empty] | Instrument Air |  |  | Pressure reducing valve |  |  | PCV
Dilution water Pressure indicator PI600 | C2NC-1500-DIL-PI_600 | C2NC-1500-DIL | Instruments | Dilution water Pressure indicator. Function: Local pressure indication | Ashcroft | Process gauge T5500/T6500 Dual Scale 100mm Low | [8 empty] | 9263 | 2E | BR-A-PI600 | [5 empty] | Water | AISI 316L | 1/2" NPT (male) |  | Pressure indicator | [7 empty] | 0 - 6 bar |  |  |  |  | Water | AISI 316L | 1/2" NPT (male) |  |  |  | Pressure indicator |  |  |  |  | Water | [9 empty] | Water |  |  | Pressure indicator |  |  | PI
Settler and sludge pump Settler S450 | C2NC-1500-SLG-S_450 | C2NC-1500-SLG | Equipment | Settler and sludge pump Settler. Function: Removal of large particles | Midwestern Fabricators | According drawing DMT | [8 empty] | 9263 | 2D | BR-A-S450 | [5 empty] | Process water | FRP | diameter: 39" height:19'-9" |  | Settler
Dilution water Pressure indicator PI650 | C2NC-1500-DIL-PI_650 | C2NC-1500-DIL | Instruments | Dilution water Pressure indicator. Function: Local pressure indication | Ashcroft | Process gauge T5500/T6500 Dual Scale 100mm Low | [8 empty] | 9263 | 2E | BR-A-PI650 | [5 empty] | Water |  | 1/2" NPT |  | Pressure indicator | [7 empty] | 0 - 6 bar |  |  |  |  | Water |  | 1/2" NPT |  |  |  | Pressure indicator |  |  |  |  | Water | [9 empty] | Water |  |  | Pressure indicator |  |  | PI
Bioreactor and aeration Pressure transmitter PIT400 | C2NC-1500-BR-PIT_400 | C2NC-1500-BR | Instruments | Bioreactor and aeration Pressure transmitter. Function: Pressure indication bioreactor for level control | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263 | 2C | BR-A-PIT400 |  | 24 VDC | 0.026 |  |  | Process water | SS316 | 2" 150# |  | Pressure transmitter | [7 empty] | 15 psi(g) sensor |  |  |  | 24 VDC | Process water | SS316 | 2" 150# |  |  |  | Pressure transmitter |  |  |  |  | Process water | [8 empty] | 24 VDC | Process water |  |  | Pressure transmitter |  | Analog | PIT
Settler and sludge pump Pressure transmitter PIT452 | C2NC-1500-SLG-PIT_452 | C2NC-1500-SLG | Instruments | Settler and sludge pump Pressure transmitter. Function: Pressure indication sludge pump dicharge | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263 | 2D | BR-A-PIT452 |  | 24 VDC | 0.026 |  |  | Sludge | SS316 | 1/2" NPT |  | Pressure transmitter | [7 empty] | 150 psi(g) sensor |  |  |  | 24 VDC | Sludge | SS316 | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | Sludge | [8 empty] | 24 VDC | Sludge |  |  | Pressure transmitter |  | Analog | PIT
Caustic scrubber Pressure transmitter PT100 | C2NC-1500-CS-PT_100 | C2NC-1500-CS | Instruments | Caustic scrubber Pressure transmitter. Function: Measure inlet pressure | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263 | 2A | BR-A-PT100 |  | 24 VDC | 0.026 |  |  | Raw biogas | AISI 316L | 1/2" NPT (male) |  | Pressure transmitter | [7 empty] | 15 psi(g) sensor |  |  |  | 24 VDC | Raw biogas | AISI 316L | 1/2" NPT (male) |  |  |  | Pressure transmitter |  |  |  |  | Raw biogas | [8 empty] | 24 VDC | Raw biogas |  |  | Pressure transmitter |  | Analog | PT
Caustic scrubber Pressure transmitter PT102 | C2NC-1500-CS-PT_102 | C2NC-1500-CS | Instruments | Caustic scrubber Pressure transmitter. Function: Pressure Indication of outlet biogas | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263 | 2A | BR-A-PT102 |  | 24 VDC | 0.026 |  |  | Clean biogas | SS316 | 1/2" NPT |  | Pressure transmitter | [7 empty] | 15 psi(g) sensor |  |  |  | 24 VDC | Clean biogas | SS316 | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | Clean biogas | [8 empty] | 24 VDC | Clean biogas |  |  | Pressure transmitter |  | Analog | PT
Settler and sludge pump Peristaltic discharge pump P450 | C2NC-1500-SLG-P_450 | C2NC-1500-SLG | Equipment | Settler and sludge pump Peristaltic discharge pump . Function: Discharge of sulphur sludge | Verder | Dura 25 | [8 empty] | 9263 | 2D | BR-A-P450 | [5 empty] | Sludge | EPDM hose | 1" ANSI |  | Peristaltic discharge pump
Settler and sludge pump Motor P450_M | C2NC-1500-SLG-P_450_M | C2NC-1500-SLG | Equipment | Settler and sludge pump Motor. Function: Drive P450 | Verder | Dura 25 | [8 empty] | 9263 | 2D | BR-A-P450_M |  | 48 VAC | 2,1 |  |  | - | composition | - |  | Motor
Bioreactor and aeration Pressure transmitter PT501 | C2NC-1500-BR-PT_501 | C2NC-1500-BR | Instruments | Bioreactor and aeration Pressure transmitter. Function: Pressure indication air discharge | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263 | 2C | BR-A-PT501 |  | 24 VDC | 0.026 |  |  | Air | SS316 | 1/2" NPT |  | Pressure transmitter | [7 empty] | 30 psi(g) sensor |  |  |  | 24 VDC | Air | SS316 | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | Air | [8 empty] | 24 VDC | Air |  |  | Pressure transmitter |  | Analog | PT
Dilution water Pressure transmitter PT600 | C2NC-1500-DIL-PT_600 | C2NC-1500-DIL | Instruments | Dilution water Pressure transmitter. Function: Pressure indication supply water | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263 | 2E | BR-A-PT600 |  | 24 VDC | 0.026 |  |  | Water | SS316 | 1/2" NPT |  | Pressure transmitter | [7 empty] | 150 psi(g) sensor |  |  |  | 24 VDC | Water | SS316 | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | Water | [8 empty] | 24 VDC | Water |  |  | Pressure transmitter |  | Analog | PT
Non hazardous proces room Pressure transmitter PT900 | C2NC-1500-NHPR-PT_900 | C2NC-1500-NHPR | Instruments | Non hazardous proces room Pressure transmitter. Function: Pressure indication instrument air | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263 | 2H | BR-A-PT900 |  | 24 VDC | 0.026 |  |  | Instrument Air | SS316 | 1/2" NPT |  | Pressure transmitter | [7 empty] | 150 psi(g) sensor |  |  |  | 24 VDC | Instrument Air | SS316 | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Pressure transmitter |  | Analog | PT
Measurement loop and GQA Quality measurement processing unit QITA360 | C2NC-1500-MEAS-QITA_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement processing unit. Function: Processing unit of quality measurement | Endress & Hauser | Liquiline CM444 | [8 empty] | 9263 | 2G | BR-A-QITA360 |  | 24 VDC | 3 | 0.068 |  | - | composition | - |  | Quality measurement processing unit | [11 empty] | 24 VDC | - | composition | - |  |  |  | Quality measurement processing unit |  |  |  |  | - | [8 empty] | 24 VDC | - |  |  | Quality measurement processing unit |  |  | QITA
Measurement loop and GQA Quality measurement (pH) QT360 | C2NC-1500-MEAS-QT_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (pH). Function: PH indication of process liquid | Endress & Hauser | pH meter: Orbipore CPS91D | [8 empty] | 9263 | 2G | BR-A-QT360 | [5 empty] | - | composition | - |  | Quality measurement (pH) | [7 empty] | 0 - 145 psi |  |  |  |  | - | composition | - |  |  |  | Quality measurement (pH) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (pH) |  | Analog | QT
Measurement loop and GQA Quality measurement (pH) QT360 | C2NC-1500-MEAS-QT_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (pH). Function: cable | Endress & Hauser | pH meter: cable CYK10 | [8 empty] | 9263 | 2G | BR-A-QT360 | [5 empty] | - | composition | - |  | Quality measurement (pH) | [12 empty] | - | composition | - |  |  |  | Quality measurement (pH) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (pH) |  |  | QT
Measurement loop and GQA Quality measurement (pH) QT360 | C2NC-1500-MEAS-QT_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (pH). Function: buffer | Endress & Hauser | pH meter: pH7 buffer CPY20 | [8 empty] | 9263 | 2G | BR-A-QT360 | [5 empty] | - | composition | - |  | Quality measurement (pH) | [12 empty] | - | composition | - |  |  |  | Quality measurement (pH) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (pH) |  |  | QT
Measurement loop and GQA Quality measurement (pH) QT360 | C2NC-1500-MEAS-QT_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (pH). Function: buffer | Endress & Hauser | pH meter: pH10 buffer CPY20 | [8 empty] | 9263 | 2G | BR-A-QT360 | [5 empty] | - | composition | - |  | Quality measurement (pH) | [12 empty] | - | composition | - |  |  |  | Quality measurement (pH) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (pH) |  |  | QT
Measurement loop and GQA Quality measurement (Redox) QT361 | C2NC-1500-MEAS-QT_361 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Redox). Function: Redox indication of process liquid | Rust Automation & Controls - Knick | redox meter: SE 564 memosens ORP sensor | [8 empty] | 9263 | 2G | BR-A-QT361 | [5 empty] | Process water | composition | special |  | Quality measurement (Redox) | [7 empty] | 0 - 145 psi |  |  |  |  | Process water | composition | special |  |  |  | Quality measurement (Redox) |  |  |  |  | Process water | [9 empty] | Process water |  |  | Quality measurement (Redox) |  | Analog | QT
Measurement loop and GQA Quality measurement (Redox) QT361 | C2NC-1500-MEAS-QT_361 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Redox). Function: cable | Endress & Hauser | redox meter: cable CYK10 | [8 empty] | 9263 | 2G | BR-A-QT361 | [5 empty] | - | composition | - |  | Quality measurement (Redox) | [12 empty] | - | composition | - |  |  |  | Quality measurement (Redox) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (Redox) |  |  | QT
Measurement loop and GQA Quality measurement (Redox) QT361 | C2NC-1500-MEAS-QT_361 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Redox). Function: Redox indication of process liquid | Endress & Hauser | redox meter: buffer for calibration CPY3 | [8 empty] | 9263 | 2G | BR-A-QT361 | [5 empty] | - | composition | - |  | Quality measurement (Redox) | [12 empty] | - | composition | - |  |  |  | Quality measurement (Redox) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (Redox) |  |  | QT
Measurement loop and GQA Quality measurement (Conductivity) QT362 | C2NC-1500-MEAS-QT_362 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Conductivity). Function: Conductivity indication process liquid | Endress & Hauser | Conductivity meter: Indumax CLS50D | [8 empty] | 9263 | 2G | BR-A-QT362 | [5 empty] | Process water | composition | 1" NPT |  | Quality measurement (Conductivity) | [7 empty] | 0 - 290 psi |  |  |  |  | Process water | composition | 1" NPT |  |  |  | Quality measurement (Conductivity) |  |  |  |  | Process water | [9 empty] | Process water |  |  | Quality measurement (Conductivity) |  | Analog | QT
Measurement loop and GQA Quality measurement (Conductivity) QT362 | C2NC-1500-MEAS-QT_362 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Conductivity). Function: Conductivity indication process liquid | Endress & Hauser | Calibration solutuin CLY11 | [8 empty] | 9263 | 2G | BR-A-QT362 | [5 empty] | - | composition | - |  | Quality measurement (Conductivity) | [12 empty] | - | composition | - |  |  |  | Quality measurement (Conductivity) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (Conductivity) |  |  | QT
Measurement loop and GQA Quality measurement (Conductivity) QT362 | C2NC-1500-MEAS-QT_362 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Conductivity). Function: Conductivity indication process liquid | Endress & Hauser | Calibration solutuin CLY11 | [8 empty] | 9263 | 2G | BR-A-QT362 | [5 empty] | - | composition | - |  | Quality measurement (Conductivity) | [12 empty] | - | composition | - |  |  |  | Quality measurement (Conductivity) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (Conductivity) |  |  | QT
Non hazardous proces room Sound indicator ( Horn ) SI900 | C2NC-1500-NHPR-SI_900 | C2NC-1500-NHPR | Instruments | Non hazardous proces room Sound indicator ( Horn ). Function: CREATE AUDIO WARNING SIGNAL | E2S Warning signals | D2xS1 AC115 AB1 A1R | [8 empty] | 9263 | 2H | BR-A-SI900 |  | 115 VAC |  |  |  | AMBIENT AIR | Aluminium - Red - RAL3000 | 130x180x125mm (wxhxd) |  | Sound indicator ( Horn ) | [11 empty] | 115 VAC | AMBIENT AIR | Aluminium - Red - RAL3000 | 130x180x125mm (wxhxd) |  |  |  | Sound indicator ( Horn ) |  |  |  |  | AMBIENT AIR | [8 empty] | 115 VAC | AMBIENT AIR |  |  | Sound indicator ( Horn ) |  | Digital | SI
Circulation pumps Temperature indicator TI310 | C2NC-1500-CIRC-TI_310 | C2NC-1500-CIRC | Instruments | Circulation pumps Temperature indicator. Function: indicate temperature | ASHCROFT | EI Bimetal Thermometer D3" | [8 empty] | 9263 | 2B | BR-A-TI310 | [5 empty] | Process water | AISI 316 | 1/2" NPT |  | Temperature indicator | [12 empty] | Process water | AISI 316 | 1/2" NPT |  |  |  | Temperature indicator |  |  |  |  | Process water | [9 empty] | Process water |  |  | Temperature indicator |  |  | TI
Circulation pumps Thermowell TI310 | C2NC-1500-CIRC-TI_310 | C2NC-1500-CIRC | Instruments | Circulation pumps Thermowell. Function: protect temperature indicator | McMaster-Carr | for 2-1/2" x 1/4" Stem, 316 Stainless Steel, 1/2 NPT Connection | [8 empty] | 9263 | 2B | BR-A-TI310 | [5 empty] | Process water | AISI 316 | 1" NPT |  | Thermowell | [7 empty] | 7,000 psi @ 70° F |  |  |  |  | Process water | AISI 316 | 1" NPT |  |  |  | Thermowell |  |  |  |  | Process water | [9 empty] | Process water |  |  | Thermowell |  |  | TI
Caustic scrubber Temperature transmitter TT100 | C2NC-1500-CS-TT_100 | C2NC-1500-CS | Instruments | Caustic scrubber Temperature transmitter. Function: Measure inlet temperature raw biogas | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263 | 2A | BR-A-TT100 |  | 24 VDC | 0.03 |  |  | Raw biogas | SS316 | 1/2" NPTM |  | Temperature transmitter | [11 empty] | 24 VDC | Raw biogas | SS316 | 1/2" NPTM |  |  |  | Temperature transmitter |  |  |  |  | Raw biogas | [8 empty] | 24 VDC | Raw biogas |  |  | Temperature transmitter |  | Analog | TT
Caustic scrubber Temperature transmitter TT102 | C2NC-1500-CS-TT_102 | C2NC-1500-CS | Instruments | Caustic scrubber Temperature transmitter. Function: Temperature indication outlet biogas | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263 | 2A | BR-A-TT102 |  | 24 VDC | 0.03 |  |  | Clean biogas | SS316 | 1/2" NPTM |  | Temperature transmitter | [11 empty] | 24 VDC | Clean biogas | SS316 | 1/2" NPTM |  |  |  | Temperature transmitter |  |  |  |  | Clean biogas | [8 empty] | 24 VDC | Clean biogas |  |  | Temperature transmitter |  | Analog | TT
Circulation pumps Temperature transmitter TT300 | C2NC-1500-CIRC-TT_300 | C2NC-1500-CIRC | Instruments | Circulation pumps Temperature transmitter. Function: Temperature indication bioreactor outlet | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263 | 2B | BR-A-TT300 |  | 24 VDC | 0.03 |  |  | Process water | SS316 | 1/2" NPTM |  | Temperature transmitter | [11 empty] | 24 VDC | Process water | SS316 | 1/2" NPTM |  |  |  | Temperature transmitter |  |  |  |  | Process water | [8 empty] | 24 VDC | Process water |  |  | Temperature transmitter |  | Analog | TT
Bioreactor and aeration Temperature transmitter TT510 | C2NC-1500-BR-TT_510 | C2NC-1500-BR | Instruments | Bioreactor and aeration Temperature transmitter. Function: Temperature transmitter air discharge | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263 | 2C | BR-A-TT510 |  | 24 VDC | 0.03 |  |  | Air | SS316 | 1/2" NPTM |  | Temperature transmitter | [11 empty] | 24 VDC | Air | SS316 | 1/2" NPTM |  |  |  | Temperature transmitter |  |  |  |  | Air | [8 empty] | 24 VDC | Air |  |  | Temperature transmitter |  | Analog | TT
Bioreactor and aeration Temperature transmitter TT520 | C2NC-1500-BR-TT_520 | C2NC-1500-BR | Instruments | Bioreactor and aeration Temperature transmitter. Function: Temperature indication air discharge | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263 | 2C | BR-A-TT520 |  | 24 VDC | 0.03 |  |  | Air | SS316 | 1/2" NPTM |  | Temperature transmitter | [11 empty] | 24 VDC | Air | SS316 | 1/2" NPTM |  |  |  | Temperature transmitter |  |  |  |  | Air | [8 empty] | 24 VDC | Air |  |  | Temperature transmitter |  | Analog | TT
Non hazardous proces room Temperature transmitter TT900 | C2NC-1500-NHPR-TT_900 | C2NC-1500-NHPR | Instruments | Non hazardous proces room Temperature transmitter. Function: MEASURE AREA TEMPERATURE | Endress & Hauser | TST434-J1A4DW (inclusive TMT181-I PCP FM+CSA, Class I, Div 1+2 ) RTD Thermometer TST434 | [8 empty] | 9263 | 2H | BR-A-TT900 |  | 24 VDC |  |  |  | AMBIENT AIR | Composition of materials |  |  | Temperature transmitter | [11 empty] | 24 VDC | AMBIENT AIR | Composition of materials |  |  |  |  | Temperature transmitter |  |  |  |  | AMBIENT AIR | [8 empty] | 24 VDC | AMBIENT AIR |  |  | Temperature transmitter |  | Analog | TT
Caustic scrubber Butterfly valve V104 | C2NC-1500-CS-V_104 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Blow flow to scrubber | Apollo | 16 Apollo 215L-16SSP8TA8 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator and chain Wheel | [8 empty] | 9263 | 2A | BR-A-V104 | [5 empty] | Raw biogas | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Raw biogas | AISI316 / PTFE | 16" 150# |  |  |  | Butterfly valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Butterfly valve |  |  | V
Caustic scrubber Butterfly valve V109 | C2NC-1500-CS-V_109 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Block flow after scrubber | Apollo | 16 Apollo 215L-16SSP8TA8 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator and Chain Wheel | [8 empty] | 9263 | 2A | BR-A-V109 | [5 empty] | Clean biogas | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Clean biogas | AISI316 / PTFE | 16" 150# |  |  |  | Butterfly valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Butterfly valve |  |  | V
Caustic scrubber Butterfly valve V201 | C2NC-1500-CS-V_201 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Fill or drain scrubber | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2A | BR-A-V201 | [5 empty] | Process water | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 3" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Circulation pumps Butterfly valve V202 | C2NC-1500-CIRC-V_202 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block circulation flow to scrubber | Apollo | 14 Apollo 215L-14SSP8TA8 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator and Chainwheel Operator | [8 empty] | 9263 | 2B | BR-A-V202 | [5 empty] | Process water | AISI316 / PTFE | 14" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 14" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Caustic scrubber Butterfly valve V204 | C2NC-1500-CS-V_204 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: block flow to bioreactor | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2A | BR-A-V204 | [5 empty] | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 16" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Circulation pumps Butterfly valve V205 | C2NC-1500-CIRC-V_205 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block circulation flow to scrubber | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2B | BR-A-V205 | [5 empty] | Process water | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Circulation pumps Butterfly valve V301 | C2NC-1500-CIRC-V_301 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block in pump | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2B | BR-A-V301 | [5 empty] | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 16" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Circulation pumps Butterfly valve V302 | C2NC-1500-CIRC-V_302 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block in pump | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2B | BR-A-V302 | [5 empty] | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 16" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Circulation pumps Ball valve V303 | C2NC-1500-CIRC-V_303 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Vent | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V303 | [5 empty] | Process water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | AISI316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V304 | C2NC-1500-CIRC-V_304 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Sample/Drain | Flotite | 1" 320-SS-1-FFF-L-025 | [8 empty] | 9263 | 2B | BR-A-V304 | [5 empty] | Process water | AISI316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | AISI316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V305 | C2NC-1500-CIRC-V_305 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block circulation flow to sprayer | Flotite | 2" F150-SS-FFG-L-060 | [8 empty] | 9263 | 2B | BR-A-V305 | [5 empty] | Process water | AISI316 / PTFE | 2" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | AISI316 / PTFE | 2" |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V306 | C2NC-1500-CIRC-V_306 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Drain | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V306 | [5 empty] | Process water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | AISI316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Butterfly valve V311 | C2NC-1500-CIRC-V_311 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block in pump | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2B | BR-A-V311 | [5 empty] | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 16" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Dosing skids Ball valve V710 | C2NC-1500-CHEM-V_710 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Block caustic suction line | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V710 | [5 empty] | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Caustic 20% | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Dosing skids Ball valve V715 | C2NC-1500-CHEM-V_715 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V715 | [5 empty] | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Caustic 20% | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Dosing skids Strainer F710 | C2NC-1500-CHEM-F_710 | C2NC-1500-CHEM | Equipment | Dosing skids Strainer. Function: Filter caustic | Georg Fischer | Type 305 | [8 empty] | 9263 | 2F | BR-A-F710 | [5 empty] | Caustic 20% | PP | 1/2" |  | Strainer
Dosing skids Ball valve V712 | C2NC-1500-CHEM-V_712 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Block in filter | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V712 | [5 empty] | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Caustic 20% | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Dosing skids Dosing Pump (local setpoint, no 4-20mA) P710 | C2NC-1500-CHEM-P_710 | C2NC-1500-CHEM | Equipment | Dosing skids Dosing Pump (local setpoint, no 4-20mA). Function: Pump caustic to Scrubber | Grundfos | DDA 200-4 AR-PVC/E/C-F-31A7A7BG | [8 empty] | 9263 | 2F | BR-A-P710 |  | 12 VAC | 0.2 |  |  | Caustic 20% | PVC, EPDM, ceramic | 1 1/4" NPT (male) |  | Dosing Pump (local setpoint, no 4-20mA)
Dosing skids Pressure control valve (backpressure) PCV710 | C2NC-1500-CHEM-PCV_710 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV710 | [5 empty] | Caustic 20% | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [12 empty] | Caustic 20% | PP / EPDM | 1/2" |  |  |  | Pressure control valve (backpressure) |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V716 | C2NC-1500-CHEM-V_716 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Isolate PI710 | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V716 | [5 empty] | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Caustic 20% | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Dosing skids Pressure gauge PI710 | C2NC-1500-CHEM-PI_710 | C2NC-1500-CHEM | Instruments | Dosing skids Pressure gauge. Function: Local pressure indication caustic | Ashcroft | Process gauge T5500/T6500 Dual Scale 100mm back | [8 empty] | 9263 | 2F | BR-A-PI710 | [5 empty] | Caustic 20% | AISI 316L | 1/2" NPT (male) |  | Pressure gauge | [7 empty] | 0 - 6 bar |  |  |  |  | Caustic 20% | AISI 316L | 1/2" NPT (male) |  |  |  | Pressure gauge |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Pressure gauge |  |  | PI
Dosing skids Pressure control valve (backpressure) PCV711 | C2NC-1500-CHEM-PCV_711 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV711 | [5 empty] | Caustic 20% | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [12 empty] | Caustic 20% | PP / EPDM | 1/2" |  |  |  | Pressure control valve (backpressure) |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V717 | C2NC-1500-CHEM-V_717 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V717 | [5 empty] | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Caustic 20% | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Circulation pumps Butterfly valve V312 | C2NC-1500-CIRC-V_312 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block in pump | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2B | BR-A-V312 | [5 empty] | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 16" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Dosing skids Level switch LS710 | C2NC-1500-CHEM-LS_710 | C2NC-1500-CHEM | Instruments | Dosing skids Level switch. Function: Leak detection | Eriks | EL10 | [8 empty] | 9263 | 2F | BR-A-LS710 |  | 24 VDC |  |  |  | Caustic 20% | PVC-U | 1/2" |  | Level switch | [11 empty] | 24 VDC | Caustic 20% | PVC-U | 1/2" |  |  |  | Level switch |  |  |  |  | Caustic 20% | [8 empty] | 24 VDC | Caustic 20% |  |  | Level switch |  | Digital | LS
Dosing skids Ball valve V718 | C2NC-1500-CHEM-V_718 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Draining cabinet | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V718 | [5 empty] | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Caustic 20% | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Dosing skids Vessel BV720 | C2NC-1500-CHEM-BV_720 | C2NC-1500-CHEM | Valves | Dosing skids Vessel. Function: Storage of nutrients | Grundfos | 300L tank | [8 empty] | 9263 | 2F | BR-A-BV720 | [5 empty] | Nutrients | PE | 300 Liter tank |  | Vessel | [12 empty] | Nutrients | PE | 300 Liter tank |  |  |  | Vessel |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Vessel |  |  | BV
Dosing skids Strainer F720 | C2NC-1500-CHEM-F_720 | C2NC-1500-CHEM | Equipment | Dosing skids Strainer. Function: Filter influent nutrient pump | Grundfos | Part of suction lance RSL-1200-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-F720 | [5 empty] | Nutrients | PP / EPDM | special |  | Strainer
Dosing skids Check valve CV720 | C2NC-1500-CHEM-CV_720 | C2NC-1500-CHEM | Valves | Dosing skids Check valve. Function: Prevent backflow of nutrients into storage vessel | Grundfos | Part of suction lance RSL-1200-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-CV720 | [5 empty] | Nutrients | PVC-U / EPDM | special |  | Check valve | [12 empty] | Nutrients | PVC-U / EPDM | special |  |  |  | Check valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Check valve |  |  | CV
Dosing skids Level switch LS720 | C2NC-1500-CHEM-LS_720 | C2NC-1500-CHEM | Instruments | Dosing skids Level switch. Function: Indicate LL level in storage vessel | Grundfos | Part of suction lance RSL-1200-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-LS720 |  | 24 VDC |  |  |  | Nutrients | PVC-U | special |  | Level switch | [11 empty] | 24 VDC | Nutrients | PVC-U | special |  |  |  | Level switch |  |  |  |  | Nutrients | [8 empty] | 24 VDC | Nutrients |  |  | Level switch |  | Digital | LS
Dosing skids Level switch LS721 | C2NC-1500-CHEM-LS_721 | C2NC-1500-CHEM | Instruments | Dosing skids Level switch. Function: Indicate L level in storage vessel | Grundfos | Part of suction lance RSL-1200-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-LS721 |  | 24 VDC |  |  |  | Nutrients | PVC-U | special |  | Level switch | [11 empty] | 24 VDC | Nutrients | PVC-U | special |  |  |  | Level switch |  |  |  |  | Nutrients | [8 empty] | 24 VDC | Nutrients |  |  | Level switch |  | Digital | LS
Dosing skids Ball valve V720 | C2NC-1500-CHEM-V_720 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Block nutrients suction line | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V720 | [5 empty] | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Nutrients | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Ball valve V721 | C2NC-1500-CHEM-V_721 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V721 | [5 empty] | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Nutrients | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Dosing Pump (local setpoint, no 4-20mA) P720 | C2NC-1500-CHEM-P_720 | C2NC-1500-CHEM | Equipment | Dosing skids Dosing Pump (local setpoint, no 4-20mA). Function: Pump nutrients to scrubber | Grundfos | DDA 7.5-16 AR-PVC/E/C-F-31U7U7BG | [8 empty] | 9263 | 2F | BR-A-P720 |  | 12 VAC | 0.2 |  |  | Nutrients | PVC, EPDM, ceramic | 5/8" NPT (male) |  | Dosing Pump (local setpoint, no 4-20mA)
Dosing skids Pressure control valve (backpressure) PCV720 | C2NC-1500-CHEM-PCV_720 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV720 | [5 empty] | Nutrients | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [12 empty] | Nutrients | PP / EPDM | 1/2" |  |  |  | Pressure control valve (backpressure) |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V722 | C2NC-1500-CHEM-V_722 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Isolate PI720 | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V722 | [5 empty] | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Nutrients | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Pressure gauge PI720 | C2NC-1500-CHEM-PI_720 | C2NC-1500-CHEM | Instruments | Dosing skids Pressure gauge. Function: Local pressure indication nutrients | Ashcroft | Process gauge T5500/T6500 Dual Scale 100mm Back | [8 empty] | 9263 | 2F | BR-A-PI720 | [5 empty] | Nutrients | AISI 316L | 1/2" NPT (male) |  | Pressure gauge | [7 empty] | 0 - 6 bar |  |  |  |  | Nutrients | AISI 316L | 1/2" NPT (male) |  |  |  | Pressure gauge |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Pressure gauge |  |  | PI
Dosing skids Pressure control valve (backpressure) PCV721 | C2NC-1500-CHEM-PCV_721 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV721 | [5 empty] | Nutrients | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [12 empty] | Nutrients | PP / EPDM | 1/2" |  |  |  | Pressure control valve (backpressure) |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V723 | C2NC-1500-CHEM-V_723 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V723 | [5 empty] | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Nutrients | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Ball valve V724 | C2NC-1500-CHEM-V_724 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Draining cabinet | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V724 | [5 empty] | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Nutrients | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Ball valve V725 | C2NC-1500-CHEM-V_725 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Draining cabinet | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V725 | [5 empty] | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Nutrients | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Vessel BV730 | C2NC-1500-CHEM-BV_730 | C2NC-1500-CHEM | Valves | Dosing skids Vessel. Function: Storage of antifoam | Grundfos | Tank 60ltr PE-transp./black | [8 empty] | 9263 | 2F | BR-A-BV730 | [5 empty] | Antifoam | PE | 60l (15 gallons) |  | Vessel | [12 empty] | Antifoam | PE | 60l (15 gallons) |  |  |  | Vessel |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Vessel |  |  | BV
Dosing skids Strainer F730 | C2NC-1500-CHEM-F_730 | C2NC-1500-CHEM | Equipment | Dosing skids Strainer. Function: Filter influent antifoam pump | Grundfos | part of suction lance RSL-0500-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-F730 | [5 empty] | Antifoam | PVC-U | special |  | Strainer
Dosing skids Check valve CV730 | C2NC-1500-CHEM-CV_730 | C2NC-1500-CHEM | Valves | Dosing skids Check valve. Function: Prevent backflow of antifoam into storage vessel | Grundfos | part of suction lance RSL-0500-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-CV730 | [5 empty] | Antifoam | PVC-U / EPDM | special |  | Check valve | [12 empty] | Antifoam | PVC-U / EPDM | special |  |  |  | Check valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Check valve |  |  | CV
Dosing skids Level switch LS730 | C2NC-1500-CHEM-LS_730 | C2NC-1500-CHEM | Instruments | Dosing skids Level switch. Function: Indicate LL level in storage vessel | Grundfos | part of suction lance RSL-0500-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-LS730 |  | 24 VDC |  |  |  | Antifoam | PVC-U | special |  | Level switch | [11 empty] | 24 VDC | Antifoam | PVC-U | special |  |  |  | Level switch |  |  |  |  | Antifoam | [8 empty] | 24 VDC | Antifoam |  |  | Level switch |  | Digital | LS
Dosing skids Level switch LS731 | C2NC-1500-CHEM-LS_731 | C2NC-1500-CHEM | Instruments | Dosing skids Level switch. Function: Indicate L level in storage vessel | Grundfos | part of suction lance RSL-0500-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-LS731 |  | 24 VDC |  |  |  | Antifoam | PVC-U | special |  | Level switch | [11 empty] | 24 VDC | Antifoam | PVC-U | special |  |  |  | Level switch |  |  |  |  | Antifoam | [8 empty] | 24 VDC | Antifoam |  |  | Level switch |  | Digital | LS
Dosing skids Ball valve V730 | C2NC-1500-CHEM-V_730 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Block antifoam input | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V730 | [5 empty] | Antifoam | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Antifoam | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V
Dosing skids Ball valve V731 | C2NC-1500-CHEM-V_731 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V731 | [5 empty] | Antifoam | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Antifoam | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V
Dosing skids Dosing Pump (local setpoint, no 4-20mA) P730 | C2NC-1500-CHEM-P_730 | C2NC-1500-CHEM | Equipment | Dosing skids Dosing Pump (local setpoint, no 4-20mA). Function: Pump antifoam to scrubber | Grundfos | DDA 7.5-16 AR-PVC/E/C-F-31U7U7BG | [8 empty] | 9263 | 2F | BR-A-P730 |  | 12 VAC | 0.2 |  |  | Antifoam | composition | 5/8" NPT (male) |  | Dosing Pump (local setpoint, no 4-20mA)
Dosing skids Pressure control valve (backpressure) PCV730 | C2NC-1500-CHEM-PCV_730 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV730 | [5 empty] | Antifoam | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [12 empty] | Antifoam | PP / EPDM | 1/2" |  |  |  | Pressure control valve (backpressure) |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V732 | C2NC-1500-CHEM-V_732 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Isolate PI730 | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V732 | [5 empty] | Antifoam | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Antifoam | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V
Dosing skids Pressure gauge PI730 | C2NC-1500-CHEM-PI_730 | C2NC-1500-CHEM | Instruments | Dosing skids Pressure gauge. Function: Local pressure indication antifoam | Ashcroft | Process gauge T5500/T6500 Dual Scale 100mm Back | [8 empty] | 9263 | 2F | BR-A-PI730 | [5 empty] | Antifoam | AISI 316L | 1/2" NPT (male) |  | Pressure gauge | [7 empty] | 0 - 6 bar |  |  |  |  | Antifoam | AISI 316L | 1/2" NPT (male) |  |  |  | Pressure gauge |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Pressure gauge |  |  | PI
Dosing skids Pressure control valve (backpressure) PCV731 | C2NC-1500-CHEM-PCV_731 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV731 | [5 empty] | Antifoam | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [12 empty] | Antifoam | PP / EPDM | 1/2" |  |  |  | Pressure control valve (backpressure) |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V733 | C2NC-1500-CHEM-V_733 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V733 | [5 empty] | Antifoam | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Antifoam | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V
Dosing skids Ball valve V734 | C2NC-1500-CHEM-V_734 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Draining cabinet | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V734 | [5 empty] | Antifoam | PP / EPDM | 1/2" |  | Ball valve | [12 empty] | Antifoam | PP / EPDM | 1/2" |  |  |  | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V313 | C2NC-1500-CIRC-V_313 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Vent | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V313 | [5 empty] | Process water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | AISI316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V314 | C2NC-1500-CIRC-V_314 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Drain | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V314 | [5 empty] | Process water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | AISI316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Butterfly valve V316 | C2NC-1500-CIRC-V_316 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block in heat exchanger | Apollo | 4 Apollo 215L-04SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2B | BR-A-V316 | [5 empty] | Cooling water (50% propylene glycol) | AISI316 / PTFE | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Cooling water (50% propylene glycol) | AISI316 / PTFE | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Butterfly valve |  |  | V
Circulation pumps Ball valve V320 | C2NC-1500-CIRC-V_320 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block flow to settler | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2B | BR-A-V320 | [5 empty] | Process water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | AISI316 / PTFE | 1" |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V330 | C2NC-1500-CIRC-V_330 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block circulation flow to discharge | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2B | BR-A-V330 | [5 empty] | Process water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | AISI316 / PTFE | 1" |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V341 | C2NC-1500-CIRC-V_341 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Sample/Drain | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V341 | [5 empty] | Process water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | AISI316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Measurement loop and GQA Ball valve V360 | C2NC-1500-MEAS-V_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Ball valve. Function: Purging/ inertization/sampling | Flotite | 1" 320-SS-1-FFF-025 | [8 empty] | 9263 | 2G | BR-A-V360 | [5 empty] | Process water | AISI316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | AISI316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Measurement loop and GQA Ball valve V361 | C2NC-1500-MEAS-V_361 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Ball valve. Function: Block analysis line | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2G | BR-A-V361 | [5 empty] | Process water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | AISI316 / PTFE | 1" |  |  |  | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Bioreactor and aeration Butterfly valve V400 | C2NC-1500-BR-V_400 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Fill or drain bioreactor | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V400 | [5 empty] | Process water | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 3" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V401 | C2NC-1500-BR-V_401 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block circulation flow to pumps | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2C | BR-A-V401 | [5 empty] | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 16" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V402 | C2NC-1500-BR-V_402 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block pressure transmitter | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V402 | [5 empty] | Process water | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V405 | C2NC-1500-BR-V_405 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block circulation flow from scrubber | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2C | BR-A-V405 | [5 empty] | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 16" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Settler and sludge pump Butterfly valve V406 | C2NC-1500-SLG-V_406 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Overflow of settler to bioreactor | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2D | BR-A-V406 | [5 empty] | Process water | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | AISI316 / PTFE | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Settler and sludge pump Butterfly valve V450 | C2NC-1500-SLG-V_450 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Fill / drain settler | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2D | BR-A-V450 | [5 empty] | Sludge | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Sludge | AISI316 / PTFE | 3" 150# |  |  |  | Butterfly valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Butterfly valve |  |  | V
Settler and sludge pump Butterfly valve V451 | C2NC-1500-SLG-V_451 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Block settler outlet | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2D | BR-A-V451 | [5 empty] | Sludge | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Sludge | AISI316 / PTFE | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Butterfly valve |  |  | V
Settler and sludge pump Butterfly valve V453 | C2NC-1500-SLG-V_453 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Block settler inlet | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2D | BR-A-V453 | [5 empty] | Sludge | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Sludge | AISI316 / PTFE | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Butterfly valve |  |  | V
Settler and sludge pump Ball valve V456 | C2NC-1500-SLG-V_456 | C2NC-1500-SLG | Valves | Settler and sludge pump Ball valve. Function: Sample/Drain | Flotite | 1" 320-SS-1-FFF-025 | [8 empty] | 9263 | 2D | BR-A-V456 | [5 empty] | Sludge | AISI316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Sludge | AISI316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Ball valve |  |  | V
Bioreactor and aeration Butterfly valve V510 | C2NC-1500-BR-V_510 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V510 | [5 empty] | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | AISI316 / PTFE | 3" 150# |  |  |  | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V514 | C2NC-1500-BR-V_514 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V514 | [5 empty] | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | AISI316 / PTFE | 3" 150# |  |  |  | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V515 | C2NC-1500-BR-V_515 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V515 | [5 empty] | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | AISI316 / PTFE | 3" 150# |  |  |  | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V516 | C2NC-1500-BR-V_516 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V516 | [5 empty] | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | AISI316 / PTFE | 3" 150# |  |  |  | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V517 | C2NC-1500-BR-V_517 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V517 | [5 empty] | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | AISI316 / PTFE | 3" 150# |  |  |  | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V518 | C2NC-1500-BR-V_518 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V518 | [5 empty] | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | AISI316 / PTFE | 3" 150# |  |  |  | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V519 | C2NC-1500-BR-V_519 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V519 | [5 empty] | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | AISI316 / PTFE | 3" 150# |  |  |  | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V520 | C2NC-1500-BR-V_520 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet airation line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V520 | [5 empty] | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | AISI316 / PTFE | 3" 150# |  |  |  | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Dilution water Butterfly valve V600 | C2NC-1500-DIL-V_600 | C2NC-1500-DIL | Valves | Dilution water Butterfly valve. Function: Block dilution water flow | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2E | BR-A-V600 | [5 empty] | Water | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Water | AISI316 / PTFE | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | Water | [9 empty] | Water |  |  | Butterfly valve |  |  | V
Dilution water Ball valve V601 | C2NC-1500-DIL-V_601 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Drain | Flotite | 1" 320-SS-1-FFF-025 | [8 empty] | 9263 | 2E | BR-A-V601 | [5 empty] | Water | AISI316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Water | AISI316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V602 | C2NC-1500-CIRC-V_602 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: block water line | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V602 | [5 empty] | Water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Water | AISI316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Dilution water Ball valve V610 | C2NC-1500-DIL-V_610 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Block water to bioreactor / settler | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2E | BR-A-V610 | [5 empty] | Water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Water | AISI316 / PTFE | 1" |  |  |  | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V612 | C2NC-1500-CIRC-V_612 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: block water line | Flotite | 1/2" 320-SS-2-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V612 | [5 empty] | Water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Water | AISI316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Dilution water Ball valve V620 | C2NC-1500-DIL-V_620 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Block water to sulphur discharge | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2E | BR-A-V620 | [5 empty] | Water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Water | AISI316 / PTFE | 1" |  |  |  | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Dilution water Butterfly valve V630 | C2NC-1500-DIL-V_630 | C2NC-1500-DIL | Valves | Dilution water Butterfly valve. Function: Block dilution water to Scrubber | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2E | BR-A-V630 | [5 empty] | Water | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Water | AISI316 / PTFE | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | Water | [9 empty] | Water |  |  | Butterfly valve |  |  | V
Dilution water Ball valve V640 | C2NC-1500-DIL-V_640 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Block flow measurement loop | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2E | BR-A-V640 | [5 empty] | Water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Water | AISI316 / PTFE | 1" |  |  |  | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Dilution water Ball valve V650 | C2NC-1500-DIL-V_650 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Block water flow | Flotite | 1/2" 320-SS-2-FFF-L-015 | [8 empty] | 9263 | 2E | BR-A-V650 | [5 empty] | Water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Water | AISI316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Dilution water Ball valve V651 | C2NC-1500-DIL-V_651 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Deaerate system | Flotite | 1/2" 320-SS-1-FFF-L-016 | [8 empty] | 9263 | 2E | BR-A-V651 | [5 empty] | Water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Water | AISI316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Non hazardous proces room Ball Valve V900 | C2NC-1500-NHPR-V_900 | C2NC-1500-NHPR | Valves | Non hazardous proces room Ball Valve. Function: Block air flow | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2H | BR-A-V900 | [5 empty] | Instrument Air | AISI316 / PTFE | 1" |  | Ball Valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Instrument Air | AISI316 / PTFE | 1" |  |  |  | Ball Valve |  |  |  |  | Instrument Air | [9 empty] | Instrument Air |  |  | Ball Valve |  |  | V
Non hazardous proces room Ball valve V901 | C2NC-1500-NHPR-V_901 | C2NC-1500-NHPR | Valves | Non hazardous proces room Ball valve. Function: Isolate PT900 | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2H | BR-A-V901 | [5 empty] | Instrument Air | AISI316 / PTFE | 1/2" |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Instrument Air | AISI316 / PTFE | 1/2" |  |  |  | Ball valve |  |  |  |  | Instrument Air | [9 empty] | Instrument Air |  |  | Ball valve |  |  | V
Non hazardous proces room Ball valve V902 | C2NC-1500-NHPR-V_902 | C2NC-1500-NHPR | Valves | Non hazardous proces room Ball valve. Function: sampling | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2H | BR-A-V902 | [5 empty] | Instrument Air | AISI316 / PTFE | 1/2" |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Instrument Air | AISI316 / PTFE | 1/2" |  |  |  | Ball valve |  |  |  |  | Instrument Air | [9 empty] | Instrument Air |  |  | Ball valve |  |  | V
Non hazardous proces room Manual valve V910 | C2NC-1500-NHPR-V_910 | C2NC-1500-NHPR | Valves | Non hazardous proces room Manual valve. Function: block air flow | Grainger | Included in Louvre GR910 | [8 empty] | 9263 | 2H | BR-A-V910 | [5 empty] | Ambient air | Aluminium |  |  | Manual valve | [12 empty] | Ambient air | Aluminium |  |  |  |  | Manual valve |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Manual valve |  |  | V
Non hazardous proces room Manual valve V911 | C2NC-1500-NHPR-V_911 | C2NC-1500-NHPR | Valves | Non hazardous proces room Manual valve. Function: block air flow | Grainger | Included in Louvre GR911 | [8 empty] | 9263 | 2H | BR-A-V911 | [5 empty] | Ambient air | Aluminium |  |  | Manual valve | [12 empty] | Ambient air | Aluminium |  |  |  |  | Manual valve |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Manual valve |  |  | V
Non hazardous proces room Manual valve V912 | C2NC-1500-NHPR-V_912 | C2NC-1500-NHPR | Valves | Non hazardous proces room Manual valve. Function: block air flow | Grainger | Included in Louvre GR912 | [8 empty] | 9263 | 2H | BR-A-V912 | [5 empty] | Ambient air | Aluminium |  |  | Manual valve | [12 empty] | Ambient air | Aluminium |  |  |  |  | Manual valve |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Manual valve |  |  | V
Pre-Treatment Ball valve V101 | C2NC-1500-PRE-V_101 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V101 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Flow indicator transmitter FIT110 | C2NC-1500-PRE-FIT_110 | C2NC-1500-PRE | Instruments | Pre-Treatment Flow indicator transmitter. Function: Measure biogas flow | Endress & Hauser | T-mass 65I | [8 empty] | 9263-3A | 3A | MS-A-FIT110 | [5 empty] | BIOGAS | Composition of materials | 1" MNPT in 16" pipe |  | Flow indicator transmitter | [12 empty] | BIOGAS | Composition of materials | 1" MNPT in 16" pipe |  |  |  | Flow indicator transmitter |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Flow indicator transmitter |  | Analog | FIT
Pre-Treatment Heat exchanger HE110 | C2NC-1500-PRE-HE_110 | C2NC-1500-PRE | Equipment | Pre-Treatment Heat exchanger. Function: COOL DOWN GAS | Xchanger | Model C-450 | [8 empty] | 9263-3A | 3A | MS-A-HE110 | [5 empty] | BIOGAS | AISI 316 | 12" 150# (process) 2" (service) |  | Heat exchanger
Pre-Treatment Ball valve V120 | C2NC-1500-PRE-V_120 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: Block drain | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V120 | [5 empty] | CONDENSATE | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | CONDENSATE | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | CONDENSATE | [9 empty] | CONDENSATE |  |  | Ball valve |  |  | V
Pre-Treatment Ball valve V121 | C2NC-1500-PRE-V_121 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: Block drain | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V121 | [5 empty] | CONDENSATE | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | CONDENSATE | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | CONDENSATE | [9 empty] | CONDENSATE |  |  | Ball valve |  |  | V
Pre-Treatment Water separator WS110 | C2NC-1500-PRE-WS_110 | C2NC-1500-PRE | Equipment | Pre-Treatment Water separator. Function: SEPARATE CONDENSED WATER | DMT | according to drawing DMT | [8 empty] | 9263-3A | 3A | MS-A-WS110 | [5 empty] | BIOGAS | AISI 316 | 1" |  | Water separator
Pre-Treatment Level switch LS110 | C2NC-1500-PRE-LS_110 | C2NC-1500-PRE | Instruments | Pre-Treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-3A | 3A | MS-A-LS110 |  | 24 VDC |  |  |  | BIOGAS | Composition of materials | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | BIOGAS | Composition of materials | 3/4" NPT (male) |  |  |  | Level switch |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Level switch |  | Analog | LS
Pre-Treatment Level switch LS111 | C2NC-1500-PRE-LS_111 | C2NC-1500-PRE | Instruments | Pre-Treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-3A | 3A | MS-A-LS111 |  | 24 VDC |  |  |  | BIOGAS | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | BIOGAS | AISI 316L | 3/4" NPT (male) |  |  |  | Level switch |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Level switch |  | Analog | LS
Pre-Treatment Ball valve V130 | C2NC-1500-PRE-V_130 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V130 | [5 empty] | CONDENSATE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | CONDENSATE | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | CONDENSATE | [9 empty] | CONDENSATE |  |  | Ball valve |  |  | V
Pre-Treatment Ball valve AV110 | C2NC-1500-PRE-AV_110 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: CONTROL CONDENSATE DRAIN | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-AV110 | [5 empty] | CONDENSATE | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | CONDENSATE | AISI 316 / PTFE | 1" SW / BW |  |  |  | Ball valve |  |  |  |  | CONDENSATE | [9 empty] | CONDENSATE |  |  | Ball valve |  |  | AV
Pre-Treatment Pneumatic actuator AV110 | C2NC-1500-PRE-AV_110 | C2NC-1500-PRE | Valves | Pre-Treatment Pneumatic actuator. Function: CONTROL CONDENSATE DRAIN | FLO-TITE | AIR-CON | [8 empty] | 9263-3A | 3A | MS-A-AV110 | [5 empty] | CONDENSATE | ALU |  |  | Pneumatic actuator | [12 empty] | CONDENSATE | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | CONDENSATE | [9 empty] | CONDENSATE |  |  | Pneumatic actuator |  |  | AV
Pre-Treatment Solenoid valve AV110 | C2NC-1500-PRE-AV_110 | C2NC-1500-PRE | Valves | Pre-Treatment Solenoid valve. Function: CONTROL CONDENSATE DRAIN | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-3A | 3A | MS-A-AV110 |  | 24 VDC |  |  |  | CONDENSATE | ALU |  |  | Solenoid valve | [12 empty] | CONDENSATE | ALU |  |  |  |  | Solenoid valve |  |  |  |  | CONDENSATE | [8 empty] | 24 VDC | CONDENSATE |  |  | Solenoid valve |  | Digital | AV
Pre-Treatment Temperature transmitter TT110 | C2NC-1500-PRE-TT_110 | C2NC-1500-PRE | Instruments | Pre-Treatment Temperature transmitter. Function: MEASURE INLET TEMPERATURE BIOGAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-3A | 3A | MS-A-TT110 |  | 24 VDC |  |  |  | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [12 empty] | BIOGAS | AISI 316L / ALU | 1/2" NPT |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Pre-Treatment Ball valve V102 | C2NC-1500-PRE-V_102 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: BLOCK GAS MEASUREMENT LINE | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V102 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Ball valve V110 | C2NC-1500-PRE-V_110 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V110 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Ball valve V103 | C2NC-1500-PRE-V_103 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: BLOCK PRESSURE TRANSMITTER | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-V103 |  | 24 VDC |  |  |  | BIOGAS | - | - |  | Ball valve | [12 empty] | BIOGAS | - | - |  |  |  | Ball valve |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Pressure transmitter PT110 | C2NC-1500-PRE-PT_110 | C2NC-1500-PRE | Instruments | Pre-Treatment Pressure transmitter. Function: MEASURE INLET PRESSURE | Aerzen | PMC21-FA1V1HFVWJA+Z1 (E+H) | [8 empty] | 9263-3A | 3A | MS-A-PT110 |  | 24 VDC |  |  |  | BIOGAS | - | - |  | Pressure transmitter | [12 empty] | BIOGAS | - | - |  |  |  | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Pre-Treatment Ball valve V104 | C2NC-1500-PRE-V_104 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: SAMPLE/DRAIN | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-V104 | [5 empty] | BIOGAS | - | - |  | Ball valve | [12 empty] | BIOGAS | - | - |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Compensator BL110 | C2NC-1500-PRE-BL_110 | C2NC-1500-PRE | Equipment | Pre-Treatment Compensator. Function: PREVENT VIBRATIONS TO AFFECT BLOWER'S PIPE | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-BL110 | [5 empty] | BIOGAS | - | - |  | Compensator
Pre-Treatment Feed blower FB110 | C2NC-1500-PRE-FB_110 | C2NC-1500-PRE | Equipment | Pre-Treatment Feed blower. Function: BOOST BIOGAS PRESSURE | Aerzen | AERZEN GM 240 S Special Gas Blower | [8 empty] | 9263-3A | 3A | MS-A-FB110 |  | 480 VAC |  |  |  | BIOGAS |  | 16" 150# |  | Feed blower
Pre-Treatment Check valve CV110 | C2NC-1500-PRE-CV_110 | C2NC-1500-PRE | Valves | Pre-Treatment Check valve. Function: PREVENT BACKFLOW | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-CV110 | [5 empty] | BIOGAS | - | - |  | Check valve | [12 empty] | BIOGAS | - | - |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Pre-Treatment Compensator BL111 | C2NC-1500-PRE-BL_111 | C2NC-1500-PRE | Equipment | Pre-Treatment Compensator. Function: PREVENT VIBRATIONS TO AFFECT BLOWER'S PIPE | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-BL111 | [5 empty] | BIOGAS | - | - |  | Compensator
Pre-Treatment Temperature transmitter TT111 | C2NC-1500-PRE-TT_111 | C2NC-1500-PRE | Instruments | Pre-Treatment Temperature transmitter. Function: MEASURE INLET TEMPERATURE BIOGAS | Aerzen | TH13-2A11E1EBX1AK+A (E+H) | [8 empty] | 9263-3A | 3A | MS-A-TT111 |  | 24 VDC |  |  |  | BIOGAS | - | - |  | Temperature transmitter | [12 empty] | BIOGAS | - | - |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Pre-Treatment Ball valve V131 | C2NC-1500-PRE-V_131 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: BLOCK PRESSURE TRANSMITTER | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-V131 | [5 empty] | BIOGAS | - | - |  | Ball valve | [12 empty] | BIOGAS | - | - |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Pressure transmitter PT130 | C2NC-1500-PRE-PT_130 | C2NC-1500-PRE | Instruments | Pre-Treatment Pressure transmitter. Function: MEASURE PRESSURE AFTER FEEDBLOWERS | Aerzen | PMC21-FA1V1KFVWJA+Z1 (E+H) | [8 empty] | 9263-3A | 3A | MS-A-PT130 |  | 24 VDC |  |  |  | BIOGAS | - | - |  | Pressure transmitter | [12 empty] | BIOGAS | - | - |  |  |  | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Pre-Treatment Ball valve V132 | C2NC-1500-PRE-V_132 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: SAMPLE/DRAIN | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-V132 | [5 empty] | BIOGAS | - | - |  | Ball valve | [12 empty] | BIOGAS | - | - |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Dry cooler heat exchanger HE130 | C2NC-1500-PRE-HE_130 | C2NC-1500-PRE | Equipment | Pre-Treatment Dry cooler heat exchanger. Function: COOL DOWN GAS | AXH Air-coolers | 93AZF | [8 empty] | 9263-3A | 3A | MS-A-HE130 | [5 empty] | BIOGAS | AISI316 | 10" 150# |  | Dry cooler heat exchanger
Pre-Treatment Enclosure fan FA110 | C2NC-1500-PRE-FA_110 | C2NC-1500-PRE | Equipment | Pre-Treatment Enclosure fan. Function: 0 | Toshiba | EQP Global 841, XT | [8 empty] | 9263-3A | 3A | MS-A-FA110 |  | 480 VAC |  |  |  | AIR | Composition of materials |  |  | Enclosure fan
Pre-Treatment Temperature transmitter TT120 | C2NC-1500-PRE-TT_120 | C2NC-1500-PRE | Instruments | Pre-Treatment Temperature transmitter. Function: MEASURE GAS TEMPERATURE | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-3A | 3A | MS-A-TT120 |  | 24 VDC |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Temperature transmitter | [12 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Pre-Treatment Dry cooler fan FA130 | C2NC-1500-PRE-FA_130 | C2NC-1500-PRE | Equipment | Pre-Treatment Dry cooler fan. Function: COOL DOWN GAS | Aerzen | GM 10S 3" air package | [8 empty] | 9263-3A | 3A | MS-A-FA130 |  | 480 VAC |  |  |  | BIOGAS | Composition of materials | 10" 150# |  | Dry cooler fan
Pre-Treatment Vibration switch VS130 | C2NC-1500-PRE-VS_130 | C2NC-1500-PRE | Instruments | Pre-Treatment Vibration switch. Function: 0 | Murphy | Murphy VS 2EX, XP | [8 empty] | 9263-3A | 3A | MS-A-VS130 |  | 24 VDC |  |  |  |  | Composition of materials | - |  | Vibration switch | [13 empty] | Composition of materials | - |  |  |  | Vibration switch | [13 empty] | 24 VDC |  |  |  | Vibration switch |  | Digital | VS
Pre-Treatment Ball valve V133 | C2NC-1500-PRE-V_133 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V133 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Heat exchanger HE140 | C2NC-1500-PRE-HE_140 | C2NC-1500-PRE | Equipment | Pre-Treatment Heat exchanger. Function: COOL DOWN GAS | Xchanger | Model C-425 | [8 empty] | 9263-3A | 3A | MS-A-HE140 | [5 empty] | BIOGAS | AISI 316 | 12" 150# (process) 1.1/2" (service) |  | Heat exchanger
Pre-Treatment CONTROL VALVE AV130 | C2NC-1500-PRE-AV_130 | C2NC-1500-PRE | Valves | Pre-Treatment CONTROL VALVE. Function: Control recycle | FlowServe Valtek | GS General Purpose Control Valve / Flow Under / Cv: 208 / with Hood and Positioner | [8 empty] | 9263-3A | 3A | MS-A-AV130 | [5 empty] | BIOGAS | A351-CF8M (SS) / PTFE Pack. | 4" 150# |  | CONTROL VALVE | [12 empty] | BIOGAS | A351-CF8M (SS) / PTFE Pack. | 4" 150# |  |  |  | CONTROL VALVE |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | CONTROL VALVE |  |  | AV
Pre-Treatment PNEUMATIC ACTUATOR AV130 | C2NC-1500-PRE-AV_130 | C2NC-1500-PRE | Valves | Pre-Treatment PNEUMATIC ACTUATOR. Function: Control recycle | FlowServe Valtek | [9 empty] | 9263-3A | 3A | MS-A-AV130 | [5 empty] | AIR | ALU |  |  | PNEUMATIC ACTUATOR | [12 empty] | AIR | ALU |  |  |  |  | PNEUMATIC ACTUATOR |  |  |  |  | AIR | [9 empty] | AIR |  |  | PNEUMATIC ACTUATOR |  |  | AV
Pre-Treatment POSITIONER AV130 | C2NC-1500-PRE-AV_130 | C2NC-1500-PRE | Valves | Pre-Treatment POSITIONER. Function: Control recycle | FlowServe Logix 400 | Logix 400 Series Digital Positioner, Model 420-40-W1 D-11 | [8 empty] | 9263-3A | 3A | MS-A-AV130 |  | 24 VDC |  |  |  | AIR | ALU |  |  | POSITIONER | [12 empty] | AIR | ALU |  |  |  |  | POSITIONER |  |  |  |  | AIR | [8 empty] | 24 VDC | AIR |  |  | POSITIONER |  | Analog | AV
Pre-Treatment Pressure safety valve PZV130 | C2NC-1500-PRE-PZV_130 | C2NC-1500-PRE | Valves | Pre-Treatment Pressure safety valve. Function: SAFEGUARD PRESSURE | Leser | 5262T6654 | [8 empty] | 9263-3A | 3A | MS-A-PZV130 | [5 empty] | BIOGAS | AISI 316 | 6" 150# in / 8" 150# out |  | Pressure safety valve | [12 empty] | BIOGAS | AISI 316 | 6" 150# in / 8" 150# out |  |  |  | Pressure safety valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Pressure safety valve |  |  | PZV
Pre-Treatment Compensator BL130 | C2NC-1500-PRE-BL_130 | C2NC-1500-PRE | Equipment | Pre-Treatment Compensator. Function: PREVENT VIBRATIONS TO AFFECT BLOWER'S PIPE | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-BL130 | [5 empty] | BIOGAS | - | 16" 150# |  | Compensator
Pre-Treatment Ball valve V138 | C2NC-1500-PRE-V_138 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V138 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Butterfly valve AV140 | C2NC-1500-PRE-AV_140 | C2NC-1500-PRE | Valves | Pre-Treatment Butterfly valve. Function: BLOCK OFF GAS FLOW | Emerson | Keystone Series GR RSBV; ASME 150 DI Lug Body | [8 empty] | 9263-3A | 3A | MS-A-AV140 | [5 empty] | BIOGAS | AISI 316 / HNBR | 14" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / HNBR | 14" 150# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | AV
Pre-Treatment Pneumatic actuator AV140 | C2NC-1500-PRE-AV_140 | C2NC-1500-PRE | Valves | Pre-Treatment Pneumatic actuator. Function: BLOCK OFF GAS FLOW | Emerson | Keystone F89U Rack and Pinion Actuator; | [8 empty] | 9263-3A | 3A | MS-A-AV140 | [5 empty] | BIOGAS | Composition of materials | NA 150# |  | Pneumatic actuator | [7 empty] | 10 Barg - 140 Psig |  |  |  |  | BIOGAS | Composition of materials | NA 150# |  |  |  | Pneumatic actuator |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Pneumatic actuator |  |  | AV
Pre-Treatment Solenoid valve AV140 | C2NC-1500-PRE-AV_140 | C2NC-1500-PRE | Valves | Pre-Treatment Solenoid valve. Function: BLOCK OFF GAS FLOW | Asco | ASCO 8551 Solenoid Valve; 3-Way Aluminum Body | [8 empty] | 9263-3A | 3A | MS-A-AV140 |  | 24 VDC |  |  |  | BIOGAS | Composition of materials |  |  | Solenoid valve | [12 empty] | BIOGAS | Composition of materials |  |  |  |  | Solenoid valve |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Solenoid valve |  | Digital | AV
Pre-Treatment Ball valve V135 | C2NC-1500-PRE-V_135 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V135 | [5 empty] | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Pre-Treatment Butterfly valve V752 | C2NC-1500-PRE-V_752 | C2NC-1500-PRE | Valves | Pre-Treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Emerson | FIG 320 WAFER TRIM 112 | [8 empty] | 9263-3A | 3A | MS-A-V752 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Pre-Treatment Dearation valve DAV750 | C2NC-1500-PRE-DAV_750 | C2NC-1500-PRE | Equipment | Pre-Treatment Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO NPT | [8 empty] | 9263-3A | 3A | MS-A-DAV750 | [5 empty] | GLYCOL MIXTURE | Brass | 1/2" FNPT |  | Dearation valve
Pre-Treatment Ball valve V753 | C2NC-1500-PRE-V_753 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V753 | [5 empty] | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Pre-Treatment Butterfly valve V751 | C2NC-1500-PRE-V_751 | C2NC-1500-PRE | Valves | Pre-Treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Emerson | FIG 320 WAFER TRIM 112 | [8 empty] | 9263-3A | 3A | MS-A-V751 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Pre-Treatment Ball valve V743 | C2NC-1500-PRE-V_743 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V743 | [5 empty] | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Pre-Treatment Butterfly valve V744 | C2NC-1500-PRE-V_744 | C2NC-1500-PRE | Valves | Pre-Treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Emerson | FIG 320 WAFER TRIM 112 | [8 empty] | 9263-3A | 3A | MS-A-V744 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Pre-Treatment Dearation valve DAV740 | C2NC-1500-PRE-DAV_740 | C2NC-1500-PRE | Equipment | Pre-Treatment Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO NPT | [8 empty] | 9263-3A | 3A | MS-A-DAV740 | [5 empty] | GLYCOL MIXTURE | Brass | 1/2" FNPT |  | Dearation valve
Pre-Treatment Butterfly valve V745 | C2NC-1500-PRE-V_745 | C2NC-1500-PRE | Valves | Pre-Treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Emerson | FIG 320 WAFER TRIM 112 | [8 empty] | 9263-3A | 3A | MS-A-V745 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Active carbon vessels Pressure indicator transmitter PIT131 | C2NC-1500-ACV-PIT_131 | C2NC-1500-ACV | Instruments | Active carbon vessels Pressure indicator transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-3B | 3B | MS-A-PIT131 |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Active carbon vessels Temperature transmitter TT130 | C2NC-1500-ACV-TT_130 | C2NC-1500-ACV | Instruments | Active carbon vessels Temperature transmitter. Function: MEASURE INLET TEMPERATURE BIOGAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-3B | 3B | MS-A-TT130 |  | 24 VDC |  |  |  | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [12 empty] | BIOGAS | AISI 316L / ALU | 1/2" NPT |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Active carbon vessels Butterfly valve V150A | C2NC-1500-ACV-V_150A | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V150A | [5 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [12 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Ball valve V151A | C2NC-1500-ACV-V_151A | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: SAMPLE/DRAIN | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V151A | [5 empty] | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Spectacle flange SF150A | C2NC-1500-ACV-SF_150A | C2NC-1500-ACV | Equipment | Active carbon vessels Spectacle flange. Function: BLOCK IN CARBON VESSEL | DMT | Spectacle blind flange | [8 empty] | 9263-3B | 3B | MS-A-SF150A | [5 empty] | BIOGAS | AISI 316 | 20" 150# |  | Spectacle flange
Active carbon vessels Ball valve V154A | C2NC-1500-ACV-V_154A | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: DRAIN | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V154A | [5 empty] | BIOGAS | AISI 316L / PTFE | 2" NPT |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316L / PTFE | 2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Carbon vessel CF150A | C2NC-1500-ACV-CF_150A | C2NC-1500-ACV | Tanks | Active carbon vessels Carbon vessel. Function: REMOVING POLLUTANTS FROM BIOGAS | Kuipers | according to drawing DMT | [8 empty] | 9263-3B | 3B | MS-A-CF150A | [33 empty] | BIOGAS | AISI 316 | 20" 150# |  |  |  |  | Carbon vessel
Active carbon vessels Spectacle flange SF160A | C2NC-1500-ACV-SF_160A | C2NC-1500-ACV | Equipment | Active carbon vessels Spectacle flange. Function: BLOCK IN CARBON VESSEL | DMT | Spectacle blind flange | [8 empty] | 9263-3B | 3B | MS-A-SF160A | [5 empty] | BIOGAS | AISI 316 | 20" 150# |  | Spectacle flange
Active carbon vessels Ball valve V152A | C2NC-1500-ACV-V_152A | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK PRESSURE TRANSMITTER | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V152A | [5 empty] | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Pressure transmitter PT150A | C2NC-1500-ACV-PT_150A | C2NC-1500-ACV | Instruments | Active carbon vessels Pressure transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-3B | 3B | MS-A-PT150A |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Active carbon vessels Pressure safety valve PZV150A | C2NC-1500-ACV-PZV_150A | C2NC-1500-ACV | Valves | Active carbon vessels Pressure safety valve. Function: SAFEGUARD PRESSURE | Leser | 52626652 | [8 empty] | 9263-3B | 3B | MS-A-PZV150A | [5 empty] | BIOGAS | CS with SS internals | 6" 150# in / 8" 150# out |  | Pressure safety valve | [12 empty] | BIOGAS | CS with SS internals | 6" 150# in / 8" 150# out |  |  |  | Pressure safety valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Pressure safety valve |  |  | PZV
Active carbon vessels Ball valve V155A | C2NC-1500-ACV-V_155A | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK INERTISATION LINE | Emerson | F155 three piece body ball valve | [8 empty] | 9263-3B | 3B | MS-A-V155A | [5 empty] | BIOGAS | AISI 316 / PTFE | 2" NPT |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Ball valve V156A | C2NC-1500-ACV-V_156A | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK GAS MEASUREMENT LINE | Emerson | F120 two piece body ball valve | [8 empty] | 9263-3B | 3B | MS-A-V156A | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT (Female) |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Butterfly valve V158A | C2NC-1500-ACV-V_158A | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V158A | [5 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [12 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Butterfly valve V160A | C2NC-1500-ACV-V_160A | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V160A | [5 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [12 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Butterfly valve V150B | C2NC-1500-ACV-V_150B | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V150B | [5 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [12 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Ball valve V151B | C2NC-1500-ACV-V_151B | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: SAMPLE/DRAIN | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V151B | [5 empty] | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Spectacle flange SF150B | C2NC-1500-ACV-SF_150B | C2NC-1500-ACV | Equipment | Active carbon vessels Spectacle flange. Function: BLOCK IN CARBON VESSEL | DMT | Spectacle blind flange | [8 empty] | 9263-3B | 3B | MS-A-SF150B | [5 empty] | BIOGAS | AISI 316 | 20" 150# |  | Spectacle flange
Active carbon vessels Ball valve V154B | C2NC-1500-ACV-V_154B | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: DRAIN | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V154B | [5 empty] | BIOGAS | AISI 316L / PTFE | 2" NPT |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316L / PTFE | 2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Carbon vessel CF150B | C2NC-1500-ACV-CF_150B | C2NC-1500-ACV | Tanks | Active carbon vessels Carbon vessel. Function: REMOVING POLLUTANTS FROM BIOGAS | Kuipers | according to drawing DMT | [8 empty] | 9263-3B | 3B | MS-A-CF150B | [33 empty] | BIOGAS | AISI 316 | 20" 150# |  |  |  |  | Carbon vessel
Active carbon vessels Spectacle flange SF160B | C2NC-1500-ACV-SF_160B | C2NC-1500-ACV | Equipment | Active carbon vessels Spectacle flange. Function: BLOCK IN CARBON VESSEL | DMT | Spectacle blind flange | [8 empty] | 9263-3B | 3B | MS-A-SF160B | [5 empty] | BIOGAS | AISI 316 | 20" 150# |  | Spectacle flange
Active carbon vessels Ball valve V152B | C2NC-1500-ACV-V_152B | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK PRESSURE TRANSMITTER | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V152B | [5 empty] | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Pressure transmitter PT150B | C2NC-1500-ACV-PT_150B | C2NC-1500-ACV | Instruments | Active carbon vessels Pressure transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-3B | 3B | MS-A-PT150B |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Active carbon vessels Pressure safety valve PZV150B | C2NC-1500-ACV-PZV_150B | C2NC-1500-ACV | Valves | Active carbon vessels Pressure safety valve. Function: SAFEGUARD PRESSURE | Leser | 52626652 | [8 empty] | 9263-3B | 3B | MS-A-PZV150B | [5 empty] | BIOGAS | CS with SS internals | 6" 150# in / 8" 150# out |  | Pressure safety valve | [12 empty] | BIOGAS | CS with SS internals | 6" 150# in / 8" 150# out |  |  |  | Pressure safety valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Pressure safety valve |  |  | PZV
Active carbon vessels Ball valve V155B | C2NC-1500-ACV-V_155B | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK INERTISATION LINE | Emerson | F155 three piece body ball valve | [8 empty] | 9263-3B | 3B | MS-A-V155B | [5 empty] | BIOGAS | AISI 316 / PTFE | 2" NPT |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Ball valve V156B | C2NC-1500-ACV-V_156B | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK GAS MEASUREMENT LINE | Emerson | F120 two piece body ball valve | [8 empty] | 9263-3B | 3B | MS-A-V156B | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT (Female) |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Butterfly valve V158B | C2NC-1500-ACV-V_158B | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V158B | [5 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [12 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Butterfly valve V160B | C2NC-1500-ACV-V_160B | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V160B | [5 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [12 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Ball valve V160 | C2NC-1500-ACV-V_160 | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK PRESSURE TRANSMITTER | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V160 | [5 empty] | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Pressure transmitter PT160 | C2NC-1500-ACV-PT_160 | C2NC-1500-ACV | Instruments | Active carbon vessels Pressure transmitter. Function: MEASURE OUTLET PRESSURE | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-3B | 3B | MS-A-PT160 |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Active carbon vessels Temperature transmitter TT160 | C2NC-1500-ACV-TT_160 | C2NC-1500-ACV | Instruments | Active carbon vessels Temperature transmitter. Function: MEASURE OUTLET TEMPERATURE BIOGAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-3B | 3B | MS-A-TT160 |  | 24 VDC |  |  |  | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [12 empty] | BIOGAS | AISI 316L / ALU | 1/2" NPT |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Feed gas compressor Ball valve V200 | C2NC-1500-FGC-V_200 | C2NC-1500-FGC | Valves | Feed gas compressor Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4A | 4A | MS-A-V200 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Feed gas compressor Butterfly valve V201 | C2NC-1500-FGC-V_201 | C2NC-1500-FGC | Valves | Feed gas compressor Butterfly valve. Function: Block Filter | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-4A | 4A | MS-A-V201 | [5 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [12 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Feed gas compressor Filter F200 | C2NC-1500-FGC-F_200 | C2NC-1500-FGC | Equipment | Feed gas compressor Filter. Function: FILTER PARTICLES | Omega Air | GBF 3000 DN500 ASME - including filter elements 20 pcs. (76090 GP) 3µm | [8 empty] | 9263-4A | 4A | MS-A-F200 | [5 empty] | BIOGAS | CS | 12" 150# |  | Filter
Feed gas compressor Gas compressor GC200 | C2NC-1500-FGC-GC_200 | C2NC-1500-FGC | Equipment | Feed gas compressor Gas compressor. Function: COMPRESS BIOGAS | Vilter | [9 empty] | 9263-4A | 4A | MS-A-GC200 |  | 4160 VAC |  |  |  | BIOGAS |  |  |  | Gas compressor
Feed gas compressor Check valve CV202 | C2NC-1500-FGC-CV_202 | C2NC-1500-FGC | Valves | Feed gas compressor Check valve. Function: 0 | Titan | CV 44-CS | [8 empty] | 9263-4A | 4A | MS-A-CV202 | [5 empty] | BIOGAS | CS | 4" 300# |  | Check valve | [7 empty] | 740 Psi |  |  |  |  | BIOGAS | CS | 4" 300# |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Feed gas compressor Butterfly valve V202 | C2NC-1500-FGC-V_202 | C2NC-1500-FGC | Valves | Feed gas compressor Butterfly valve. Function: 0 | ABZ valve | ABZolute 400 series lugged ANSI 300 | [8 empty] | 9263-4A | 4A | MS-A-V202 | [5 empty] | BIOGAS | CS | 4" 300# |  | Butterfly valve | [12 empty] | BIOGAS | CS | 4" 300# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Feed gas compressor Heat exchanger gas compressor HE200 | C2NC-1500-FGC-HE_200 | C2NC-1500-FGC | Equipment | Feed gas compressor Heat exchanger gas compressor. Function: COOL DOWND COOLING MEDIUM | Vilter | TTA545-6-90-1F78H-D | [8 empty] | 9263-4A | 4A | MS-A-HE200 | [5 empty] | OIL |  |  |  | Heat exchanger gas compressor
Feed gas compressor Butterfly valve V211 | C2NC-1500-FGC-V_211 | C2NC-1500-FGC | Valves | Feed gas compressor Butterfly valve. Function: Block Filter | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-4A | 4A | MA-A-V211 | [5 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [12 empty] | BIOGAS | AISI 316 / NBR | 20" 150# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Feed gas compressor Filter F210 | C2NC-1500-FGC-F_210 | C2NC-1500-FGC | Equipment | Feed gas compressor Filter. Function: FILTER PARTICLES | Omega Air | GBF 3000 DN500 ASME - including filter elements 20 pcs. (76090 GP) 3µm | [8 empty] | 9263-4A | 4A | MS-A-F210 | [5 empty] | BIOGAS | CS | 12" 150# |  | Filter
Feed gas compressor Gas compressor GC210 | C2NC-1500-FGC-GC_210 | C2NC-1500-FGC | Equipment | Feed gas compressor Gas compressor. Function: COMPRESS BIOGAS | Vilter | [9 empty] | 9263-4A | 4A | MS-A-GC210 |  | 4160 VAC |  |  |  | BIOGAS |  |  |  | Gas compressor
Feed gas compressor Check valve CV212 | C2NC-1500-FGC-CV_212 | C2NC-1500-FGC | Valves | Feed gas compressor Check valve. Function: 0 | Titan | CV 44-CS | [8 empty] | 9263-4A | 4A | MS-A-CV212 | [5 empty] | BIOGAS | CS | 4" 300# |  | Check valve | [7 empty] | 740 Psi |  |  |  |  | BIOGAS | CS | 4" 300# |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Feed gas compressor Butterfly valve V212 | C2NC-1500-FGC-V_212 | C2NC-1500-FGC | Valves | Feed gas compressor Butterfly valve. Function: 0 | ABZ valve | ABZolute 400 series lugged ANSI 300 | [8 empty] | 9263-4A | 4A | MS-A-V212 | [5 empty] | BIOGAS | CS | 4" 300# |  | Butterfly valve | [12 empty] | BIOGAS | CS | 4" 300# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Feed gas compressor Heat exchanger gas compressor HE210 | C2NC-1500-FGC-HE_210 | C2NC-1500-FGC | Equipment | Feed gas compressor Heat exchanger gas compressor. Function: COOL DOWND COOLING MEDIUM | Vilter | TTA545-6-90-1F78H-D | [8 empty] | 9263-4A | 4A | MS-A-HE210 | [5 empty] | OIL |  |  |  | Heat exchanger gas compressor
Compressed gas treatment Ball valve AV304 | C2NC-1500-CGT-AV_304 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN CONDENSATE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-AV304 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | AV
Compressed gas treatment Pneumatic actuator AV304 | C2NC-1500-CGT-AV_304 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: DRAIN CONDENSATE | Air Con | Air Con CSR63 | [8 empty] | 9263-4B | 4B | MS-A-AV304 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Solenoid valve AV304 | C2NC-1500-CGT-AV_304 | C2NC-1500-CGT | Valves | Compressed gas treatment Solenoid valve. Function: DRAIN CONDENSATE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4B | 4B | MS-A-AV304 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Compressed gas treatment Ball valve V306 | C2NC-1500-CGT-V_306 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V306 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Dry cooler heat exchanger HE300 | C2NC-1500-CGT-HE_300 | C2NC-1500-CGT | Equipment | Compressed gas treatment Dry cooler heat exchanger. Function: COOL DOWN GAS | Vilter | TTS440-8-123-1F78H-P | [8 empty] | 9263-4B | 4B | MS-A-HE300 | [5 empty] | BIOGAS |  | 6" 300# |  | Dry cooler heat exchanger
Compressed gas treatment Dry Cooler Fan (in Vilter package) FA300 | C2NC-1500-CGT-FA_300 | C2NC-1500-CGT | Equipment | Compressed gas treatment Dry Cooler Fan (in Vilter package). Function: COOL DOWN GAS | Vilter | STAMP | [8 empty] | 9263-4B | 4B | MS-A-FA300 |  | 480 VAC |  |  |  | BIOGAS |  |  |  | Dry Cooler Fan (in Vilter package)
Compressed gas treatment Temperature transmitter TT300 | C2NC-1500-CGT-TT_300 | C2NC-1500-CGT | Instruments | Compressed gas treatment Temperature transmitter. Function: Measure inlet temperature | Vilter | - | [8 empty] | 9263-4B | 4B | MS-A-TT300 |  | 24 VDC |  |  |  | BIOGAS | - | - |  | Temperature transmitter | [12 empty] | BIOGAS | - | - |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Compressed gas treatment Temperature transmitter TT310 | C2NC-1500-CGT-TT_310 | C2NC-1500-CGT | Instruments | Compressed gas treatment Temperature transmitter. Function: Measure outlet temperature | Vilter | - | [8 empty] | 9263-4B | 4B | MS-A-TT310 |  | 24 VDC |  |  |  | BIOGAS | - | - |  | Temperature transmitter | [12 empty] | BIOGAS | - | - |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Compressed gas treatment Ball valve AV310 | C2NC-1500-CGT-AV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN CONDENSATE TO CLIENT | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-AV310 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | AV
Compressed gas treatment Pneumatic actuator AV310 | C2NC-1500-CGT-AV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: DRAIN CONDENSATE TO CLIENT | Air Con | Air Con CSR63 | [8 empty] | 9263-4B | 4B | MS-A-AV310 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Solenoid valve AV310 | C2NC-1500-CGT-AV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Solenoid valve. Function: DRAIN CONDENSATE TO CLIENT | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4B | 4B | MS-A-AV310 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Compressed gas treatment Ball valve AV314 | C2NC-1500-CGT-AV_314 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN CONDENSATE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-AV314 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | AV
Compressed gas treatment Pneumatic actuator AV314 | C2NC-1500-CGT-AV_314 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: DRAIN CONDENSATE | Air Con | Air Con CSR63 | [8 empty] | 9263-4B | 4B | MS-A-AV314 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Water separator WS300 | C2NC-1500-CGT-WS_300 | C2NC-1500-CGT | Equipment | Compressed gas treatment Water separator. Function: SEPARATE CONDENSED WATER | Omega Air | SFH SS 088 PN20 6" Cl.300 SS304 - ASME - Including filter element SFH 088 SS : cyclone is welded inside | [8 empty] | 9263-4B | 4B | MS-A-WS300 | [5 empty] | BIOGAS | AISI 304 | 6" #300 |  | Water separator
Compressed gas treatment Filter (Water separator) F310 | C2NC-1500-CGT-F_310 | C2NC-1500-CGT | Equipment | Compressed gas treatment Filter (Water separator). Function: SEPARATE CONDENSED WATER | Omega Air | WHFIF 900 6" SS304 - ASME - Including filter elements: 1 x 3 pcs.(PN 3030) 5µm | [8 empty] | 9263-4B | 4B | MS-A-F310 | [5 empty] | BIOGAS | AISI 304 | 6" #300 |  | Filter (Water separator)
Compressed gas treatment Filter F320 | C2NC-1500-CGT-F_320 | C2NC-1500-CGT | Equipment | Compressed gas treatment Filter. Function: FILTER PARTICLES | Omega Air | WHFIF 900 6" SS304 - ASME - Including filter elements : 2 x 3 pcs. (PR 3030) 1µm | [8 empty] | 9263-4B | 4B | MS-A-F320 | [5 empty] | BIOGAS | AISI 304 | 6" #300 |  | Filter
Compressed gas treatment Filter F330 | C2NC-1500-CGT-F_330 | C2NC-1500-CGT | Equipment | Compressed gas treatment Filter. Function: FILTER PARTICLES | Omega Air | WHFIF 900 6" SS304 - ASME - Including filter elements : 2 x 3 pcs. (PM 3030) 0,1µm | [8 empty] | 9263-4B | 4B | MS-A-F330 | [5 empty] | BIOGAS | AISI 304 | 6" #300 |  | Filter
Compressed gas treatment Solenoid valve AV314 | C2NC-1500-CGT-AV_314 | C2NC-1500-CGT | Valves | Compressed gas treatment Solenoid valve. Function: DRAIN CONDENSATE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4B | 4B | MS-A-AV314 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Compressed gas treatment Control valve AV340 | C2NC-1500-CGT-AV_340 | C2NC-1500-CGT | Valves | Compressed gas treatment Control valve. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | Conovalve | S803 - D Control Valve 6"- ANSI CLASS 300 AV340 | [8 empty] | 9263-4B | 4B | MS-A-AV340 | [5 empty] | BIOGAS | AISI 316L / PTFE | 6" #300 |  | Control valve | [7 empty] | ASME CLASS 300 |  |  |  |  | BIOGAS | AISI 316L / PTFE | 6" #300 |  |  |  | Control valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Control valve |  |  | AV
Compressed gas treatment Pneumatic actuator AV340 | C2NC-1500-CGT-AV_340 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | S430/I | [8 empty] | 9263-4B | 4B | MS-A-AV340 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Control unit/ positioner AV340 | C2NC-1500-CGT-AV_340 | C2NC-1500-CGT | Valves | Compressed gas treatment Control unit/ positioner. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | V200E-IS (using Non Incendive Field Wiring for use without barrier in Class I Div.2 !! | [8 empty] | 9263-4B | 4B | MS-A-AV340 |  | 24 VDC |  |  |  | COMPRESSED AIR |  |  |  | Control unit/ positioner | [12 empty] | COMPRESSED AIR | [5 empty] | Control unit/ positioner |  |  |  |  | COMPRESSED AIR | [8 empty] | 24 VDC | COMPRESSED AIR |  |  | Control unit/ positioner |  | Analog | AV
Compressed gas treatment Ball valve AV324 | C2NC-1500-CGT-AV_324 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN CONDENSATE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-AV324 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | AV
Compressed gas treatment Pneumatic actuator AV324 | C2NC-1500-CGT-AV_324 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: DRAIN CONDENSATE | Air Con | Air Con CSR63 | [8 empty] | 9263-4B | 4B | MS-A-AV324 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Solenoid valve AV324 | C2NC-1500-CGT-AV_324 | C2NC-1500-CGT | Valves | Compressed gas treatment Solenoid valve. Function: DRAIN CONDENSATE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4B | 4B | MS-A-AV324 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Compressed gas treatment Ball valve AV334 | C2NC-1500-CGT-AV_334 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN CONDENSATE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-AV334 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | AV
Compressed gas treatment Filter F350 | C2NC-1500-CGT-F_350 | C2NC-1500-CGT | Equipment | Compressed gas treatment Filter. Function: FILTER PARTICLES | Omega Air | WHFIF 900 6"SS304 - ASME - Including filter elements : 2 x 3 pcs. (PR 3030) 1µm | [8 empty] | 9263-4B | 4B | MS-A-F350 | [5 empty] | BIOGAS | AISI 304 | 6" #300 |  | Filter
Compressed gas treatment Pneumatic actuator AV334 | C2NC-1500-CGT-AV_334 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: DRAIN CONDENSATE | Air Con | Air Con CSR63 | [8 empty] | 9263-4B | 4B | MS-A-AV334 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Filter F360 | C2NC-1500-CGT-F_360 | C2NC-1500-CGT | Equipment | Compressed gas treatment Filter. Function: FILTER PARTICLES | Omega Air | WHFIF 900 6" SS304 - ASME - Including filter elements : 2 x 3 pcs. (PS 3030) 0,01µm | [8 empty] | 9263-4B | 4B | MS-A-F360 | [5 empty] | BIOGAS | AISI 304 | 6" #300 |  | Filter
Compressed gas treatment Solenoid valve AV334 | C2NC-1500-CGT-AV_334 | C2NC-1500-CGT | Valves | Compressed gas treatment Solenoid valve. Function: DRAIN CONDENSATE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4B | 4B | MS-A-AV334 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV400 | C2NC-1500-MBR-AV_400 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANES | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV400 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV400 | C2NC-1500-MBR-AV_400 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANES | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV400 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV400 | C2NC-1500-MBR-AV_400 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANES | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV400 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV401 | C2NC-1500-MBR-AV_401 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: ISOLATE PERMEATE SIDE MEMBRANES | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV401 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV401 | C2NC-1500-MBR-AV_401 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: ISOLATE PERMEATE SIDE MEMBRANES | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV401 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV401 | C2NC-1500-MBR-AV_401 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: ISOLATE PERMEATE SIDE MEMBRANES | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV401 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.01 | C2NC-1500-MBR-AV_411.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.01 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.01 | C2NC-1500-MBR-AV_411.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.01 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.01 | C2NC-1500-MBR-AV_411.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.01 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.02 | C2NC-1500-MBR-AV_411.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.02 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.02 | C2NC-1500-MBR-AV_411.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.02 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.02 | C2NC-1500-MBR-AV_411.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.02 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.03 | C2NC-1500-MBR-AV_411.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.03 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.03 | C2NC-1500-MBR-AV_411.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.03 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.03 | C2NC-1500-MBR-AV_411.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.03 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.04 | C2NC-1500-MBR-AV_411.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.04 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.04 | C2NC-1500-MBR-AV_411.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.04 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.04 | C2NC-1500-MBR-AV_411.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.04 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.05 | C2NC-1500-MBR-AV_411.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.05 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.05 | C2NC-1500-MBR-AV_411.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.05 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.05 | C2NC-1500-MBR-AV_411.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.05 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.06 | C2NC-1500-MBR-AV_411.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.06 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.06 | C2NC-1500-MBR-AV_411.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.06 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.06 | C2NC-1500-MBR-AV_411.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.06 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.07 | C2NC-1500-MBR-AV_411.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.07 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.07 | C2NC-1500-MBR-AV_411.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.07 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.07 | C2NC-1500-MBR-AV_411.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.07 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.08 | C2NC-1500-MBR-AV_411.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.08 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.08 | C2NC-1500-MBR-AV_411.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.08 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.08 | C2NC-1500-MBR-AV_411.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.08 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.09 | C2NC-1500-MBR-AV_411.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.09 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.09 | C2NC-1500-MBR-AV_411.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.09 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.09 | C2NC-1500-MBR-AV_411.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.09 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.01 | C2NC-1500-MBR-AV_412.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.01 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.01 | C2NC-1500-MBR-AV_412.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.01 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.01 | C2NC-1500-MBR-AV_412.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.01 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.02 | C2NC-1500-MBR-AV_412.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.02 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.02 | C2NC-1500-MBR-AV_412.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.02 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.02 | C2NC-1500-MBR-AV_412.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.02 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.03 | C2NC-1500-MBR-AV_412.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.03 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.03 | C2NC-1500-MBR-AV_412.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.03 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.03 | C2NC-1500-MBR-AV_412.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.03 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.04 | C2NC-1500-MBR-AV_412.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.04 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.04 | C2NC-1500-MBR-AV_412.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.04 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.04 | C2NC-1500-MBR-AV_412.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.04 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.05 | C2NC-1500-MBR-AV_412.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.05 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.05 | C2NC-1500-MBR-AV_412.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.05 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.05 | C2NC-1500-MBR-AV_412.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.05 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.06 | C2NC-1500-MBR-AV_412.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.06 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.06 | C2NC-1500-MBR-AV_412.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.06 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.06 | C2NC-1500-MBR-AV_412.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.06 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.07 | C2NC-1500-MBR-AV_412.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.07 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.07 | C2NC-1500-MBR-AV_412.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.07 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.07 | C2NC-1500-MBR-AV_412.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.07 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.08 | C2NC-1500-MBR-AV_412.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.08 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.08 | C2NC-1500-MBR-AV_412.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.08 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.08 | C2NC-1500-MBR-AV_412.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.08 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.09 | C2NC-1500-MBR-AV_412.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.09 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.09 | C2NC-1500-MBR-AV_412.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.09 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.09 | C2NC-1500-MBR-AV_412.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.09 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Membranes Butterfly valve AV551 | C2NC-1500-MBR-AV_551 | C2NC-1500-MBR | Valves | Membranes Butterfly valve. Function: PROTECT FLARE | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C | 4C | MS-A-AV551 | [5 empty] | BIOGAS | AISI 316L / PTFE | 6" 300# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316L / PTFE | 6" 300# |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | AV
Membranes Pneumatic actuator AV551 | C2NC-1500-MBR-AV_551 | C2NC-1500-MBR | Valves | Membranes Pneumatic actuator. Function: PROTECT FLARE | Xomox | SR-FC | [8 empty] | 9263-4C | 4C | MS-A-AV551 | [5 empty] | BIOGAS | ALU |  |  | Pneumatic actuator | [7 empty] | 10 Barg - 140 Psig |  |  |  |  | BIOGAS | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Pneumatic actuator |  |  | AV
Membranes Solenoid valve AV551 | C2NC-1500-MBR-AV_551 | C2NC-1500-MBR | Valves | Membranes Solenoid valve. Function: PROTECT FLARE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C | 4C | MS-A-AV551 |  | 24 VDC |  |  |  | BIOGAS | ALU |  |  | Solenoid valve | [12 empty] | BIOGAS | ALU |  |  |  |  | Solenoid valve |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Solenoid valve |  | Digital | AV
Membranes Ball valve AV620 | C2NC-1500-MBR-AV_620 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK BY PASS | FLO-TITE | FULL-FLO SERIES | [8 empty] | 9263-4C | 4C | MS-A-AV620 | [5 empty] | BIOGAS | AISI 316 / PTFE | 2" 150# |  | Ball valve | [7 empty] | 280 Psig |  |  |  |  | BIOGAS | AISI 316 / PTFE | 2" 150# |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | AV
Membranes Pneumatic actuator AV620 | C2NC-1500-MBR-AV_620 | C2NC-1500-MBR | Valves | Membranes Pneumatic actuator. Function: BLOCK BY PASS | Air Con | CSR52 | [8 empty] | 9263-4C | 4C | MS-A-AV620 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [7 empty] | 10 Barg - 140 Psig |  |  |  |  | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes Solenoid valve AV620 | C2NC-1500-MBR-AV_620 | C2NC-1500-MBR | Valves | Membranes Solenoid valve. Function: BLOCK BY PASS | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C | 4C | MS-A-AV620 |  | 24 VDC |  |  |  |  | ALU |  |  | Solenoid valve | [13 empty] | ALU |  |  |  |  | Solenoid valve | [13 empty] | 24 VDC |  |  |  | Solenoid valve |  | Digital | AV
Compressed gas treatment Buffer vessel BV310 | C2NC-1500-CGT-BV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Buffer vessel. Function: COLLECT CONDENSATE | Fabricator | according to drawing DMT | [8 empty] | 9263-4B | 4B | MS-A-BV310 | [5 empty] | PROCESSS WATER | AISI 316 | 6" sch 80 |  | Buffer vessel | [7 empty] | 300 PSIG |  |  |  |  | PROCESSS WATER | AISI 316 | 6" sch 80 |  |  |  | Buffer vessel |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Buffer vessel |  |  | BV
Compressed gas treatment Carbon filter CF340 | C2NC-1500-CGT-CF_340 | C2NC-1500-CGT | Tanks | Compressed gas treatment Carbon filter. Function: REMOVE RESIDUAL OIL | Apache | according to drawing DMT | [8 empty] | 9263-4B | 4B | MS-A-CF340 | [33 empty] | BIOGAS | AISI 304 | 6" #300 |  |  |  |  | Carbon Filter
Compressed gas treatment Check valve CV310 | C2NC-1500-CGT-CV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Check valve. Function: PREVENT BACKFLOW | Swagelok | C Series | [8 empty] | 9263-4B | 4B | MS-A-CV310 | [5 empty] | PROCESS WATER | AISI 316L / FKM | 1/2" SWAGELOK |  | Check valve | [7 empty] | 3000 PSIG @ 100°F |  |  |  |  | PROCESS WATER | AISI 316L / FKM | 1/2" SWAGELOK |  |  |  | Check valve |  |  |  |  | PROCESS WATER | [9 empty] | PROCESS WATER |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.01 | C2NC-1500-MBR-CV_413.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.01 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.02 | C2NC-1500-MBR-CV_413.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.02 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.03 | C2NC-1500-MBR-CV_413.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.03 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.04 | C2NC-1500-MBR-CV_413.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.04 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.05 | C2NC-1500-MBR-CV_413.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.05 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.06 | C2NC-1500-MBR-CV_413.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.06 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.07 | C2NC-1500-MBR-CV_413.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.07 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.08 | C2NC-1500-MBR-CV_413.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.08 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.09 | C2NC-1500-MBR-CV_413.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.09 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.10 | C2NC-1500-MBR-CV_413.10 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.10 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.11 | C2NC-1500-MBR-CV_413.11 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.11 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.12 | C2NC-1500-MBR-CV_413.12 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.12 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.13 | C2NC-1500-MBR-CV_413.13 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.13 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.14 | C2NC-1500-MBR-CV_413.14 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.14 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes Check valve CV510 | C2NC-1500-MBR-CV_510 | C2NC-1500-MBR | Valves | Membranes Check valve. Function: PREVENT BACKFLOW FROM PRODUCT GAS | Champion Valves Inc | Double disc spring loaded wafer check valve | [8 empty] | 9263-4C | 4C | MS-A-CV510 | [5 empty] | BIOGAS | AISI 316 / NBR | 6" #300 |  | Check valve | [7 empty] | 300 PSIG |  |  |  |  | BIOGAS | AISI 316 / NBR | 6" #300 |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes Check valve CV520 | C2NC-1500-MBR-CV_520 | C2NC-1500-MBR | Valves | Membranes Check valve. Function: PREVENT BACKFLOW | Champion Valves Inc | Double disc spring loaded wafer check valve | [8 empty] | 9263-4C | 4C | MS-A-CV520 | [5 empty] | BIOGAS | AISI 316 / NBR | 8" #300 |  | Check valve | [7 empty] | 300 PSIG |  |  |  |  | BIOGAS | AISI 316 / NBR | 8" #300 |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Membranes Check valve CV631 | C2NC-1500-MBR-CV_631 | C2NC-1500-MBR | Valves | Membranes Check valve. Function: PREVENT BACKFLOW | Champion Valves Inc | CV 12-SS | [8 empty] | 9263-4C | 4C | MS-A-CV631 | [5 empty] | BIOGAS | AISI 316 / NBR | 12" 150# |  | Check valve | [7 empty] | 300 PSIG |  |  |  |  | BIOGAS | AISI 316 / NBR | 12" 150# |  |  |  | Check valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Check valve |  |  | CV
Compressed gas treatment Dearation valve DAV741 | C2NC-1500-CGT-DAV_741 | C2NC-1500-CGT | Equipment | Compressed gas treatment Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO NPT | [8 empty] | 9263-4B | 4B | MS-A-DAV741 | [5 empty] | GLYCOL MIXTURE | Brass | 1/2" FNPT |  | Dearation valve
Container unit Emergency stop ES912 | C2NC-1500-CU-ES_912 | C2NC-1500-CU | Instruments | Container unit Emergency stop. Function: STOP INSTALLATION | Square D Schneider | Mushroom type, color Red, manual pull-release | [8 empty] | 9263-4F | 4F | MS-A-ES912 |  | 24 VDC | [7 empty] | Emergency stop | [18 empty] | Emergency stop | [13 empty] | 24 VDC |  |  |  | Emergency stop |  |  | ES
Container unit Emergency stop ES913 | C2NC-1500-CU-ES_913 | C2NC-1500-CU | Instruments | Container unit Emergency stop. Function: STOP INSTALLATION | Square D Schneider | Mushroom type, color Red, manual pull-release | [8 empty] | 9263-4F | 4F | MS-A-ES913 |  | 24 VDC | [7 empty] | Emergency stop | [18 empty] | Emergency stop | [13 empty] | 24 VDC |  |  |  | Emergency stop |  |  | ES
Container unit Fan FA910 | C2NC-1500-CU-FA_910 | C2NC-1500-CU | Equipment | Container unit Fan. Function: AIR VENTILATION CONTAINER | PennBarry | Penn Barry DX18B with 1/3 HP and 675 RPM | [8 empty] | 9263-4F | 4F | MS-A-FA910 |  | 480 VAC |  |  |  | AMBIENT AIR | Composition of materials |  |  | Fan
Membranes Flow indicator transmitter FIT500 | C2NC-1500-MBR-FIT_500 | C2NC-1500-MBR | Instruments | Membranes Flow indicator transmitter. Function: MEASURE FLOW OF PRODUCT GAS | Endress & Hauser | Promass 40E50 | [8 empty] | 9263-4C | 4C | MS-A-FIT500 |  | 24 VDC |  |  |  | BIOGAS | AISI 316 | 2" 300# |  | Flow indicator transmitter | [7 empty] | 1450 PSIG |  |  |  |  | BIOGAS | AISI 316 | 2" 300# |  |  |  | Flow indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Flow indicator transmitter |  | Analog | FIT
Membranes Flow indicator transmitter FIT520 | C2NC-1500-MBR-FIT_520 | C2NC-1500-MBR | Instruments | Membranes Flow indicator transmitter. Function: MEASURE FLOW TO STACK | Endress & Hauser | T-mass 65I | [8 empty] | 9263-4C | 4C | MS-A-FIT520 |  | 24 VDC |  |  |  | BIOGAS | AISI 316 | 1" NPT in 8" pipe |  | Flow indicator transmitter | [7 empty] | 290 PSIG |  |  |  |  | BIOGAS | AISI 316 | 1" NPT in 8" pipe |  |  |  | Flow indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Flow indicator transmitter |  | Analog | FIT
Container unit Flow switch FS910 | C2NC-1500-CU-FS_910 | C2NC-1500-CU | Instruments | Container unit Flow switch. Function: CONFIRM AIR FLOW | Ameritrol | FX-1000-D, 1 MNPT, 1.8 probe | [8 empty] | 9263-4F | 4F | MS-A-FS910 |  | 24 VDC |  |  |  | AMBIENT AIR |  |  |  | Flow switch | [12 empty] | AMBIENT AIR | [5 empty] | Flow switch |  |  |  |  | AMBIENT AIR | [8 empty] | 24 VDC | AMBIENT AIR |  |  | Flow switch |  | Digital | FS
Container unit Grid GR910 | C2NC-1500-CU-GR_910 | C2NC-1500-CU | Equipment | Container unit Grid. Function: Air outlet | PennBarry | part of FA910 | [8 empty] | 9263-4F | 4F | MS-A-GR910 | [5 empty] | Ambient air | Aluminium |  |  | Grid
Container unit Grid GR911 | C2NC-1500-CU-GR_911 | C2NC-1500-CU | Equipment | Container unit Grid. Function: Air outlet | PennBarry | part of FA910 | [8 empty] | 9263-4F | 4F | MS-A-GR911 | [5 empty] | Ambient air | Aluminium |  |  | Grid
Container unit Grid GR914 | C2NC-1500-CU-GR_914 | C2NC-1500-CU | Equipment | Container unit Grid. Function: Air inlet | Greenhack | EACA-601 24x24" | [8 empty] | 9263-4F | 4F | MS-A-GR914 | [5 empty] | Ambient air | Aluminium | 24x24" |  | Grid
Container unit Grid GR915 | C2NC-1500-CU-GR_915 | C2NC-1500-CU | Equipment | Container unit Grid. Function: Air inlet | Greenhack | EACA-601 24x24" | [8 empty] | 9263-4F | 4F | MS-A-GR915 | [5 empty] | Ambient air | Aluminium | 24x24" |  | Grid
Compressed gas treatment Heat exchanger HE310 | C2NC-1500-CGT-HE_310 | C2NC-1500-CGT | Equipment | Compressed gas treatment Heat exchanger. Function: COOL DOWN GAS | Swep | B427Lx314/1P-SC-S 4x4"VIC + 28259 SUPPORT LEGS + 22266 | [8 empty] | 9263-4B | 4B | MS-A-HE310 | [5 empty] | BIOGAS |  | 4" VIC |  | Heat exchanger
Compressed gas treatment Heat exchanger HE340 | C2NC-1500-CGT-HE_340 | C2NC-1500-CGT | Equipment | Compressed gas treatment Heat exchanger. Function: COOL DOWN GAS | Swep | B65Lx242/1P-SC-S 4x4"VIC + SUPPORT LEG + 22266 ASME U | [8 empty] | 9263-4B | 4B | MS-A-HE340 | [5 empty] | BIOGAS |  | 4" VIC |  | Heat exchanger
Compressed gas treatment Heat exchanger HE460 | C2NC-1500-CGT-HE_460 | C2NC-1500-CGT | Equipment | Compressed gas treatment Heat exchanger. Function: COOL DOWN GAS | Swep | B65Lx248/1P-SC-S 4x4"VIC + SUPPORT LEGS + 22266 ASME U | [8 empty] | 9263-4B | 4B | MS-A-HE460 | [5 empty] | BIOGAS |  | 4" VIC |  | Heat exchanger
Container unit Heater (switches as one with /912 & /913) HE911 | C2NC-1500-CU-HE_911 | C2NC-1500-CU | Equipment | Container unit Heater (switches as one with /912 & /913). Function: HEATING CONTROL ROOM | Markel | Hazardous Location WALL CONVECTOR heaters | [8 empty] | 9263-4F | 4F | MS-A-HE911 |  | 480 VAC |  |  |  | AMBIENT AIR |  |  |  | Heater (switches as one with /912 & /913)
Container unit Heater (switches as one with /911 & /913) HE912 | C2NC-1500-CU-HE_912 | C2NC-1500-CU | Equipment | Container unit Heater (switches as one with /911 & /913). Function: HEATING CONTROL ROOM | Markel | Hazardous Location WALL CONVECTOR heaters | [8 empty] | 9263-4F | 4F | MS-A-HE912 |  | 480 VAC |  |  |  | AMBIENT AIR |  |  |  | Heater (switches as one with /911 & /913)
Container unit Heater (switches as one with /911 & /912) HE913 | C2NC-1500-CU-HE_913 | C2NC-1500-CU | Equipment | Container unit Heater (switches as one with /911 & /912). Function: HEATING CONTROL ROOM | Markel | Hazardous Location WALL CONVECTOR heaters | [8 empty] | 9263-4F | 4F | MS-A-HE913 |  | 480 VAC |  |  |  | AMBIENT AIR |  |  |  | Heater (switches as one with /911 & /912)
Container unit LEL TRANSMITTER LEL910 | C2NC-1500-CU-LEL_910 | C2NC-1500-CU | Instruments | Container unit LEL TRANSMITTER. Function: DETECTION OF FLAMMABLE GASSES AND VAPORS | Dräger | Polytron® 5700 IR (incl. magnetic wand) | [8 empty] | 9263-4F | 4F | MS-A-LEL910 |  | 24 VDC |  |  |  | AMBIENT AIR | AISI 316 L |  |  | LEL TRANSMITTER | [12 empty] | AMBIENT AIR | AISI 316 L |  |  |  |  | LEL TRANSMITTER |  |  |  |  | AMBIENT AIR | [8 empty] | 24 VDC | AMBIENT AIR |  |  | LEL TRANSMITTER |  | Analog | LEL
Compressed gas treatment Level switch LS300 | C2NC-1500-CGT-LS_300 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS300 |  | 24 VDC |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  |  |  | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Compressed gas treatment Level switch LS310 | C2NC-1500-CGT-LS_310 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS310 |  | 24 VDC |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  |  |  | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Compressed gas treatment Level switch LS312 | C2NC-1500-CGT-LS_312 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: HIGH LEVEL GUARD FUNCTIONING OF BV310 | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS312 |  | 24 VDC |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  |  |  | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Compressed gas treatment Level switch LS313 | C2NC-1500-CGT-LS_313 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: LOW LEVEL GUARD FUNCTIONING OF BV310 | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS313 |  | 24 VDC |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  |  |  | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Compressed gas treatment Level switch LS320 | C2NC-1500-CGT-LS_320 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS320 |  | 24 VDC |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  |  |  | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Compressed gas treatment Level switch LS330 | C2NC-1500-CGT-LS_330 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS330 |  | 24 VDC |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  |  |  | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Membranes stage 1 Needle valve NV400 | C2NC-1500-MBR-NV_400 | C2NC-1500-MBR | Valves | Membranes stage 1 Needle valve. Function: CONTROL FLOW TO MEMBRANES | Swagelok | Stainless Steel Integral Bonnet Needle Valve, 0.73 Cv, 1/2 in. Swagelok Tube Fitting, Regulating Stem | [8 empty] | 9263-4C1 | 4C1 | MS-A-NV400 | [5 empty] | Biogas | ASI 316 | 1/2" swagelok |  | Needle valve | [7 empty] | 3435 PSIG |  |  |  |  | Biogas | ASI 316 | 1/2" swagelok |  |  |  | Needle valve |  |  |  |  | Biogas | [9 empty] | Biogas |  |  | Needle valve |  |  | NV
Membranes stage 1 Orifice OF400 | C2NC-1500-MBR-OF_400 | C2NC-1500-MBR | Equipment | Membranes stage 1 Orifice. Function: REDUCE FLOW AND PRESSURE TO MEMBRANES | DMT | Dia 2,5 mm / 0,1" | [8 empty] | 9263-4C1 | 4C1 | MS-A-OF400 | [5 empty] | BIOGAS | ASI 316 | 1/2" #300 |  | Orifice
Membranes Orifice OF550 | C2NC-1500-MBR-OF_550 | C2NC-1500-MBR | Equipment | Membranes Orifice. Function: REDUCE FLOW AND PRESSURE TO FLARE | DMT | Dia 5mm / 0.2" according drawing DMT | [8 empty] | 9263-4C | 4C | MS-A-OF550 | [5 empty] | BIOGAS | ASI 316 | 6" #300 |  | Orifice
Membranes stage 1 Membrane stage 1, 1st row M1.1.01 | C2NC-1500-MBR-M_1.1.01 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.01 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.02 | C2NC-1500-MBR-M_1.1.02 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.02 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.03 | C2NC-1500-MBR-M_1.1.03 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.03 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.04 | C2NC-1500-MBR-M_1.1.04 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.04 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.04 | C2NC-1500-MBR-M_1.1.04 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.04 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.06 | C2NC-1500-MBR-M_1.1.06 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.06 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.07 | C2NC-1500-MBR-M_1.1.07 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.07 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.08 | C2NC-1500-MBR-M_1.1.08 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.08 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.09 | C2NC-1500-MBR-M_1.1.09 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.09 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.10 | C2NC-1500-MBR-M_1.1.10 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.10 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.11 | C2NC-1500-MBR-M_1.1.11 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.11 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.12 | C2NC-1500-MBR-M_1.1.12 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.12 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.13 | C2NC-1500-MBR-M_1.1.13 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.13 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Membranes stage 1 Membrane stage 1, 1st row M1.1.14 | C2NC-1500-MBR-M_1.1.14 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.14 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row
Compressed gas treatment Back pressure regulator PCV310 | C2NC-1500-CGT-PCV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Back pressure regulator. Function: REDUCE PRESSURE ON CONDENSATE TANK | Swagelok | Stainless Steel BP Regulator, 0 to 100 psig (3.4 bar), A Configuration, PCTFE Seal, 1/4 in. FNPT, 0.20 Cv | [8 empty] | 9263-4B | 4B | MS-A-PCV310 | [5 empty] | PROCESSS WATER | AISI 316L / PTFE | 1/4" NPT (FEMALE) |  | Back pressure regulator | [7 empty] | 248 Barg - 3600 Psig |  |  |  |  | PROCESSS WATER | AISI 316L / PTFE | 1/4" NPT (FEMALE) |  |  |  | Back pressure regulator |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Back pressure regulator |  |  | PCV
Membranes Back pressure regulator PCV500 | C2NC-1500-MBR-PCV_500 | C2NC-1500-MBR | Valves | Membranes Back pressure regulator. Function: REDUCE PRESSURE TO GASANALYZER | Swagelok | Stainless Steel PR Regulator, 0 to 25 psig (1.7 bar), 3600 psig (248 bar) inlet, C Config, PCTFE Seat, 1/4 in. FNPT, 0.06 Cv | [8 empty] | 9263-4C | 4C | MS-A-PCV500 | [5 empty] | BIOGAS | AISI 316L / PTFE | 1/4" NPT (FEMALE) |  | Back pressure regulator | [7 empty] | 248 Barg - 3600 Psig |  |  |  |  | BIOGAS | AISI 316L / PTFE | 1/4" NPT (FEMALE) |  |  |  | Back pressure regulator |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Back pressure regulator |  |  | PCV
Container unit Pressure reducing valve PCV910 | C2NC-1500-CU-PCV_910 | C2NC-1500-CU | Valves | Container unit Pressure reducing valve. Function: Adjust air supply pressure | Festo | MS6-LFR size 9 | [8 empty] | 9263-4F | 4F | MS-A-PCV910 | [5 empty] | Instrument Air | composition | 1" |  | Pressure reducing valve | [7 empty] | 0,8 - 20 bar |  |  |  |  | Instrument Air | composition | 1" |  |  |  | Pressure reducing valve |  |  |  |  | Instrument Air | [9 empty] | Instrument Air |  |  | Pressure reducing valve |  |  | PCV
Compressed gas treatment Pressure indicator PI310 | C2NC-1500-CGT-PI_310 | C2NC-1500-CGT | Instruments | Compressed gas treatment Pressure indicator. Function: INDICATE PRESSURE | Ashcroft | 1008S Pressure Gauge D63mm | [8 empty] | 9263-4B | 4B | MS-A-PI310 |  |  |  | NEMA 4 / IP65 |  | PROCESSS WATER | AISI 316 | 1/4"NPT (MALE) |  | Pressure indicator | [7 empty] | 0-60 Psig |  |  |  |  | PROCESSS WATER | AISI 316 | 1/4"NPT (MALE) |  |  |  | Pressure indicator |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Pressure indicator |  |  | PI
Membranes Pressure indicator PI500 | C2NC-1500-MBR-PI_500 | C2NC-1500-MBR | Instruments | Membranes Pressure indicator. Function: INDICATE SET PRESSURE TO GAS ANLYZER | Ashcroft | 1008S Pressure Gauge D63mm | [8 empty] | 9263-4C | 4C | MS-A-PI500 |  |  |  | NEMA 4 / IP65 |  | BIOGAS | AISI 316 | 1/4"NPT (MALE) |  | Pressure indicator | [7 empty] | 0-30 Psig |  |  |  |  | BIOGAS | AISI 316 | 1/4"NPT (MALE) |  |  |  | Pressure indicator |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Pressure indicator |  |  | PI
Compressed gas treatment Pressure indicator transmitter PIT320 | C2NC-1500-CGT-PIT_320 | C2NC-1500-CGT | Instruments | Compressed gas treatment Pressure indicator transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4B | 4B | MS-A-PIT320 |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Compressed gas treatment Pressure indicator transmitter PIT340 | C2NC-1500-CGT-PIT_340 | C2NC-1500-CGT | Instruments | Compressed gas treatment Pressure indicator transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4B | 4B | MS-A-PIT340 |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Membranes Pressure indicator transmitter PIT370 | C2NC-1500-MBR-PIT_370 | C2NC-1500-MBR | Instruments | Membranes Pressure indicator transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4C | 4C | MS-A-PIT370 |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Membranes Pressure indicator transmitter PIT500 | C2NC-1500-MBR-PIT_500 | C2NC-1500-MBR | Instruments | Membranes Pressure indicator transmitter. Function: MEASSURE PRESSURE AFTER STAGE 2B | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4C | 4C | MS-A-PIT500 |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Membranes Pressure indicator transmitter PIT510 | C2NC-1500-MBR-PIT_510 | C2NC-1500-MBR | Instruments | Membranes Pressure indicator transmitter. Function: MEASSURE PRESSURE AFTER AV400 | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4C | 4C | MS-A-PIT510 |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Membranes Pressure indicator transmitter PIT550 | C2NC-1500-MBR-PIT_550 | C2NC-1500-MBR | Instruments | Membranes Pressure indicator transmitter. Function: MEASSURE PRESSURE AFTER AV400 | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4C | 4C | MS-A-PIT550 |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Compressed gas treatment Pressure transmitter PT310 | C2NC-1500-CGT-PT_310 | C2NC-1500-CGT | Instruments | Compressed gas treatment Pressure transmitter. Function: MEASURE PRESSURE IN BV310 | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-4B | 4B | MS-A-PT310 |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Membranes stage 1 Pressure transmitter PT400 | C2NC-1500-MBR-PT_400 | C2NC-1500-MBR | Instruments | Membranes stage 1 Pressure transmitter. Function: MEASSURE PRESSURE AFTER AV400 | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-4C1 | 4C1 | MS-A-PT400 |  | 24 VDC |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | 316L / FKM | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Container unit Pressure transmitter PT910 | C2NC-1500-CU-PT_910 | C2NC-1500-CU | Instruments | Container unit Pressure transmitter. Function: MONITOR PRESSURE | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-4F | 4F | MS-A-PT910 |  | 24 VDC |  |  |  | INSTRUMENT AIR | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | INSTRUMENT AIR | 316L / FKM | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | INSTRUMENT AIR | [8 empty] | 24 VDC | INSTRUMENT AIR |  |  | Pressure transmitter |  | Analog | PT
Membranes stage 1 Spectacle flange SF420 | C2NC-1500-MBR-SF_420 | C2NC-1500-MBR | Equipment | Membranes stage 1 Spectacle flange. Function: BLOCK IN MEMBRANES | Fabricator MS | according to drawing DMT | [8 empty] | 9263-4C1 | 4C1 | MS-A-SF420 | [5 empty] | BIOGAS | AISI 316 | 8" #300 |  | Spectacle flange
Membranes stage 1 Spectacle flange SF421 | C2NC-1500-MBR-SF_421 | C2NC-1500-MBR | Equipment | Membranes stage 1 Spectacle flange. Function: BLOCK IN MEMBRANES | Fabricator MS | according to drawing DMT | [8 empty] | 9263-4C1 | 4C1 | MS-A-SF421 | [5 empty] | BIOGAS | AISI 316 | 6" #300 |  | Spectacle flange
Membranes Spectacle flange SF512 | C2NC-1500-MBR-SF_512 | C2NC-1500-MBR | Equipment | Membranes Spectacle flange. Function: BLOCK STACK DURING START-UP | DMT | according to drawing DMT | [8 empty] | 9263-4C | 4C | MS-A-SF512 | [5 empty] | BIOGAS | AISI 316 | 6" #300 |  | Spectacle flange
Membranes stage 1 Membrane stage 1, 2nd row M1.2.01 | C2NC-1500-MBR-M_1.2.01 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 2nd row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.2.01 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 2nd row
Membranes stage 1 Membrane stage 1, 2nd row M1.2.02 | C2NC-1500-MBR-M_1.2.02 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 2nd row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.2.02 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 2nd row
Membranes stage 1 Membrane stage 1, 2nd row M1.2.03 | C2NC-1500-MBR-M_1.2.03 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 2nd row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.2.03 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 2nd row
Membranes stage 1 Membrane stage 1, 2nd row M1.2.04 | C2NC-1500-MBR-M_1.2.04 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 2nd row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.2.04 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 2nd row
Container unit Sound indicator ( Horn ) SI910 | C2NC-1500-CU-SI_910 | C2NC-1500-CU | Instruments | Container unit Sound indicator ( Horn ). Function: CREATE AUDIO WARNING SIGNAL | E2S Warning signals | D2xS1 AC115 AB1 A1R | [8 empty] | 9263-4F | 4F | MS-A-SI910 |  | 115 VAC |  |  |  | AMBIENT AIR | Aluminium - Red - RAL3000 | 130x180x125mm (wxhxd) |  | Sound indicator ( Horn ) | [12 empty] | AMBIENT AIR | Aluminium - Red - RAL3000 | 130x180x125mm (wxhxd) |  |  |  | Sound indicator ( Horn ) |  |  |  |  | AMBIENT AIR | [8 empty] | 115 VAC | AMBIENT AIR |  |  | Sound indicator ( Horn ) |  | Digital | SI
Container unit Sound indicator ( Horn ) SI912 | C2NC-1500-CU-SI_912 | C2NC-1500-CU | Instruments | Container unit Sound indicator ( Horn ). Function: CREATE AUDIO WARNING SIGNAL | E2S Warning signals | D2xS1 AC115 AB1 A1R | [8 empty] | 9263-4F | 4F | MS-A-SI912 |  | 115 VAC |  |  |  | AMBIENT AIR | Aluminium - Red - RAL3000 | 130x180x125mm (wxhxd) |  | Sound indicator ( Horn ) | [12 empty] | AMBIENT AIR | Aluminium - Red - RAL3000 | 130x180x125mm (wxhxd) |  |  |  | Sound indicator ( Horn ) |  |  |  |  | AMBIENT AIR | [8 empty] | 115 VAC | AMBIENT AIR |  |  | Sound indicator ( Horn ) |  | Digital | SI
Container unit Signal lamp SL910 | C2NC-1500-CU-SL_910 | C2NC-1500-CU | Instruments | Container unit Signal lamp. Function: CREATE VISUAL WARNING | Edwards Signaling | 105 Series (Blue High Intensity Beacon) | [8 empty] | 9263-4F | 4F | MS-A-SL910 |  | 120 VAC |  |  |  | AMBIENT AIR |  | Diam. 4,5' |  | Signal lamp | [12 empty] | AMBIENT AIR |  | Diam. 4,5' |  |  |  | Signal lamp |  |  |  |  | AMBIENT AIR | [8 empty] | 120 VAC | AMBIENT AIR |  |  | Signal lamp |  | Digital | SL
Membranes Control valve AV460 | C2NC-1500-MBR-AV_460 | C2NC-1500-MBR | Valves | Membranes Control valve. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | Conovalve | S803 - D Control Valve 4"- ANSI CLASS 300 AV460 CV160 | [8 empty] | 9263-4C | 4C | MS-A-AV460 | [5 empty] | BIOGAS | AISI 316L / PTFE | 4" #300 |  | Control valve | [7 empty] | ASME CLASS 300 |  |  |  |  | BIOGAS | AISI 316L / PTFE | 4" #300 |  |  |  | Control valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Control valve |  |  | AV
Membranes Pneumatic actuator AV460 | C2NC-1500-MBR-AV_460 | C2NC-1500-MBR | Valves | Membranes Pneumatic actuator. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | S340/I | [8 empty] | 9263-4C | 4C | MS-A-AV460 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes Control unit/ positioner AV460 | C2NC-1500-MBR-AV_460 | C2NC-1500-MBR | Valves | Membranes Control unit/ positioner. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | V200E-IS (using Non Incendive Field Wiring for use without barrier in Class I Div.2 !! | [8 empty] | 9263-4C | 4C | MS-A-AV460 |  | 24 VDC |  |  |  | COMPRESSED AIR |  |  |  | Control unit/ positioner | [12 empty] | COMPRESSED AIR | [5 empty] | Control unit/ positioner |  |  |  |  | COMPRESSED AIR | [8 empty] | 24 VDC | COMPRESSED AIR |  |  | Control unit/ positioner |  | Analog | AV
Container unit Signal lamp SL911 | C2NC-1500-CU-SL_911 | C2NC-1500-CU | Instruments | Container unit Signal lamp. Function: CREATE VISUAL WARNING | Edwards Signaling | 105 Series (Blue High Intensity Beacon) | [8 empty] | 9263-4F | 4F | MS-A-SL911 |  | 120 VAC |  |  |  | AMBIENT AIR |  | Diam. 4,5' |  | Signal lamp | [12 empty] | AMBIENT AIR |  | Diam. 4,5' |  |  |  | Signal lamp |  |  |  |  | AMBIENT AIR | [8 empty] | 120 VAC | AMBIENT AIR |  |  | Signal lamp |  | Digital | SL
Membranes stage 2A Membrane stage 2A, 1st row M2.1.01 | C2NC-1500-MBR-M_2.1.01 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.01 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row
Membranes stage 2A Membrane stage 2A, 1st row M2.1.02 | C2NC-1500-MBR-M_2.1.02 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.02 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row
Membranes stage 2A Membrane stage 2A, 1st row M2.1.03 | C2NC-1500-MBR-M_2.1.03 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.03 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row
Membranes stage 2A Membrane stage 2A, 1st row M2.1.04 | C2NC-1500-MBR-M_2.1.04 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.04 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row
Membranes stage 2A Membrane stage 2A, 1st row M2.1.05 | C2NC-1500-MBR-M_2.1.05 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.05 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row
Membranes stage 2A Membrane stage 2A, 1st row M2.1.06 | C2NC-1500-MBR-M_2.1.06 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.06 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row
Membranes stage 2A Membrane stage 2A, 1st row M2.1.07 | C2NC-1500-MBR-M_2.1.07 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.07 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row
Membranes stage 2A Membrane stage 2A, 1st row M2.1.08 | C2NC-1500-MBR-M_2.1.08 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.08 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row
Membranes stage 2A Membrane stage 2A, 1st row M2.1.09 | C2NC-1500-MBR-M_2.1.09 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.09 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row
Membranes stage 2A Membrane stage 2A, 1st row M2.1.10 | C2NC-1500-MBR-M_2.1.10 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.10 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row
Compressed gas treatment Temperature transmitter TT320 | C2NC-1500-CGT-TT_320 | C2NC-1500-CGT | Instruments | Compressed gas treatment Temperature transmitter. Function: MEASURE INLET TEMPERATURE BIOGAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4B | 4B | MS-A-TT320 |  | 24 VDC |  |  |  | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [12 empty] | BIOGAS | AISI 316L / ALU | 1/2" NPT |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Membranes stage 2B Membrane stage 2B, 1st row M2.3.01 | C2NC-1500-MBR-M_2.3.01 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.01 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.3.02 | C2NC-1500-MBR-M_2.3.02 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.02 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.3.03 | C2NC-1500-MBR-M_2.3.03 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.03 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.3.04 | C2NC-1500-MBR-M_2.3.04 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.04 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.3.05 | C2NC-1500-MBR-M_2.3.05 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.05 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.3.06 | C2NC-1500-MBR-M_2.3.06 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.06 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.3.07 | C2NC-1500-MBR-M_2.3.07 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.07 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.3.08 | C2NC-1500-MBR-M_2.3.08 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.08 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Compressed gas treatment Temperature transmitter TT340 | C2NC-1500-CGT-TT_340 | C2NC-1500-CGT | Instruments | Compressed gas treatment Temperature transmitter. Function: MEASURE INLET TEMPERATURE BIOGAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4B | 4B | MS-A-TT340 |  | 24 VDC |  |  |  | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [12 empty] | BIOGAS | AISI 316L / ALU | 1/2" NPT |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Membranes Temperature transmitter TT370 | C2NC-1500-MBR-TT_370 | C2NC-1500-MBR | Instruments | Membranes Temperature transmitter. Function: MEASURE INLET AFTER FILTERS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4C | 4C | MS-A-TT370 |  | 24 VDC |  |  |  | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [12 empty] | BIOGAS | AISI 316L / ALU | 1/2" NPT |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Membranes stage 2B Membrane stage 2B, 1st row M2.4.01 | C2NC-1500-MBR-M_2.4.01 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.01 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.4.02 | C2NC-1500-MBR-M_2.4.02 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.02 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.4.03 | C2NC-1500-MBR-M_2.4.03 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.03 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.4.04 | C2NC-1500-MBR-M_2.4.04 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.04 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.4.05 | C2NC-1500-MBR-M_2.4.05 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.05 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.4.06 | C2NC-1500-MBR-M_2.4.06 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.06 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.4.07 | C2NC-1500-MBR-M_2.4.07 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.07 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes stage 2B Membrane stage 2B, 1st row M2.4.08 | C2NC-1500-MBR-M_2.4.08 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.08 | [5 empty] | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row
Membranes Temperature transmitter TT460 | C2NC-1500-MBR-TT_460 | C2NC-1500-MBR | Instruments | Membranes Temperature transmitter. Function: MEASURE TEMPERATURE BEFORE HE460 | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4C | 4C | MS-A-TT460 |  | 24 VDC |  |  |  | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [12 empty] | BIOGAS | AISI 316L / ALU | 1/2" NPT |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Membranes Temperature transmitter TT500 | C2NC-1500-MBR-TT_500 | C2NC-1500-MBR | Instruments | Membranes Temperature transmitter. Function: MEASURE OUTLET TEMPERATURE PRODUCT GAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4C | 4C | MS-A-TT500 |  | 24 VDC |  |  |  | BIOGAS | AISI 316L / ALU | 1/2" NPT, 2,5" |  | Temperature transmitter | [12 empty] | BIOGAS | AISI 316L / ALU | 1/2" NPT, 2,5" |  |  |  | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Container unit Temperature transmitter TT910 | C2NC-1500-CU-TT_910 | C2NC-1500-CU | Instruments | Container unit Temperature transmitter. Function: MEASURE AREA TEMPERATURE | Endress & Hauser | TST434-J1A4DW (inclusive TMT181-I PCP FM+CSA, Class I, Div 1+2 ) RTD Thermometer TST434 | [8 empty] | 9263-4F | 4F | MS-A-TT910 |  | 24 VDC |  |  |  | AMBIENT AIR | Composition of materials |  |  | Temperature transmitter | [12 empty] | AMBIENT AIR | Composition of materials |  |  |  |  | Temperature transmitter |  |  |  |  | AMBIENT AIR | [8 empty] | 24 VDC | AMBIENT AIR |  |  | Temperature transmitter |  | Analog | TT
Compressed gas treatment Ball valve V301 | C2NC-1500-CGT-V_301 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: FILTER DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V301 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V302 | C2NC-1500-CGT-V_302 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V302 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V303 | C2NC-1500-CGT-V_303 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V303 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V304 | C2NC-1500-CGT-V_304 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V304 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V305 | C2NC-1500-CGT-V_305 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V305 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Control valve AV500 | C2NC-1500-MBR-AV_500 | C2NC-1500-MBR | Valves | Membranes Control valve. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | Conovalve | S800 Control valve 2" - ANSI CLASS 300 AV500 | [8 empty] | 9263-4C | 4C | MS-A-AV500 | [5 empty] | BIOGAS | AISI 316L / PTFE | 2" #300 |  | Control valve | [7 empty] | ASME CLASS 300 |  |  |  |  | BIOGAS | AISI 316L / PTFE | 2" #300 |  |  |  | Control valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Control valve |  |  | AV
Membranes Pneumatic actuator AV500 | C2NC-1500-MBR-AV_500 | C2NC-1500-MBR | Valves | Membranes Pneumatic actuator. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | S275/I | [8 empty] | 9263-4C | 4C | MS-A-AV500 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes Control unit/ positioner AV500 | C2NC-1500-MBR-AV_500 | C2NC-1500-MBR | Valves | Membranes Control unit/ positioner. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | V200E-IS (using Non Incendive Field Wiring for use without barrier in Class I Div.2 !! | [8 empty] | 9263-4C | 4C | MS-A-AV500 |  | 24 VDC |  |  |  | COMPRESSED AIR |  |  |  | Control unit/ positioner | [12 empty] | COMPRESSED AIR | [5 empty] | Control unit/ positioner |  |  |  |  | COMPRESSED AIR | [8 empty] | 24 VDC | COMPRESSED AIR |  |  | Control unit/ positioner |  | Analog | AV
Compressed gas treatment Ball valve V307 | C2NC-1500-CGT-V_307 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V307 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V309 | C2NC-1500-CGT-V_309 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V309 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V310 | C2NC-1500-CGT-V_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V310 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V311 | C2NC-1500-CGT-V_311 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: FILTER DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V311 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V312 | C2NC-1500-CGT-V_312 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V312 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V313 | C2NC-1500-CGT-V_313 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V313 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Membrane Separation Control valve AV550 | C2NC-1500-MBR-AV_550 | C2NC-1500-MBR | Valves | Membrane Separation Control valve. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | Conovalve | S800 Control valve 2 1/2" - ANSI CLASS 300 AV550 CV28 | [8 empty] | 9263-4C | 4C | MS-A-AV550 | [5 empty] | BIOGAS | AISI 316L / PTFE | 2.5" #300 |  | Control valve | [7 empty] | ASME CLASS 300 |  |  |  |  | BIOGAS | AISI 316L / PTFE | 2.5" #300 |  |  |  | Control valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Control valve |  |  | AV
Membrane Separation Pneumatic actuator AV550 | C2NC-1500-MBR-AV_550 | C2NC-1500-MBR | Valves | Membrane Separation Pneumatic actuator. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | S275/I | [8 empty] | 9263-4C | 4C | MS-A-AV550 | [5 empty] | COMPRESSED AIR | ALU |  |  | Pneumatic actuator | [12 empty] | COMPRESSED AIR | ALU |  |  |  |  | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [9 empty] | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membrane Separation Control unit/ positioner AV550 | C2NC-1500-MBR-AV_550 | C2NC-1500-MBR | Valves | Membrane Separation Control unit/ positioner. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | V200E-IS (using Non Incendive Field Wiring for use without barrier in Class I Div.2 !! | [8 empty] | 9263-4C | 4C | MS-A-AV550 |  | 24 VDC |  |  |  | COMPRESSED AIR |  |  |  | Control unit/ positioner | [12 empty] | COMPRESSED AIR | [5 empty] | Control unit/ positioner |  |  |  |  | COMPRESSED AIR | [8 empty] | 24 VDC | COMPRESSED AIR |  |  | Control unit/ positioner |  | Analog | AV
Compressed gas treatment Ball valve V320 | C2NC-1500-CGT-V_320 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: Block PT | FLO-TITE | [9 empty] | 9263-4B | 4B | MS-A-V320 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V321 | C2NC-1500-CGT-V_321 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: FILTER DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V321 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V322 | C2NC-1500-CGT-V_322 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V322 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V323 | C2NC-1500-CGT-V_323 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V323 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V331 | C2NC-1500-CGT-V_331 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: FILTER DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V331 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V332 | C2NC-1500-CGT-V_332 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V332 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V333 | C2NC-1500-CGT-V_333 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V333 | [5 empty] | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  |  |  | Ball valve |  |  |  |  | PROCESSS WATER | [9 empty] | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V340 | C2NC-1500-CGT-V_340 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: Block PT | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V340 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V342 | C2NC-1500-CGT-V_342 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V342 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V350 | C2NC-1500-CGT-V_350 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V350 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V360 | C2NC-1500-CGT-V_360 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V360 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Butterfly valve V370 | C2NC-1500-CGT-V_370 | C2NC-1500-CGT | Valves | Compressed gas treatment Butterfly valve. Function: BLOCK COMPRESSED GAS TREATMENT | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4B | 4B | MS-A-V370 | [5 empty] | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 6" #300 |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes Ball valve V371 | C2NC-1500-MBR-V_371 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V371 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes stage 1 Ball valve V400 | C2NC-1500-MBR-V_400 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: ISOLATE PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C1 | 4C1 | MS-A-V400 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V401 | C2NC-1500-MBR-V_401 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V401 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes stage 1 Ball valve V402 | C2NC-1500-MBR-V_402 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C1 | 4C1 | MS-A-V402 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V405 | C2NC-1500-MBR-V_405 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V405 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V408 | C2NC-1500-MBR-V_408 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V408 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Butterfly valve V409 | C2NC-1500-MBR-V_409 | C2NC-1500-MBR | Valves | Membranes Butterfly valve. Function: BLOCK MEMBRANE STAGE 2A | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C | 4C | MS-A-V409 | [5 empty] | BIOGAS | AISI 316 / PTFE | 8" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 8" #300 |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes Ball valve V410 | C2NC-1500-MBR-V_410 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V410 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes stage 2B Ball valve V412 | C2NC-1500-MBR-V_412 | C2NC-1500-MBR | Valves | Membranes stage 2B Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C3 | 4C3 | MS-A-V412 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Cooling skid Chiller CH720 | C2NC-1500-CLG-CH_720 | C2NC-1500-CLG | Equipment | Cooling skid Chiller. Function: COOL DOWN COOLING FLUID | York | YORK Model YLAA0155SE Packaged Scroll Chillers | [8 empty] | 9263-4D | 4D | MS-A-CH720 |  | 480 VAC |  |  |  | GLYCOL MIXTURE |  | 4 " 150# |  | Chiller
Cooling skid Compensator BL720 | C2NC-1500-CLG-BL_720 | C2NC-1500-CLG | Equipment | Cooling skid Compensator. Function: 0 | Mason | Mason Model SFEJ Neoprene Flexible Pipe Connection Isolators | [8 empty] | 9263-4D | 4D | MS-A-BL720 | [5 empty] | GLYCOL MIXTURE |  | 4 " 150# |  | Compensator
Cooling skid Butterfly valve V726 | C2NC-1500-CLG-V_726 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V726 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Temperature transmitter TT720 | C2NC-1500-CLG-TT_720 | C2NC-1500-CLG | Instruments | Cooling skid Temperature transmitter. Function: MEASURE TEMPERATURE IN CIRCUIT | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4D | 4D | MS-A-TT720 |  | 24 VDC |  |  |  | GLYCOL MIXTURE | AISI 316L / ALU | 1/2" NPT, 2,5" |  | Temperature transmitter | [12 empty] | GLYCOL MIXTURE | AISI 316L / ALU | 1/2" NPT, 2,5" |  |  |  | Temperature transmitter |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 24 VDC | GLYCOL MIXTURE |  |  | Temperature transmitter |  | Analog | TT
Cooling skid Ball valve V724 | C2NC-1500-CLG-V_724 | C2NC-1500-CLG | Valves | Cooling skid Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4D | 4D | MS-A-V724 | [5 empty] | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Cooling skid Butterfly valve V730 | C2NC-1500-CLG-V_730 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V730 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Compensator BL731 | C2NC-1500-CLG-BL_731 | C2NC-1500-CLG | Equipment | Cooling skid Compensator. Function: 0 | Mason | Mason Model SFEJ Neoprene Flexible Pipe Connection Isolators | [8 empty] | 9263-4D | 4D | MS-A-BL731 | [5 empty] | GLYCOL MIXTURE |  | 4 " 150# |  | Compensator
Cooling skid Dearation valve DAV730 | C2NC-1500-CLG-DAV_730 | C2NC-1500-CLG | Equipment | Cooling skid Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO | [8 empty] | 9263-4D | 4D | MS-A-DAV730 | [5 empty] | GLYCOL MIXTURE | Brass | 1/2"NPT in, G3/4"out |  | Dearation valve
Cooling skid Chiller CH730 | C2NC-1500-CLG-CH_730 | C2NC-1500-CLG | Equipment | Cooling skid Chiller. Function: COOL DOWN COOLING FLUID | York | YORK Model YLAA0155SE Packaged Scroll Chillers | [8 empty] | 9263-4D | 4D | MS-A-CH730 |  | 480 VAC |  |  |  | GLYCOL MIXTURE |  | 4 " 150# |  | Chiller
Cooling skid Compensator BL730 | C2NC-1500-CLG-BL_730 | C2NC-1500-CLG | Equipment | Cooling skid Compensator. Function: 0 | Mason | Mason Model SFEJ Neoprene Flexible Pipe Connection Isolators | [8 empty] | 9263-4D | 4D | MS-A-BL730 | [5 empty] | GLYCOL MIXTURE |  | 4 " 150# |  | Compensator
Cooling skid Butterfly valve V732 | C2NC-1500-CLG-V_732 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V732 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Butterfly valve V731 | C2NC-1500-CLG-V_731 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V731 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Flow indicator transmitter FIT710 | C2NC-1500-CLG-FIT_710 | C2NC-1500-CLG | Instruments | Cooling skid Flow indicator transmitter. Function: GUARDING CIRCULATION FLOW | Endress & Hauser | Promag W 400, 5W4C80, DN80 3" | [8 empty] | 9263-4D | 4D | MS-A-FIT710 |  | 120 VAC | 0.15 | 0.01 | 0.01 | GLYCOL MIXTURE | Composition of materials | 3" 150# |  | Flow indicator transmitter | [7 empty] | 73-101 psi |  |  |  |  | GLYCOL MIXTURE | Composition of materials | 3" 150# |  |  |  | Flow indicator transmitter |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 120 VAC | GLYCOL MIXTURE |  |  | Flow indicator transmitter |  | Analog | FIT
Cooling skid Pressure transmitter PT710 | C2NC-1500-CLG-PT_710 | C2NC-1500-CLG | Instruments | Cooling skid Pressure transmitter. Function: MEASURE PRESSURE IN CIRCUIT | Endress & Hauser | Cerabar PMP21 | [8 empty] | 9263-4D | 4D | MS-A-PT710 |  | 24 VDC |  |  |  | GLYCOL MIXTURE | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | GLYCOL MIXTURE | 316L / FKM | 1/2" NPT |  |  |  | Pressure transmitter |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 24 VDC | GLYCOL MIXTURE |  |  | Pressure transmitter |  | Analog | PT
Cooling skid Temperature transmitter TT730 | C2NC-1500-CLG-TT_730 | C2NC-1500-CLG | Instruments | Cooling skid Temperature transmitter. Function: MEASURE TEMPERATURE IN CIRCUIT | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4D | 4D | MS-A-TT730 |  | 24 VDC |  |  |  | GLYCOL MIXTURE | AISI 316L / ALU | 1/2" NPT, 2,5" |  | Temperature transmitter | [12 empty] | GLYCOL MIXTURE | AISI 316L / ALU | 1/2" NPT, 2,5" |  |  |  | Temperature transmitter |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 24 VDC | GLYCOL MIXTURE |  |  | Temperature transmitter |  | Analog | TT
Cooling skid Butterfly valve V721 | C2NC-1500-CLG-V_721 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE PUMP | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V721 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Strainer ST720 | C2NC-1500-CLG-ST_720 | C2NC-1500-CLG | Equipment | Cooling skid Strainer. Function: PROTECT PUMP AND CHILLER | Titan | YS 61-SS Strainer, Flanged ends, Raised Face | [8 empty] | 9263-4D | 4D | MS-A-ST720 | [5 empty] | GLYCOL MIXTURE | Composition of materials | 2" 150# |  | Strainer
Cooling skid Pump P720 | C2NC-1500-CLG-P_720 | C2NC-1500-CLG | Equipment | Cooling skid Pump. Function: CIRCULATING OF GLYCOL | Carver | GH ? General Horizontal Series | [8 empty] | 9263-4D | 4D | MS-A-P720 |  | 480 VAC |  |  |  | GLYCOL MIXTURE | AISI 316 | 2.1/2" inlet 2"outlet NPT |  | Pump
Cooling skid Butterfly valve V722 | C2NC-1500-CLG-V_722 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE PUMP | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V722 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Butterfly valve V723 | C2NC-1500-CLG-V_723 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE BUFFER VESSEL | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V723 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Butterfly valve V710 | C2NC-1500-CLG-V_710 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE BUFFER VESSEL | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V710 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Buffer vessel BV710 | C2NC-1500-CLG-BV_710 | C2NC-1500-CLG | Valves | Cooling skid Buffer vessel. Function: STABILIZING TEMPERATURE OF COOLING SYSTEM | DMT | according to drawing DMT | [8 empty] | 9263-4D | 4D | MS-A-BV710 | [5 empty] | GLYCOL MIXTURE | AISI 304 | 4" 150# |  | Buffer vessel | [12 empty] | GLYCOL MIXTURE | AISI 304 | 4" 150# |  |  |  | Buffer vessel |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Buffer vessel |  |  | BV
Cooling skid Pressure safety valve PZV710 | C2NC-1500-CLG-PZV_710 | C2NC-1500-CLG | Valves | Cooling skid Pressure safety valve. Function: 0 | Apollo valves | Cast Bronze Adjustable Relief Valve, MNPT Inlet Type, FNPT Outlet Type | [8 empty] | 9263-4D | 4D | MS-A-PZV710 | [5 empty] | GLYCOL MIXTURE | Cast Bronze | 1/2" MNPT |  | Pressure safety valve | [12 empty] | GLYCOL MIXTURE | Cast Bronze | 1/2" MNPT |  |  |  | Pressure safety valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Pressure safety valve |  |  | PZV
Cooling skid Ball valve V714 | C2NC-1500-CLG-V_714 | C2NC-1500-CLG | Valves | Cooling skid Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4D | 4D | MS-A-V714 | [5 empty] | GLYCOL MIXTURE | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / PTFE | 1" NPT |  |  |  | Ball valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Cooling skid Dearation valve DAV710 | C2NC-1500-CLG-DAV_710 | C2NC-1500-CLG | Equipment | Cooling skid Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO | [8 empty] | 9263-4D | 4D | MS-A-DAV710 | [5 empty] | GLYCOL MIXTURE | Brass | 1/2"NPT in, G3/4"out |  | Dearation valve
Cooling skid Expansion vessel EV710 | C2NC-1500-CLG-EV_710 | C2NC-1500-CLG | Equipment | Cooling skid Expansion vessel. Function: REDUCE PRESSURE FLUCTUATIONS COOLING CIRCUIT | Amtrol | Extrol AX-120V 68 gallons vertical | [8 empty] | 9263-4D | 4D | MS-A-EV710 | [5 empty] | GLYCOL MIXTURE | Carbon steel | 1" FNPT |  | Expansion vessel
Cooling skid Butterfly valve V711 | C2NC-1500-CLG-V_711 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE BUFFER VESSEL | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V711 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Ball valve V713 | C2NC-1500-CLG-V_713 | C2NC-1500-CLG | Valves | Cooling skid Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4D | 4D | MS-A-V713 | [5 empty] | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Cooling skid Pressure indicator PI710 | C2NC-1500-CLG-PI_710 | C2NC-1500-CLG | Instruments | Cooling skid Pressure indicator. Function: INDICATE PRESSURE COOLING CIRCUIT | Ashcroft | 1008S Pressure Gauge D63mm | [8 empty] | 9263-4D | 4D | MS-A-PI710 |  |  |  | NEMA 4 / IP65 |  | GLYCOL MIXTURE | AISI 316 | 1/4"NPT (MALE) |  | Pressure indicator | [7 empty] | 0-60 Psig |  |  |  |  | GLYCOL MIXTURE | AISI 316 | 1/4"NPT (MALE) |  |  |  | Pressure indicator |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Pressure indicator |  |  | PI
Cooling skid Strainer ST710 | C2NC-1500-CLG-ST_710 | C2NC-1500-CLG | Equipment | Cooling skid Strainer. Function: PROTECT PUMP AND CHILLER | Titan | YS 61-SS Strainer, Flanged ends, Raised Face | [8 empty] | 9263-4D | 4D | MS-A-ST710 | [5 empty] | GLYCOL MIXTURE | Composition of materials | 4" 150# |  | Strainer
Cooling skid Butterfly valve V715 | C2NC-1500-CLG-V_715 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE BUFFER VESSEL | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V715 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Pump P710 | C2NC-1500-CLG-P_710 | C2NC-1500-CLG | Equipment | Cooling skid Pump. Function: CIRCULATING OF GLYCOL | Carver | GH ? General Horizontal Series | [8 empty] | 9263-4D | 4D | MS-A-P710 |  | 480 VAC |  |  |  | GLYCOL MIXTURE | AISI 316 | 3" inlet 2,5"outlet - 150# |  | Pump
Cooling skid Dearation valve DAV711 | C2NC-1500-CLG-DAV_711 | C2NC-1500-CLG | Equipment | Cooling skid Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO | [8 empty] | 9263-4D | 4D | MS-A-DAV711 | [5 empty] | GLYCOL MIXTURE | Brass | 1/2"NPT in, G3/4"out |  | Dearation valve
Cooling skid Butterfly valve V712 | C2NC-1500-CLG-V_712 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V712 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Butterfly valve V720 | C2NC-1500-CLG-V_720 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V720 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Compensator BL721 | C2NC-1500-CLG-BL_721 | C2NC-1500-CLG | Equipment | Cooling skid Compensator. Function: 0 | Mason | Mason Model SFEJ Neoprene Flexible Pipe Connection Isolators | [8 empty] | 9263-4D | 4D | MS-A-BL721 | [5 empty] | GLYCOL MIXTURE |  | 4 " 150# |  | Compensator
Gas analyser Gas Quality Analyser Board GQA800 | C2NC-1500-GA-GQA_800 | C2NC-1500-GA | Instruments | Gas analyser Gas Quality Analyser Board. Function: ANALYSE GAS QUALITY | GE sensing | CH4, CO2,O2, H2S Biogas measurement panel | [8 empty] | 9263-4E | 4E | MS-A-GQA800 | [5 empty] | BIOGAS |  |  |  | Gas Quality Analyser Board | [12 empty] | BIOGAS | [5 empty] | Gas Quality Analyser Board |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Gas Quality Analyser Board |  |  | GQA
Gas analyser Three-way valve AV800 | C2NC-1500-GA-AV_800 | C2NC-1500-GA | Valves | Gas analyser Three-way valve. Function: Switch Routing on Analyser Board | GE sensing | ?? | [8 empty] | 9263-4E | 4E | MS-A-AV800 |  | 120 VAC |  |  |  | BIOGAS |  |  |  | Three-way valve | [12 empty] | BIOGAS | [5 empty] | Three-way valve |  |  |  |  | BIOGAS | [8 empty] | 120 VAC | BIOGAS |  |  | Three-way valve |  | Digital | AV
Gas analyser Gas quality analyser QT841 | C2NC-1500-GA-QT_841 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : CH4 : 0-10% | GE sensing | [9 empty] | 9263-4E | 4E | MS-A-QT841 |  | 24 VDC | [7 empty] | Gas quality analyser | [18 empty] | Gas quality analyser | [13 empty] | 24 VDC |  |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Gas quality analyser QT814 | C2NC-1500-GA-QT_814 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : H2S : 0-300ppm | GE sensing | [9 empty] | 9263-4E | 4E | MS-A-QT814 |  | 24 VDC | [7 empty] | Gas quality analyser | [18 empty] | Gas quality analyser | [13 empty] | 24 VDC |  |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Pump P810 | C2NC-1500-GA-P_810 | C2NC-1500-GA | Equipment | Gas analyser Pump. Function: 0 | GE sensing | [9 empty] | 9263-4E | 4E | MS-A-P810 |  | 115 VAC | [7 empty] | Pump
Gas analyser Gas quality analyser QT823 | C2NC-1500-GA-QT_823 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : O2 : 0-2% | GE sensing | [9 empty] | 9263-4E | 4E | MS-A-QT823 |  | 24 VDC | [7 empty] | Gas quality analyser | [18 empty] | Gas quality analyser | [13 empty] | 24 VDC |  |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Gas quality analyser QT824 | C2NC-1500-GA-QT_824 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : H2S : 0-50ppm | GE sensing | [9 empty] | 9263-4E | 4E | MS-A-QT824 |  | 24 VDC | [7 empty] | Gas quality analyser | [18 empty] | Gas quality analyser | [13 empty] | 24 VDC |  |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Gas quality analyser QT831 | C2NC-1500-GA-QT_831 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : CH4 : 90-100% | GE sensing | [9 empty] | 9263-4E | 4E | MS-A-QT831 |  | 24 VDC | [7 empty] | Gas quality analyser | [18 empty] | Gas quality analyser | [13 empty] | 24 VDC |  |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Gas quality analyser QT832 | C2NC-1500-GA-QT_832 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : CO2 : 0-10% | GE sensing | [9 empty] | 9263-4E | 4E | MS-A-QT832 |  | 24 VDC | [7 empty] | Gas quality analyser | [18 empty] | Gas quality analyser | [13 empty] | 24 VDC |  |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Gas quality analyser QT833 | C2NC-1500-GA-QT_833 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : O2 : 0-2% | GE sensing | [9 empty] | 9263-4E | 4E | MS-A-QT833 |  | 24 VDC | [7 empty] | Gas quality analyser | [18 empty] | Gas quality analyser | [13 empty] | 24 VDC |  |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Pump P820 | C2NC-1500-GA-P_820 | C2NC-1500-GA | Equipment | Gas analyser Pump. Function: 0 | GE sensing | [9 empty] | 9263-4E | 4E | MS-A-P820 |  | 115 VAC | [7 empty] | Pump
Membranes stage 2B Ball valve V413 | C2NC-1500-MBR-V_413 | C2NC-1500-MBR | Valves | Membranes stage 2B Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C3 | 4C3 | MS-A-V413 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes stage 1 Butterfly valve V420 | C2NC-1500-MBR-V_420 | C2NC-1500-MBR | Valves | Membranes stage 1 Butterfly valve. Function: BLOCK IN MEMBRANES | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C1 | 4C1 | MS-A-V420 | [5 empty] | BIOGAS | AISI 316 / PTFE | 8" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 8" #300 |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes stage 1 Butterfly valve V421 | C2NC-1500-MBR-V_421 | C2NC-1500-MBR | Valves | Membranes stage 1 Butterfly valve. Function: BLOCK IN MEMBRANES | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C1 | 4C1 | MS-A-V421 | [5 empty] | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 6" #300 |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes stage 2B Butterfly valve V430 | C2NC-1500-MBR-V_430 | C2NC-1500-MBR | Valves | Membranes stage 2B Butterfly valve. Function: BLOCK OUTLET MEMBRANE SYSTEM | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C3 | 4C3 | MS-A-V430 | [5 empty] | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 6" #300 |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes stage 2B Butterfly valve V431 | C2NC-1500-MBR-V_431 | C2NC-1500-MBR | Valves | Membranes stage 2B Butterfly valve. Function: BLOCK OUTLET MEMBRANE SYSTEM | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C3 | 4C3 | MS-A-V431 | [5 empty] | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 6" #300 |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes Ball valve V500 | C2NC-1500-MBR-V_500 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V500 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V501 | C2NC-1500-MBR-V_501 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: ISOLATE SAMPLE LINE | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V501 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V510 | C2NC-1500-MBR-V_510 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V510 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V511 | C2NC-1500-MBR-V_511 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V511 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Butterfly valve V512 | C2NC-1500-MBR-V_512 | C2NC-1500-MBR | Valves | Membranes Butterfly valve. Function: BLOCK START-UP LINE | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C | 4C | MS-A-V512 | [5 empty] | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 6" #300 |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes Butterfly valve V513 | C2NC-1500-MBR-V_513 | C2NC-1500-MBR | Valves | Membranes Butterfly valve. Function: BLOCK OUTLET MEMBRANE SYSTEM | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C | 4C | MS-A-V513 | [5 empty] | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 6" #300 |  |  |  | Butterfly valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes Ball valve V521 | C2NC-1500-MBR-V_521 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: ISOLATE SAMPLE LINE | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V521 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V522 | C2NC-1500-MBR-V_522 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V522 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V550 | C2NC-1500-MBR-V_550 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V550 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V631 | C2NC-1500-MBR-V_631 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V631 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V632 | C2NC-1500-MBR-V_632 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: ISOLATE SAMPLE LINE | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V632 | [5 empty] | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | BIOGAS | [9 empty] | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Butterfly valve V740 | C2NC-1500-CGT-V_740 | C2NC-1500-CGT | Valves | Compressed gas treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Apollo valves | 215 | [8 empty] | 9263-4B | 4B | MS-A-V740 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Compressed gas treatment Butterfly valve V741 | C2NC-1500-CGT-V_741 | C2NC-1500-CGT | Valves | Compressed gas treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Apollo valves | 215 | [8 empty] | 9263-4B | 4B | MS-A-V741 | [5 empty] | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  |  |  | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [9 empty] | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Container unit Ball valve V910 | C2NC-1500-CU-V_910 | C2NC-1500-CU | Valves | Container unit Ball valve. Function: ISOLATE INSTRUMENT AIRLINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4F | 4F | MS-A-V910 | [5 empty] | INSTRUMENT AIR | AISI 316 / PTFE | 1" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | INSTRUMENT AIR | AISI 316 / PTFE | 1" SW |  |  |  | Ball valve |  |  |  |  | INSTRUMENT AIR | [9 empty] | INSTRUMENT AIR |  |  | Ball valve |  |  | V
Container unit Ball valve V911 | C2NC-1500-CU-V_911 | C2NC-1500-CU | Valves | Container unit Ball valve. Function: SAMPLE/DRAIN/CLEANING | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4F | 4F | MS-A-V911 | [5 empty] | INSTRUMENT AIR | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | INSTRUMENT AIR | AISI 316 / PTFE | 1/2" NPT |  |  |  | Ball valve |  |  |  |  | INSTRUMENT AIR | [9 empty] | INSTRUMENT AIR |  |  | Ball valve |  |  | V
Container unit Manual valve V914 | C2NC-1500-CU-V_914 | C2NC-1500-CU | Valves | Container unit Manual valve. Function: block air flow | Greenhack | Part of GR914 | [8 empty] | 9263-4F | 4F | MS-A-V914 | [5 empty] | Ambient air | Aluminium | 24x24" |  | Manual valve | [12 empty] | Ambient air | Aluminium | 24x24" |  |  |  | Manual valve |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Manual valve |  |  | V
Container unit Manual valve V915 | C2NC-1500-CU-V_915 | C2NC-1500-CU | Valves | Container unit Manual valve. Function: block air flow | Greenhack | Part of GR914 | [8 empty] | 9263-4F | 4F | MS-A-V915 | [5 empty] | Ambient air | Aluminium | 24x24" |  | Manual valve | [12 empty] | Ambient air | Aluminium | 24x24" |  |  |  | Manual valve |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Manual valve |  |  | V
Control area container Heater HE900 | C2NC-1500-CU-HE_900 | C2NC-1500-CU | Equipment | Control area container Heater. Function: Heating | TPI Corporation | Hazardous-Location Electric Heater, 3.6 kW, 480V AC, 3-phase, Convection Heating Method | [8 empty] | 9263-4F | 4F | MS-A-HE900 |  | 480 VAC |  |  |  | Ambient air | Steel | 40x18x9" |  | Heater
Control area container Grid GR900 | C2NC-1500-CU-GR_900 | C2NC-1500-CU | Equipment | Control area container Grid. Function: Air inlet | Systemair | PZAL-500x500-S | [8 empty] | 9263-4F | 4F | MS-A-GR900 | [5 empty] | Ambient air | Aluminium | 500x500 mm |  | Grid
Control area container Fan FA900 | C2NC-1500-CU-FA_900 | C2NC-1500-CU | Equipment | Control area container Fan. Function: Refresh air inside container | J&D Manufacturing | VES201C | [8 empty] | 9263-4F | 4F | MS-A-FA900 |  | 120 VAC |  |  |  | Ambient air | Aluminium | 500x500 mm |  | Fan
Control area container Manual valve V900 | C2NC-1500-CU-V_900 | C2NC-1500-CU | Valves | Control area container Manual valve. Function: Block air flow | Systemair | RK-500x500-R | [8 empty] | 9263-4F | 4F | MS-A-V900 | [5 empty] | Ambient air | Aluminium | 500x500 mm |  | Manual valve | [12 empty] | Ambient air | Aluminium | 500x500 mm |  |  |  | Manual valve |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Manual valve |  |  | V
Control area container Emergency stop ES900 | C2NC-1500-CU-ES_900 | C2NC-1500-CU | Instruments | Control area container Emergency stop. Function: STOP INSTALLATION | Schneider | 9001SK | [8 empty] | 9263-4F | 4F | MS-A-ES900 |  | 24 VDC |  |  |  |  | - |  |  | Emergency stop | [13 empty] | - |  |  |  |  | Emergency stop | [13 empty] | 24 VDC |  |  |  | Emergency stop |  |  | ES
Control area container Manual valve V901 | C2NC-1500-CU-V_901 | C2NC-1500-CU | Valves | Control area container Manual valve. Function: Block air flow | Systemair | RK-400x400-R | [8 empty] | 9263-4F | 4F | MS-A-V901 | [5 empty] | Ambient air | Aluminium | 400x400 mm |  | Manual valve | [12 empty] | Ambient air | Aluminium | 400x400 mm |  |  |  | Manual valve |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Manual valve |  |  | V
Control area container Grid GR901 | C2NC-1500-CU-GR_901 | C2NC-1500-CU | Equipment | Control area container Grid. Function: Air outlet | Systemair | PZAL-400x400-S | [8 empty] | 9263-4F | 4F | MS-A-GR901 | [5 empty] | Ambient air | Aluminium | 400x400 mm |  | Grid
Control area container Temperature transmitter TT900 | C2NC-1500-CU-TT_900 | C2NC-1500-CU | Instruments | Control area container Temperature transmitter. Function: MEASURE TEMPERATURE CONTROL ROOM | Endress & Hauser | TST434-J1A4DW (inclusive TMT181-I PCP FM+CSA, Class I, Div 1+2 ) RTD Thermometer TST434 | [8 empty] | 9263-4F | 4F | MS-A-TT900 |  | 24 VDC |  |  |  | Ambient air | Composition of materials |  |  | Temperature transmitter | [12 empty] | Ambient air | Composition of materials |  |  |  |  | Temperature transmitter |  |  |  |  | Ambient air | [8 empty] | 24 VDC | Ambient air |  |  | Temperature transmitter |  | Analog | TT
Control area container Temperature transmitter TT901 | C2NC-1500-CU-TT_901 | C2NC-1500-CU | Instruments | Control area container Temperature transmitter. Function: MEASURE TEMPERATURE OF AMBIENT | Endress & Hauser | TST434-J1A4DW (inclusive TMT181-I PCP FM+CSA, Class I, Div 1+2 ) RTD Thermometer TST434 | [8 empty] | 9263-4F | 4F | MS-A-TT901 |  | 24 VDC |  |  |  | Ambient air | Composition of materials |  |  | Temperature transmitter | [12 empty] | Ambient air | Composition of materials |  |  |  |  | Temperature transmitter |  |  |  |  | Ambient air | [8 empty] | 24 VDC | Ambient air |  |  | Temperature transmitter |  | Analog | TT
Sales gas compressor Sales gas compressor GC570 | C2NC-1500-GC-GC_570 | C2NC-1500-GC | Equipment | Sales gas compressor Sales gas compressor. Function: PRESSURIZE GAS | Safe | SW373B10,5-EM | [8 empty] | 9263-5A | 5A | MS-A-GC570 | [5 empty] | Gas | Composition of materials | 6" 150# in / 2" 600# out |  | Sales gas compressor
Sales gas compressor Dry cooler fan FA570 | C2NC-1500-GC-FA_570 | C2NC-1500-GC | Equipment | Sales gas compressor Dry cooler fan. Function: PRESSURIZE GAS | Thermokey | V shaped 8 fan air cooler 22F0013086 | [8 empty] | 9263-5A | 5A | MS-A-FA570 | [5 empty] | Gas | Composition of materials | 3" 150# |  | Dry cooler fan

## 1500 - Ref (Del After Upload)
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual RQD | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | horsepower | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Connection Type | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | *Any Custom Fields* | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes
GAS PLANT | C2NC-1500 | C2NC | Locations and Facilities | GAS PLANT
GAS PLANT PRE-TREATMENT | C2NC-1500-PRE | C2NC-1500 | Locations and Facilities | GAS PLANT PRE-TREATMENT
GAS PLANT ACTIVE CARBON VESSELS | C2NC-1500-ACV | C2NC-1500 | Locations and Facilities | GAS PLANT ACTIVE CARBON VESSELS
GAS PLANT MEMBRANES | C2NC-1500-MBR | C2NC-1500 | Locations and Facilities | GAS PLANT MEMBRANES
GAS PLANT COMPRESSORS | C2NC-1500-CMP | C2NC-1500 | Locations and Facilities | GAS PLANT COMPRESSORS
GAS PLANT COOLING | C2NC-1500-CLG | C2NC-1500 | Locations and Facilities | GAS PLANT COOLING
Caustic scrubber Butterfly valve V100 | C2NC-1500-CS-V_100 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Blow flow at gas inlet | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263 | 2A | BR-A-V100 |  |  | NA | NA | NA | Raw biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Raw biogas | [5 empty] | Butterfly valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Butterfly valve |  |  | V | V | Valves
Caustic scrubber Ball valve V101 | C2NC-1500-CS-V_101 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V101 |  |  | NA | NA | NA | Raw biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Raw biogas | [5 empty] | Ball valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Ball valve |  |  | V | DV | Valves
Caustic scrubber Ball valve V102 | C2NC-1500-CS-V_102 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V102 |  |  | NA | NA | NA | Raw biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Raw biogas | [5 empty] | Ball valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Ball valve |  |  | V | BV | Valves
Circulation pumps Butterfly valve AV315 | C2NC-1500-CIRC-AV_315 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block flow to discharge | Apollo | 215L-04SSP8TA0 150# 316SS Lug Butterfly Valve with Spring return Rack & Pinion Actuator Fail Close | [8 empty] | 9263 | 2B | BR-A-AV315 |  |  | NA | NA | NA | Cooling water (50% propylene glycol) | AISI 316 / RTFM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Cooling water (50% propylene glycol) | [5 empty] | Butterfly valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Butterfly valve |  |  | AV | AV | Valves
Caustic scrubber Ball valve V103 | C2NC-1500-CS-V_103 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Block pressure transmitter | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V103 |  |  | NA | NA | NA | Raw biogas | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Raw biogas | [5 empty] | Ball valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Ball valve |  |  | V | PCV | Valves
Circulation pumps Pneumatic actuator AV315 | C2NC-1500-CIRC-AV_315 | C2NC-1500-CIRC | Valves | Circulation pumps Pneumatic actuator. Function: Deliver instrument air | Air Con | Included AV315 | [8 empty] | 9263 | 2B | BR-A-AV315 |  |  | NA | NA | NA | NA | Composition of materials | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Pneumatic actuator |  |  |  |  | NA | [9 empty] | NA |  |  | Pneumatic actuator |  |  | AV | OPS | Valves
Circulation pumps Solenoid valve AV315 | C2NC-1500-CIRC-AV_315 | C2NC-1500-CIRC | Valves | Circulation pumps Solenoid valve. Function: Switch instrument air to BR-A-AV315 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2B | BR-A-AV315 |  | 24 VDC | < 0,5 | NA | NA | Instrument Air | Composition of materials | NA |  | Solenoid valve | [7 empty] | NA |  |  |  | 24 VDC | Instrument Air | [5 empty] | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | UPSO | Valves
Caustic scrubber Ball valve V105 | C2NC-1500-CS-V_105 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V105 |  |  | NA | NA | NA | Raw biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Raw biogas | [5 empty] | Ball valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Ball valve |  |  | V | OPSO | Valves
Caustic scrubber Biogas Feed Pipe BFP200 | C2NC-1500-CS-BFP_200 | C2NC-1500-CS | Lines | Caustic scrubber Biogas Feed Pipe. Function: 0 | 0 | design by MTE | [8 empty] | 9263 | 2A | BR-A-BFP200 |  |  | 0 | 0 | 0 | 0 | FRP | 0 |  | Biogas Feed Pipe | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Biogas Feed Pipe |  |  |  |  | 0 | [9 empty] | 0 |  |  | Biogas Feed Pipe |  |  | BFP | SV | Valves
Caustic scrubber Scrubber S200 | C2NC-1500-CS-S_200 | C2NC-1500-CS | Equipment | Caustic scrubber Scrubber. Function: Removal of H2S | Midwestern Fabricators | According drawing DMT | [8 empty] | 9263 | 2A | BR-A-S200 |  |  | NA | NA | NA | Raw biogas | FRP | Ø2743mm h=13200mm |  | Scrubber | [7 empty] | 0 |  |  |  |  | Raw biogas | [5 empty] | Scrubber |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Scrubber |  |  | S | CVO | Valves
Caustic scrubber Spraying Nozzle SN200 | C2NC-1500-CS-SN_200 | C2NC-1500-CS | Equipment | Caustic scrubber Spraying Nozzle. Function: Foam removal | Bete | TFXP Full cone spiral spray nozzle TF40 | [8 empty] | 9263 | 2A | BR-A-SN200 |  |  | NA | NA | NA | Process water | AISI 316 | 1" NPT |  | Spraying Nozzle | [7 empty] | 0.5-0.7 bar |  |  |  |  | Process water | [5 empty] | Spraying Nozzle |  |  |  |  | Process water | [9 empty] | Process water |  |  | Spraying Nozzle |  |  | SN | CV | Valves
Caustic scrubber Spray nozzle feed pipe SFP200 | C2NC-1500-CS-SFP_200 | C2NC-1500-CS | Lines | Caustic scrubber Spray nozzle feed pipe. Function: mounting of spray nozzle | DMT | according 9263-8019 | [8 empty] | 9263 | 2A | BR-A-SFP200 |  |  | 0 | 0 | 0 | Process water | AISI 316 | 1" NPT / 2" |  | Spray nozzle feed pipe | [7 empty] | 0 |  |  |  |  | Process water | [5 empty] | Spray nozzle feed pipe |  |  |  |  | Process water | [9 empty] | Process water |  |  | Spray nozzle feed pipe |  |  | SFP | PZV | Valves
Caustic scrubber Support plate SP200 | C2NC-1500-CS-SP_200 | C2NC-1500-CS | Equipment | Caustic scrubber Support plate. Function: support packing | MTE | MSP43 support plate | [8 empty] | 9263 | 2A | BR-A-SP200 |  |  | 0 | 0 | 0 | Raw biogas | PP | Ø = 2700mm |  | Support plate | [7 empty] | 0 |  |  |  |  | Raw biogas | [5 empty] | Support plate |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Support plate |  |  | SP | TI | Instruments
Caustic scrubber Packing material PM200 | C2NC-1500-CS-PM_200 | C2NC-1500-CS | Equipment | Caustic scrubber Packing material. Function: Increase contact area | RVT | 1,5" (38mm) Raflux Ring 38-8 Tower Packing | [8 empty] | 9263 | 2A | BR-A-PM200 |  |  | NA | NA | NA | Raw biogas | PP | Ø = 2700mm |  | Packing material | [7 empty] | 0 |  |  |  |  | Raw biogas | [5 empty] | Packing material |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Packing material |  |  | PM | PI | Instruments
Caustic scrubber Packing grid PG200 | C2NC-1500-CS-PG_200 | C2NC-1500-CS | Equipment | Caustic scrubber Packing grid. Function: 0 | MTE | 0 | [8 empty] | 9263 | 2A | BR-A-PG200 |  |  | 0 | 0 | 0 | 0 | PP | 0 |  | Packing grid | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Packing grid |  |  |  |  | 0 | [9 empty] | 0 |  |  | Packing grid |  |  | PG | FI | Instruments
Caustic scrubber Liquid distributor LD200 | C2NC-1500-CS-LD_200 | C2NC-1500-CS | Equipment | Caustic scrubber Liquid distributor. Function: Water distribution | MTE | Trough type liquid distributor, type MLD 131 | [8 empty] | 9263 | 2A | BR-A-LD200 |  |  | NA | NA | NA | Raw biogas | PP | Ø = 2700mm |  | Liquid distributor | [7 empty] | 0 |  |  |  |  | Raw biogas | [5 empty] | Liquid distributor |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Liquid distributor |  |  | LD | LI | Instruments
Caustic scrubber Liquid feed pipe LFP200 | C2NC-1500-CS-LFP_200 | C2NC-1500-CS | Lines | Caustic scrubber Liquid feed pipe. Function: 0 | MTE | 0 | [8 empty] | 9263 | 2A | BR-A-LFP200 |  |  | 0 | 0 | 0 | 0 | PP | 0 |  | Liquid feed pipe | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Liquid feed pipe |  |  |  |  | 0 | [9 empty] | 0 |  |  | Liquid feed pipe |  |  | LFP | LS | Instruments
Caustic scrubber Demister DM200 | C2NC-1500-CS-DM_200 | C2NC-1500-CS | Equipment | Caustic scrubber Demister. Function: Gas liquid separation | MTE | Vane type demister | [8 empty] | 9263 | 2A | BR-A-DM200 |  |  | NA | NA | NA | Raw biogas | PP | Ø700*150 mm |  | Demister | [7 empty] | 0 |  |  |  |  | Raw biogas | [5 empty] | Demister |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Demister |  |  | DM | PS | Instruments
Caustic scrubber Pressure safety valve PZV200 | C2NC-1500-CS-PZV_200 | C2NC-1500-CS | Valves | Caustic scrubber Pressure safety valve. Function: Guard column against high pressure scenarios | Rampini | High pressure relief valve dwg. 9 A | [8 empty] | 9263 | 2A | BR-A-PZV200 |  |  | NA | NA | NA | Clean biogas | AISI316L / PTFE | 10" 150# |  | Pressure safety valve | [7 empty] | 0 |  |  |  |  | Clean biogas | [5 empty] | Pressure safety valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Pressure safety valve |  |  | PZV | FS | Instruments
Caustic scrubber Ball valve V107 | C2NC-1500-CS-V_107 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V107 |  |  | NA | NA | NA | Clean biogas | AISI 316 / PTFE | 2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | [5 empty] | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | FIS | Instruments
Caustic scrubber Ball valve V108 | C2NC-1500-CS-V_108 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Block pressure transmitter | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V108 |  |  | NA | NA | NA | Clean biogas | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | [5 empty] | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | TT | Instruments
Circulation pumps Butterfly valve AV316 | C2NC-1500-CIRC-AV_316 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Bypass heat exchanger | Apollo | 215L-04SSP8TA0 150# 316SS Lug Butterfly Valve with Spring return Rack & Pinion Actuator Fail Open | [8 empty] | 9263 | 2B | BR-A-AV316 |  |  | NA | NA | NA | Cooling water (50% propylene glycol) | AISI 316 / RTFM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Cooling water (50% propylene glycol) | [5 empty] | Butterfly valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Butterfly valve |  |  | AV | TIT | Instruments
Circulation pumps Pneumatic actuator AV316 | C2NC-1500-CIRC-AV_316 | C2NC-1500-CIRC | Valves | Circulation pumps Pneumatic actuator. Function: Deliver instrument air | Air Con | Included AV316 | [8 empty] | 9263 | 2B | BR-A-AV316 |  |  | NA | NA | NA | NA | Composition of materials | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Pneumatic actuator |  |  |  |  | NA | [9 empty] | NA |  |  | Pneumatic actuator |  |  | AV | PT | Instruments
Caustic scrubber Butterfly valve V106 | C2NC-1500-CS-V_106 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Block flow scrubber bypass | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263 | 2A | BR-A-V106 |  |  | NA | NA | NA | Clean biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Clean biogas | [5 empty] | Butterfly valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Butterfly valve |  |  | V | PIT | Instruments
Caustic scrubber Ball valve V110 | C2NC-1500-CS-V_110 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V110 |  |  | NA | NA | NA | Clean biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | [5 empty] | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | FT | Instruments
Circulation pumps Solenoid valve AV316 | C2NC-1500-CIRC-AV_316 | C2NC-1500-CIRC | Valves | Circulation pumps Solenoid valve. Function: Switch instrument air to BR-A-AV316 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2B | BR-A-AV316 |  | 24 VDC | < 0,5 | NA | NA | Instrument Air | Composition of materials | NA |  | Solenoid valve | [7 empty] | NA |  |  |  | 24 VDC | Instrument Air | [5 empty] | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | FIT | Instruments
Caustic scrubber Ball valve V111 | C2NC-1500-CS-V_111 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V111 |  |  | NA | NA | NA | Clean biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | [5 empty] | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | QT | Instruments
Caustic scrubber Ball valve V112 | C2NC-1500-CS-V_112 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V112 |  |  | NA | NA | NA | Clean biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | [5 empty] | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | LT | Instruments
Caustic scrubber Butterfly valve V113 | C2NC-1500-CS-V_113 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Block flow after scrubber | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263 | 2A | BR-A-V113 |  |  | NA | NA | NA | Clean biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Clean biogas | [5 empty] | Butterfly valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Butterfly valve |  |  | V | LEL | Instruments
Caustic scrubber Spectacle flange SF100 | C2NC-1500-CS-SF_100 | C2NC-1500-CS | Equipment | Caustic scrubber Spectacle flange. Function: Block gas flow | Eriks | Spectacle flanges AISI 316 ANSI P265-GH 150 16" 25 | [8 empty] | 9263 | 2A | BR-A-SF100 |  |  | NA | NA | NA | Clean biogas | AISI 316 | 16" 150# |  | Spectacle flange | [7 empty] | 10.3 Barg - 150 Psig |  |  |  |  | Clean biogas | [5 empty] | Spectacle flange |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Spectacle flange |  |  | SF | DC | Instruments
Caustic scrubber Ball valve V114 | C2NC-1500-CS-V_114 | C2NC-1500-CS | Valves | Caustic scrubber Ball valve. Function: Sample/Drain | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2A | BR-A-V114 |  |  | NA | NA | NA | Clean biogas | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Clean biogas | [5 empty] | Ball valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Ball valve |  |  | V | FIR | Instruments
Caustic scrubber Butterfly valve V115 | C2NC-1500-CS-V_115 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Block flow to flare | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263 | 2A | BR-A-V115 |  |  | NA | NA | NA | Clean biogas | AISI316 / NBR | 16" Multi drill PN10/16, ASME 125/150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Clean biogas | [5 empty] | Butterfly valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Butterfly valve |  |  | V | QITA | Instruments
Circulation pumps Ball valve AV330 | C2NC-1500-CIRC-AV_330 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block flow to discharge | Flotite | 1" 320-SS-2-FFF-025-CDA52-PERP Fail Close | [8 empty] | 9263 | 2B | BR-A-AV330 |  |  | NA | NA | NA | Process water | AISI 316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | AV | FT | Instruments
Circulation pumps Pneumatic actuator AV330 | C2NC-1500-CIRC-AV_330 | C2NC-1500-CIRC | Valves | Circulation pumps Pneumatic actuator. Function: Deliver instrument air to AV330 | Air Con | Included AV330 | [8 empty] | 9263 | 2B | BR-A-AV330 |  |  | NA | NA | NA | NA | Composition of materials | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Pneumatic actuator |  |  |  |  | NA | [9 empty] | NA |  |  | Pneumatic actuator |  |  | AV | FIT | Instruments
Circulation pumps Solenoid valve AV330 | C2NC-1500-CIRC-AV_330 | C2NC-1500-CIRC | Valves | Circulation pumps Solenoid valve. Function: Switch instrument air to BR-A-AV330 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2B | BR-A-AV330 |  | 24 VDC | < 0,5 | NA | NA | Instrument Air | Composition of materials | NA |  | Solenoid valve | [7 empty] | NA |  |  |  | 24 VDC | Instrument Air | [5 empty] | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | SL | Instruments
Measurement loop and GQA Ball valve AV360 | C2NC-1500-MEAS-AV_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Ball valve. Function: Block flow to analysis | Flotite | 1" 320-SS-2-FFF-025-CDA52-PERP Fail Close | [8 empty] | 9263 | 2G | BR-A-AV360 |  |  | NA | NA | NA | Process water | AISI 316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | AV | ES | Instruments
Measurement loop and GQA Pneumatic actuator AV360 | C2NC-1500-MEAS-AV_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Pneumatic actuator. Function: Deliver instrument air to AV360 | Air Con | Included AV360 | [8 empty] | 9263 | 2G | BR-A-AV360 |  |  | NA | NA | NA | - | Composition of materials | - |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | - | [5 empty] | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | SI | Instruments
Measurement loop and GQA Solenoid valve AV360 | C2NC-1500-MEAS-AV_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Solenoid valve. Function: Switch instrument air to BR-A-AV360 | Asco | Included AV360 | [8 empty] | 9263 | 2G | BR-A-AV360 |  | 24 VDC | < 0,5 | NA | NA | Instrument Air | Composition of materials | NA |  | Solenoid valve | [7 empty] | NA |  |  |  | 24 VDC | Instrument Air | [5 empty] | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | P | Equipment
Circulation pumps Check valve CV721 | C2NC-1500-CIRC-CV_721 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow | Georg Fischer | Type 562 | [8 empty] | 9263 | 2B | BR-A-CV721 |  |  | NA | NA | NA | Nutrients | PP/ EPDM | 1/2" |  | Check valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Nutrients | [5 empty] | Check valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Check valve |  |  | CV | GC | Equipment
Circulation pumps Check valve CV731 | C2NC-1500-CIRC-CV_731 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow | Georg Fischer | Type 562 | [8 empty] | 9263 | 2B | BR-A-CV731 |  |  | NA | NA | NA | Antifoam | PP/ EPDM | 1/2" |  | Check valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Antifoam | [5 empty] | Check valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Check valve |  |  | CV | FB | Equipment
Circulation pumps Check valve CV701 | C2NC-1500-CIRC-CV_701 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Keep pressure in supply line | Georg Fischer | Type 562 | [8 empty] | 9263 | 2B | BR-A-CV701 |  |  | NA | NA | NA | Caustic | PP/ EPDM | 1/2" |  | Check valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Caustic | [5 empty] | Check valve |  |  |  |  | Caustic | [9 empty] | Caustic |  |  | Check valve |  |  | CV | VB | Equipment
Circulation pumps Ball valve V701 | C2NC-1500-CIRC-V_701 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block caustic flow | Georg Fischer | Type 546 | [8 empty] | 9263 | 2B | BR-A-V701 |  |  | NA | NA | NA | Caustic | PP/ EPDM | 1/2" |  | Ball valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Caustic | [5 empty] | Ball valve |  |  |  |  | Caustic | [9 empty] | Caustic |  |  | Ball valve |  |  | V | M | Equipment
Circulation pumps Ball valve V726 | C2NC-1500-CIRC-V_726 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block li ne | Georg Fischer | Type 546 | [8 empty] | 9263 | 2B | BR-A-V726 |  |  | NA | NA | NA | Nutrients | PP/ EPDM | 1/2" |  | Ball valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Nutrients | [5 empty] | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V | S | Equipment
Circulation pumps Ball valve V736 | C2NC-1500-CIRC-V_736 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block li ne | Georg Fischer | Type 546 | [8 empty] | 9263 | 2B | BR-A-V736 |  |  | NA | NA | NA | Antifoam | PP/ EPDM | 1/2" |  | Ball valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Antifoam | [5 empty] | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V | FB | Equipment
Measurement loop and GQA Ball valve AV361 | C2NC-1500-MEAS-AV_361 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Ball valve. Function: Open/close rinsing water to sensors | Flotite | 1" 320-SS-2-FFF-025-CDA52-PERP Fail Close | [8 empty] | 9263 | 2G | BR-A-AV361 |  |  | NA | NA | NA | Process water | AISI 316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | AV | MX.X.XX | Equipment
Measurement loop and GQA Pneumatic actuator AV361 | C2NC-1500-MEAS-AV_361 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Pneumatic actuator. Function: Deliver instrument air to AV361 | Air Con | Included AV361 | [8 empty] | 9263 | 2G | BR-A-AV361 |  |  | NA | NA | NA | - | Composition of materials | - |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | - | [5 empty] | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | HE | Equipment
Circulation pumps Pump P301 | C2NC-1500-CIRC-P_301 | C2NC-1500-CIRC | Equipment | Circulation pumps Pump. Function: Circulation Pump | Verder | MCP3 centrifugal pump | [8 empty] | 9263 | 2B | BR-A-P301 |  |  | NA | NA | NA | Process water | composition | 6" inlet / 5" outlet |  | Pump | [7 empty] | 0 |  |  |  |  | Process water | [5 empty] | Pump |  |  |  |  | Process water | [9 empty] | Process water |  |  | Pump |  |  | P | AC | Equipment
Circulation pumps Motor P301_M | C2NC-1500-CIRC-P_301_M | C2NC-1500-CIRC | Equipment | Circulation pumps Motor. Function: Drive P301 | Verder | MCP3 centrifugal pump | [8 empty] | 9263 | 2B | BR-A-P301_M |  | 48 VAC | 31,1 | 0 | 29,5 | - | composition | - |  | Motor | [7 empty] | 0 |  |  |  | 48 VAC | - | [5 empty] | Motor |  |  |  |  | - | [8 empty] | 48 VAC | - |  |  | Motor |  | Analog | P | HVAC | Equipment
Measurement loop and GQA Solenoid valve AV361 | C2NC-1500-MEAS-AV_361 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Solenoid valve. Function: Switch instrument air to BR-A-AV361 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2G | BR-A-AV361 |  | 24 VDC | < 0,5 | NA | NA | Instrument Air | Composition of materials | NA |  | Solenoid valve | [7 empty] | NA |  |  |  | 24 VDC | Instrument Air | [5 empty] | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | HE | Equipment
Settler and sludge pump Butterfly valve AV451 | C2NC-1500-SLG-AV_451 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Open/close sulphur sludge recycling | Apollo | 2 Apollo 215L-02SSP8TA0 150# 316SS Lug Butterfly Valve with Spring return Rack & Pinion Actuator Fail Close | [8 empty] | 9263 | 2D | BR-A-AV451 |  |  | NA | NA | NA | Sludge | AISI 316 / RTFM | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Sludge | [5 empty] | Butterfly valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Butterfly valve |  |  | AV | FA | Equipment
Settler and sludge pump Pneumatic actuator AV451 | C2NC-1500-SLG-AV_451 | C2NC-1500-SLG | Valves | Settler and sludge pump Pneumatic actuator. Function: Deliver instrument air to AV451 | Air Con | Included AV451 | [8 empty] | 9263 | 2D | BR-A-AV451 |  |  | NA | NA | NA | - | Composition of materials | - |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | - | [5 empty] | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | GR | Equipment
Settler and sludge pump Solenoid valve AV451 | C2NC-1500-SLG-AV_451 | C2NC-1500-SLG | Valves | Settler and sludge pump Solenoid valve. Function: Switch instrument air to BR-A-AV451 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2D | BR-A-AV451 |  | 24 VDC | < 0,5 | NA | NA | Instrument Air | Composition of materials | NA |  | Solenoid valve | [7 empty] | NA |  |  |  | 24 VDC | Instrument Air | [5 empty] | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | V | Equipment
Settler and sludge pump Butterfly valve AV452 | C2NC-1500-SLG-AV_452 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Open/close sulphur discharge downstream pump | Apollo | 2 Apollo 215L-02SSP8TA0 150# 316SS Lug Butterfly Valve with Spring return Rack & Pinion Actuator Fail Open | [8 empty] | 9263 | 2D | BR-A-AV452 |  |  | NA | NA | NA | Sludge | AISI 316 / RTFM | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Sludge | [5 empty] | Butterfly valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Butterfly valve |  |  | AV | BV | Tanks
Settler and sludge pump Pneumatic actuator AV452 | C2NC-1500-SLG-AV_452 | C2NC-1500-SLG | Valves | Settler and sludge pump Pneumatic actuator. Function: Deliver instrument air to AV452 | Air Con | Included AV452 | [8 empty] | 9263 | 2D | BR-A-AV452 |  |  | NA | NA | NA | - | Composition of materials | - |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | - | [5 empty] | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | CF | Tanks
Settler and sludge pump Solenoid valve AV452 | C2NC-1500-SLG-AV_452 | C2NC-1500-SLG | Valves | Settler and sludge pump Solenoid valve. Function: Switch instrument air to BR-A-AV452 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2D | BR-A-AV452 |  | 24 VDC | < 0,5 | NA | NA | Instrument Air | Composition of materials | NA |  | Solenoid valve | [7 empty] | NA |  |  |  | 24 VDC | Instrument Air | [5 empty] | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | DAV | Equipment
Dilution water Ball valve AV610 | C2NC-1500-DIL-AV_610 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Open close dilution water to settler | Flotite | 1" 320-SS-2-FFF-025-CDA52-PERP Fail Close | [8 empty] | 9263 | 2E | BR-A-AV610 |  |  | NA | NA | NA | Water | AISI 316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Water | [5 empty] | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | AV | F | Equipment
Circulation pumps Pump P310 | C2NC-1500-CIRC-P_310 | C2NC-1500-CIRC | Equipment | Circulation pumps Pump. Function: Circulation Pump | Verder | MCP3 centrifugal pump | [8 empty] | 9263 | 2B | BR-A-P310 |  |  | NA | NA | NA | Process water | composition | 6" inlet / 5" outlet |  | Pump | [7 empty] | 0 |  |  |  |  | Process water | [5 empty] | Pump |  |  |  |  | Process water | [9 empty] | Process water |  |  | Pump |  |  | P | EV | Equipment
Circulation pumps Motor P310_M | C2NC-1500-CIRC-P_310_M | C2NC-1500-CIRC | Equipment | Circulation pumps Motor. Function: Drive P310 | Verder | MCP3 centrifugal pump | [8 empty] | 9263 | 2B | BR-A-P310_M |  | 48 VAC | 31,1 | 0 | 29,5 | - | composition | - |  | Motor | [7 empty] | 0 |  |  |  | 48 VAC | - | [5 empty] | Motor |  |  |  |  | - | [8 empty] | 48 VAC | - |  |  | Motor |  | Analog | P | BL | Equipment
Dilution water Pneumatic actuator AV610 | C2NC-1500-DIL-AV_610 | C2NC-1500-DIL | Valves | Dilution water Pneumatic actuator. Function: Deliver instrument air to AV610 | Air Con | Included AV610 | [8 empty] | 9263 | 2E | BR-A-AV610 |  |  | NA | NA | NA | - | Composition of materials | - |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | - | [5 empty] | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | SM | Equipment
Dilution water Solenoid valve AV610 | C2NC-1500-DIL-AV_610 | C2NC-1500-DIL | Valves | Dilution water Solenoid valve. Function: Switch instrument air to BR-A-AV610 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2E | BR-A-AV610 |  | 24 VDC | < 0,5 | NA | NA | Instrument Air | Composition of materials | NA |  | Solenoid valve | [7 empty] | NA |  |  |  | 24 VDC | Instrument Air | [5 empty] | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | ST | Equipment
Dilution water Ball valve AV620 | C2NC-1500-DIL-AV_620 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Open close dilution water to sulphur discharge | Flotite | 1" 320-SS-2-FFF-025-CDA52-PERP Fail Close | [8 empty] | 9263 | 2E | BR-A-AV620 |  |  | NA | NA | NA | Water | AISI 316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Water | [5 empty] | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | AV | OF | Equipment
Dilution water Pneumatic actuator AV620 | C2NC-1500-DIL-AV_620 | C2NC-1500-DIL | Valves | Dilution water Pneumatic actuator. Function: Deliver instrument air to AV620 | Air Con | Included AV620 | [8 empty] | 9263 | 2E | BR-A-AV620 |  |  | NA | NA | NA | - | Composition of materials | - |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | - | [5 empty] | Pneumatic actuator |  |  |  |  | - | [9 empty] | - |  |  | Pneumatic actuator |  |  | AV | SN | Equipment
Dilution water Solenoid valve AV620 | C2NC-1500-DIL-AV_620 | C2NC-1500-DIL | Valves | Dilution water Solenoid valve. Function: Switch instrument air to BR-A-AV620 | ASCO | SC8551A001MS 24/DC | [8 empty] | 9263 | 2E | BR-A-AV620 |  | 24 VDC | < 0,5 | NA | NA | Instrument Air | Composition of materials | NA |  | Solenoid valve | [7 empty] | NA |  |  |  | 24 VDC | Instrument Air | [5 empty] | Solenoid valve |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Solenoid valve |  | Digital | AV | FA | Equipment
Circulation pumps Check valve CV301 | C2NC-1500-CIRC-CV_301 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow over stand-by pump | Titan | CV12-SS | [8 empty] | 9263 | 2B | BR-A-CV301 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 16" 150# |  | Check valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Check valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Check valve |  |  | CV | BFP | Lines
Circulation pumps Check valve CV311 | C2NC-1500-CIRC-CV_311 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow over stand-by pump | Titan | CV12-SS | [8 empty] | 9263 | 2B | BR-A-CV311 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 16" 150# |  | Check valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Check valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Check valve |  |  | CV | LFP | Lines
Measurement loop and GQA Check valve CV360 | C2NC-1500-MEAS-CV_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Check valve. Function: Prevent backflow of water | Swagelok | CH Series | [8 empty] | 9263 | 2G | BR-A-CV360 |  |  | NA | NA | NA | Process water | AISI 316 / PTFE | 1" |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | Process water | [5 empty] | Check valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Check valve |  |  | CV | SFP | Lines
Settler and sludge pump Diaphragm valve CV450 | C2NC-1500-SLG-CV_450 | C2NC-1500-SLG | Valves | Settler and sludge pump Diaphragm valve. Function: Adjust circulation flow to settler | Saunders | 3/4 Saunders 020-3306-A-11T-DE 150# 316SS Weir Body Diaphragm Valve with PTFE Diaphragm | [8 empty] | 9263 | 2D | BR-A-CV450 |  |  | NA | NA | NA | Process water | AISI316 | 3/4" ANSI 150# |  | Diaphragm valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Process water | [5 empty] | Diaphragm valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Diaphragm valve |  |  | CV | SP | Equipment
Bioreactor and aeration Check valve CV510 | C2NC-1500-BR-CV_510 | C2NC-1500-BR | Valves | Bioreactor and aeration Check valve. Function: Prevent backflow | Titan | CV12-SS | [8 empty] | 9263 | 2C | BR-A-CV510 |  |  | NA | NA | NA | Air | AISI316 / PTFE | 3" 150# |  | Check valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | [5 empty] | Check valve |  |  |  |  | Air | [9 empty] | Air |  |  | Check valve |  |  | CV | PM | Equipment
Bioreactor and aeration Check valve CV520 | C2NC-1500-BR-CV_520 | C2NC-1500-BR | Valves | Bioreactor and aeration Check valve. Function: Prevent backflow | Titan | CV12-SS | [8 empty] | 9263 | 2C | BR-A-CV520 |  |  | NA | NA | NA | Air | AISI316 / PTFE | 3" 150# |  | Check valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | [5 empty] | Check valve |  |  |  |  | Air | [9 empty] | Air |  |  | Check valve |  |  | CV | PG | Equipment
Circulation pumps Check valve CV601 | C2NC-1500-CIRC-CV_601 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow | Swagelok | C Series | [8 empty] | 9263 | 2B | BR-A-CV601 |  |  | NA | NA | NA | Water | AISI 316L / FKM | 1/2" SWAGELOK |  | Check valve | [7 empty] | 3000 PSIG @ 100°F |  |  |  |  | Water | [5 empty] | Check valve |  |  |  |  | Water | [9 empty] | Water |  |  | Check valve |  |  | CV | DM | Equipment
Circulation pumps Check valve CV611 | C2NC-1500-CIRC-CV_611 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow | Swagelok | C Series | [8 empty] | 9263 | 2B | BR-A-CV611 |  |  | NA | NA | NA | Water | AISI 316L / FKM | 1/2" SWAGELOK |  | Check valve | [7 empty] | 3000 PSIG @ 100°F |  |  |  |  | Water | [5 empty] | Check valve |  |  |  |  | Water | [9 empty] | Water |  |  | Check valve |  |  | CV | SFP | Equipment
Circulation pumps Check valve CV630 | C2NC-1500-CIRC-CV_630 | C2NC-1500-CIRC | Valves | Circulation pumps Check valve. Function: Prevent backflow | Titan | CV12-SS | [8 empty] | 9263 | 2B | BR-A-CV630 |  |  | NA | NA | NA | Water | AISI316 / PTFE | 2" 150# |  | Check valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Water | [5 empty] | Check valve |  |  |  |  | Water | [9 empty] | Water |  |  | Check valve |  |  | CV | WS | Equipment
Dilution water Check valve CV650 | C2NC-1500-DIL-CV_650 | C2NC-1500-DIL | Valves | Dilution water Check valve. Function: Prevent backlfow | Swagelok | C Series | [8 empty] | 9263 | 2E | BR-A-CV650 |  |  | NA | NA | NA | Water | AISI 316L / FKM | 1/2" SWAGELOK |  | Check valve | [7 empty] | 3000 PSIG @ 100°F |  |  |  |  | Water | [5 empty] | Check valve |  |  |  |  | Water | [9 empty] | Water |  |  | Check valve |  |  | CV | SNP | Lines
Measurement loop and GQA Flow-through armature DC360 | C2NC-1500-MEAS-DC_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Flow-through armature. Function: Armature for pH and redox sensors | Endress & Hauser | Flowfit-W | [8 empty] | 9263 | 2G | BR-A-DC360 |  |  | NA | NA | NA | Process water | PP / PAL SS316 | G1" |  | Flow-through armature | [7 empty] | NA |  |  |  |  | Process water | [5 empty] | Flow-through armature |  |  |  |  | Process water | [9 empty] | Process water |  |  | Flow-through armature |  |  | DC | VS | Instruments
Measurement loop and GQA Flow-through armature DC362 | C2NC-1500-MEAS-DC_362 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Flow-through armature. Function: Armature for conductivity sensor | Endress & Hauser | flow through armature conductivity CTSP | [8 empty] | 9263 | 2G | BR-A-DC362 |  |  | NA | NA | NA | Process water | PVC | G3/4" |  | Flow-through armature | [7 empty] | NA |  |  |  |  | Process water | [5 empty] | Flow-through armature |  |  |  |  | Process water | [9 empty] | Process water |  |  | Flow-through armature |  |  | DC | NV | Valves
Measurement loop and GQA Diaphragm valve DV360 | C2NC-1500-MEAS-DV_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Diaphragm valve. Function: Adjust flow to analysis | Saunders | 3/4" Saunders 020-3306-A-11T-DE 150# 316ss | [8 empty] | 9263 | 2G | BR-A-DV360 |  |  | NA | NA | NA | Process water | AISI316 | 3/4" ANSI 150# |  | Diaphragm valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Process water | [5 empty] | Diaphragm valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Diaphragm valve |  |  | DV | SF | Equipment
Dilution water Diaphragm valve DV610 | C2NC-1500-DIL-DV_610 | C2NC-1500-DIL | Valves | Dilution water Diaphragm valve. Function: Adjust flow water to settler | Saunders | 1 Saunders 025-3306-A-11T-PE 150# 316SS Weir Body Diaphragm Valve with PTFE Diaphragm | [8 empty] | 9263 | 2E | BR-A-DV610 |  |  | NA | NA | NA | Water | AISI316 | 1" ANSI 150# |  | Diaphragm valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Water | [5 empty] | Diaphragm valve |  |  |  |  | Water | [9 empty] | Water |  |  | Diaphragm valve |  |  | DV | LD | Equipment
Dilution water Diaphragm valve DV620 | C2NC-1500-DIL-DV_620 | C2NC-1500-DIL | Valves | Dilution water Diaphragm valve. Function: Adjust flow dilution water to sulphur discharge | Saunders | 1 Saunders 025-3306-A-11T-PE 150# 316SS Weir Body Diaphragm Valve with PTFE Diaphragm | [8 empty] | 9263 | 2E | BR-A-DV620 |  |  | NA | NA | NA | Water | AISI316 | 1" ANSI 150# |  | Diaphragm valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Water | [5 empty] | Diaphragm valve |  |  |  |  | Water | [9 empty] | Water |  |  | Diaphragm valve |  |  | DV | CH | Equipment
Dilution water Diaphragm valve DV640 | C2NC-1500-DIL-DV_640 | C2NC-1500-DIL | Valves | Dilution water Diaphragm valve. Function: Adjust dilution water to measurement loop | Saunders | 1/2 Saunders 015-3306-A-11T-PE 150# 316SS Weir Body Diaphragm Valve with PTFE Diaphragm | [8 empty] | 9263 | 2E | BR-A-DV640 |  |  | NA | NA | NA | Water | AISI316 | 1/2" ANSI 150# |  | Diaphragm valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Water | [5 empty] | Diaphragm valve |  |  |  |  | Water | [9 empty] | Water |  |  | Diaphragm valve |  |  | DV | GQA | Instruments
Non hazardous proces room Emergency stop indoor ES900 | C2NC-1500-NHPR-ES_900 | C2NC-1500-NHPR | Instruments | Non hazardous proces room Emergency stop indoor. Function: Stop installation | Schneider | 9001SK | [8 empty] | 9263 | 2H | BR-A-ES900 |  | 24 VDC | NA | NA | NA | NA | - | - |  | Emergency stop indoor | [7 empty] | NA |  |  |  | 24 VDC | NA | [5 empty] | Emergency stop indoor |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Emergency stop indoor |  |  | ES | R | Tanks
Non hazardous proces room Emergency stop outdoor ES901 | C2NC-1500-NHPR-ES_901 | C2NC-1500-NHPR | Instruments | Non hazardous proces room Emergency stop outdoor. Function: Stop installation | Schneider | 9001SK | [8 empty] | 9263 | 2H | BR-A-ES901 |  | 24 VDC | NA | NA | NA | NA | - | - |  | Emergency stop outdoor | [7 empty] | NA |  |  |  | 24 VDC | NA | [5 empty] | Emergency stop outdoor |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Emergency stop outdoor |  |  | ES
Dilution water Filter F600 | C2NC-1500-DIL-F_600 | C2NC-1500-DIL | Equipment | Dilution water Filter. Function: Filtering water | Titan | YS61-SS | [8 empty] | 9263 | 2E | BR-A-F600 |  |  | NA | NA | NA | Water | AISI 316 | 2" |  | Filter | [7 empty] | 0 |  |  |  |  | Water | [5 empty] | Filter |  |  |  |  | Water | [9 empty] | Water |  |  | Filter |  |  | F
Non hazardous proces room Fan FA910 | C2NC-1500-NHPR-FA_910 | C2NC-1500-NHPR | Equipment | Non hazardous proces room Fan. Function: refreshment process room | J&D Manufacturing | VES201C | [8 empty] | 9263 | 2H | BR-A-FA910 |  | 12 VAC | 0 | 0 | 0 | Ambient air | Composition of materials | 20" |  | Fan | [7 empty] | NA |  |  |  | 12 VAC | Ambient air | [5 empty] | Fan |  |  |  |  | Ambient air | [8 empty] | 12 VAC | Ambient air |  |  | Fan |  |  | FA
Dilution water Flow indicator FI650 | C2NC-1500-DIL-FI_650 | C2NC-1500-DIL | Instruments | Dilution water Flow indicator. Function: indicate water flow | Kytola instruments | Flowmeter A Range 8M (0,1-1,1 L/min) | [8 empty] | 9263 | 2E | BR-A-FI650 |  |  | 0 | 0 | 0 | Water | PMMA | 3/8" BSP |  | Flow indicator | [7 empty] | 20 barg |  |  |  |  | Water | [5 empty] | Flow indicator |  |  |  |  | Water | [9 empty] | Water |  |  | Flow indicator |  |  | FI
Dilution water Flow indicator recorder (Totalizer) FIR650 | C2NC-1500-DIL-FIR_650 | C2NC-1500-DIL | Instruments | Dilution water Flow indicator recorder (Totalizer). Function: record water flow | MCM | MCM 4041K61 | [8 empty] | 9263 | 2E | BR-A-FIR650 |  |  | 0 | 0 | 0 | Water | Composition of materials | 1/2" |  | Flow indicator recorder (Totalizer) | [7 empty] | 0 |  |  |  |  | Water | [5 empty] | Flow indicator recorder (Totalizer) |  |  |  |  | Water | [9 empty] | Water |  |  | Flow indicator recorder (Totalizer) |  |  | FIR
Circulation pumps Ball valve V310 | C2NC-1500-CIRC-V_310 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block deaeration valve | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263 | 2B | BR-A-V310 |  |  | NA | NA | NA | Cooling water (50% propylene glycol) | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Cooling water (50% propylene glycol) | [5 empty] | Ball valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Ball valve |  |  | V
Circulation pumps Deaeration valve DAV310 | C2NC-1500-CIRC-DAV_310 | C2NC-1500-CIRC | Equipment | Circulation pumps Deaeration valve. Function: Deaerate system | Flamco | FLEXVENT PRO NPT | [8 empty] | 9263 | 2B | BR-A-DAV310 |  |  | NA | NA | NA | Cooling water (50% propylene glycol) | Brass | 1/2" FNPT |  | Deaeration valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | Cooling water (50% propylene glycol) | [5 empty] | Deaeration valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Deaeration valve |  |  | DAV
Caustic scrubber Flow switch FIS200 | C2NC-1500-CS-FIS_200 | C2NC-1500-CS | Instruments | Caustic scrubber Flow switch. Function: validate flowrate | Ameritrol | FX – 0750 – XD | [8 empty] | 9263 | 2A | BR-A-FIS200 |  | 24 DC | 0.15 | 0 | 0 | Process water | AISI 316L | 3/4" MNPT |  | Flow switch | [7 empty] | Vacuum to 4000 PSIG (275 Bar) |  |  |  | 24 DC | Process water | [5 empty] | Flow switch |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow switch |  | Digital | FIS
Circulation pumps Flow indicator SWITCH FIS300 | C2NC-1500-CIRC-FIS_300 | C2NC-1500-CIRC | Instruments | Circulation pumps Flow indicator SWITCH. Function: Flow indication | IFM | SI5000 | [8 empty] | 9263 | 2B | BR-A-FIS300 |  | 24 DC | 0,25 / 0,06 | 0 | 0 | Process water | AISI 316L / FKM | M18 x 1,5 |  | Flow indicator SWITCH | [7 empty] | 435 PSIG (30 BARG) |  |  |  | 24 DC | Process water | [5 empty] | Flow indicator SWITCH |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow indicator SWITCH |  | Digital | FIS
Circulation pumps Flow indicator SWITCH FIS320 | C2NC-1500-CIRC-FIS_320 | C2NC-1500-CIRC | Instruments | Circulation pumps Flow indicator SWITCH. Function: Flow indication | IFM | SI5000 | [8 empty] | 9263 | 2B | BR-A-FIS320 |  | 24 DC | 0,25 / 0,06 | 0 | 0 | Process water | AISI 316L / FKM | M18 x 1,5 |  | Flow indicator SWITCH | [7 empty] | 435 PSIG (30 BARG) |  |  |  | 24 DC | Process water | [5 empty] | Flow indicator SWITCH |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow indicator SWITCH |  | Digital | FIS
Circulation pumps Butterfly valve V331 | C2NC-1500-CIRC-V_331 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Switch between heating / cooling | Emerson | Keystone Figure 322 trim 112 Resilient seated butterfly valve | [8 empty] | 9263 | 2B | BR-A-V331 |  |  | NA | NA | NA | Cooling water (50% propylene glycol) | AISI 316 / EPDM | 4" Multi drill PN 6/10/16, ASME 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Cooling water (50% propylene glycol) | [5 empty] | Butterfly valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Butterfly valve |  |  | V
Circulation pumps Butterfly valve V332 | C2NC-1500-CIRC-V_332 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Switch between heating / cooling | Emerson | Keystone Figure 322 trim 112 Resilient seated butterfly valve | [8 empty] | 9263 | 2B | BR-A-V332 |  |  | NA | NA | NA | Cooling water (50% propylene glycol) | AISI 316 / EPDM | 4" Multi drill PN 6/10/16, ASME 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Cooling water (50% propylene glycol) | [5 empty] | Butterfly valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Biologial reactor R400 | C2NC-1500-BR-R_400 | C2NC-1500-BR | Equipment | Bioreactor and aeration Biologial reactor. Function: Caustic recovery and formation of sulphur | Midwestern Fabricators | BR350 | [8 empty] | 9263 | 2C | BR-A-R400 |  |  | NA | NA | NA | Process water | FRP | 3048 x 6000 mm (10ft x 19ft 14") |  | Biologial reactor | [7 empty] | 0 |  |  |  |  | Process water | [5 empty] | Biologial reactor |  |  |  |  | Process water | [9 empty] | Process water |  |  | Biologial reactor |  |  | R
Bioreactor and aeration Air diffuser SN501_524 | C2NC-1500-BR-SN_501_524 | C2NC-1500-BR | Equipment | Bioreactor and aeration Air diffuser. Function: Air distribution | Mooers | 3/4"NPT Mooers Flexcap Diffuser | [8 empty] | 9263 | 2C | BR-A-SN501-524 |  |  | NA | NA | NA | Ambient air / Process water | PP/EPDM | 3/4" NPT |  | Air diffuser | [7 empty] | 0 |  |  |  |  | Ambient air / Process water | [5 empty] | Air diffuser |  |  |  |  | Ambient air / Process water | [9 empty] | Ambient air / Process water |  |  | Air diffuser |  |  | SN
Bioreactor and aeration Spray nozzle pipe SNP400 | C2NC-1500-BR-SNP_400 | C2NC-1500-BR | Lines | Bioreactor and aeration Spray nozzle pipe. Function: mounting of spray nozzle | DMT | according 9263-8022 | [8 empty] | 9263 | 2C | BR-A-SNP400 |  |  | 0 | 0 | 0 | Process water | AISI 316 | 1" NPT / 2" |  | Spray nozzle pipe | [7 empty] | 0 |  |  |  |  | Process water | [5 empty] | Spray nozzle pipe |  |  |  |  | Process water | [9 empty] | Process water |  |  | Spray nozzle pipe |  |  | SNP
Bioreactor and aeration Spraying Nozzle SN401 | C2NC-1500-BR-SN_401 | C2NC-1500-BR | Equipment | Bioreactor and aeration Spraying Nozzle. Function: Foam removal | Bete | TFXP Full cone spiral spray nozzle TF48 | [8 empty] | 9263 | 2C | BR-A-SN401 |  |  | NA | NA | NA | Process water | AISI 316 | 1" NPT |  | Spraying Nozzle | [7 empty] | 0,5 bar |  |  |  |  | Process water | [5 empty] | Spraying Nozzle |  |  |  |  | Process water | [9 empty] | Process water |  |  | Spraying Nozzle |  |  | SN
Circulation pumps Flow indicator SWITCH FIS330 | C2NC-1500-CIRC-FIS_330 | C2NC-1500-CIRC | Instruments | Circulation pumps Flow indicator SWITCH. Function: validate flowrate | IFM | SI5000 | [8 empty] | 9263 | 2B | BR-A-FIS330 |  | 24 DC | 0,25 / 0,06 | NA | 0 | Process water | AISI 316L / FKM | M18 x 1,5 |  | Flow indicator SWITCH | [7 empty] | 435 PSIG (30 BARG) |  |  |  | 24 DC | Process water | [5 empty] | Flow indicator SWITCH |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow indicator SWITCH |  | Digital | FIS
Measurement loop and GQA Flow indicator SWITCH FIS360 | C2NC-1500-MEAS-FIS_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Flow indicator SWITCH. Function: Flow indication measurement loop | IFM | SI5000 | [8 empty] | 9263 | 2G | BR-A-FIS360 |  | 24 DC | 0,25 / 0,06 | NA | 0 | Process water | AISI 316L / FKM | M18 x 1,5 |  | Flow indicator SWITCH | [7 empty] | 435 PSIG (30 BARG) |  |  |  | 24 DC | Process water | [5 empty] | Flow indicator SWITCH |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow indicator SWITCH |  | Digital | FIS
Dosing skids Flow indicator SWITCH FIS700 | C2NC-1500-CHEM-FIS_700 | C2NC-1500-CHEM | Instruments | Dosing skids Flow indicator SWITCH. Function: validate flowrate | IFM | SI5000 | [8 empty] | 9263 | 2F | BR-A-FIS700 |  | 24 DC | 0,25 / 0,06 | 0 | 0 | Process water | AISI 316L / FKM | M18 x 1,5 |  | Flow indicator SWITCH | [7 empty] | 435 PSIG (30 BARG) |  |  |  | 24 DC | Process water | [5 empty] | Flow indicator SWITCH |  |  |  |  | Process water | [8 empty] | 24 DC | Process water |  |  | Flow indicator SWITCH |  | Digital | FIS
Circulation pumps Flow indicator transmitter FIT340 | C2NC-1500-CIRC-FIT_340 | C2NC-1500-CIRC | Instruments | Circulation pumps Flow indicator transmitter. Function: Flow indication circulation flow to scrubber | Endress & Hauser | Promag W 400, 5W4C2F, DN250 10" | [8 empty] | 9263 | 2B | BR-A-FIT340 |  | 12 VAC | 0.15 | NA | NA | Process water | CS / ALU / ALLOY / PTFE | 10" 150# |  | Flow indicator transmitter | [7 empty] | 73-101 psi |  |  |  | 12 VAC | Process water | [5 empty] | Flow indicator transmitter |  |  |  |  | Process water | [8 empty] | 12 VAC | Process water |  |  | Flow indicator transmitter |  | Analog | FIT
Bioreactor and aeration Flow indicator transmitter FIT510 | C2NC-1500-BR-FIT_510 | C2NC-1500-BR | Instruments | Bioreactor and aeration Flow indicator transmitter. Function: Flow indication air injection | Endress & Hauser | T-mass B 150, 6BABL1, 235mm 9" | [8 empty] | 9263 | 2C | BR-A-FIT510 |  | 24 VDC | 0.35 | NA | NA | Air | SS316 / PEEK | 3/4" NPT |  | Flow indicator transmitter | [7 empty] | -7,25 - 290 psig |  |  |  | 24 VDC | Air | [5 empty] | Flow indicator transmitter |  |  |  |  | Air | [8 empty] | 24 VDC | Air |  |  | Flow indicator transmitter |  | Analog | FIT
Dilution water Flow indicator transmitter FIT610 | C2NC-1500-DIL-FIT_610 | C2NC-1500-DIL | Instruments | Dilution water Flow indicator transmitter. Function: Water consumption totalizer | Endress & Hauser | Promag W 400, 5W4C25, DN25 1" | [8 empty] | 9263 | 2E | BR-A-FIT610 |  | 12 VAC | 0.15 | NA | NA | Water | Composition of materials | 1" |  | Flow indicator transmitter | [7 empty] | 73-101 psi |  |  |  | 12 VAC | Water | [5 empty] | Flow indicator transmitter |  |  |  |  | Water | [8 empty] | 12 VAC | Water |  |  | Flow indicator transmitter |  | Analog | FIT
Non hazardous proces room Grid GR910 | C2NC-1500-NHPR-GR_910 | C2NC-1500-NHPR | Equipment | Non hazardous proces room Grid. Function: Inlet air | Grainger | 0 | [8 empty] | 9263 | 2H | BR-A-GR910 |  |  | NA | NA | NA | Ambient air | Aluminium | 400x400mm |  | Grid | [7 empty] | NA |  |  |  |  | Ambient air | [5 empty] | Grid |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Grid |  |  | GR
Non hazardous proces room Grid GR911 | C2NC-1500-NHPR-GR_911 | C2NC-1500-NHPR | Equipment | Non hazardous proces room Grid. Function: Inlet air | Grainger | 0 | [8 empty] | 9263 | 2H | BR-A-GR911 |  |  | NA | NA | NA | Ambient air | Aluminium | 500x500mm |  | Grid | [7 empty] | NA |  |  |  |  | Ambient air | [5 empty] | Grid |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Grid |  |  | GR
Non hazardous proces room Grid GR912 | C2NC-1500-NHPR-GR_912 | C2NC-1500-NHPR | Equipment | Non hazardous proces room Grid. Function: Inlet air | Grainger | 0 | [8 empty] | 9263 | 2H | BR-A-GR912 |  |  | NA | NA | NA | Ambient air | Aluminium | 500x500mm |  | Grid | [7 empty] | NA |  |  |  |  | Ambient air | [5 empty] | Grid |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Grid |  |  | GR
Circulation pumps Pipe cooler HE310 | C2NC-1500-CIRC-HE_310 | C2NC-1500-CIRC | Equipment | Circulation pumps Pipe cooler. Function: Heat transfer from hot water to proces medium | DMT | According drawing DMT | [8 empty] | 9263 | 2B | BR-A-HE310 |  |  | NA | NA | NA | Process water | AISI304 / NBR | 12" 150# |  | Pipe cooler | [7 empty] | 0 |  |  |  |  | Process water | [5 empty] | Pipe cooler |  |  |  |  | Process water | [9 empty] | Process water |  |  | Pipe cooler |  |  | HE
Non hazardous proces room Heater HE900 | C2NC-1500-NHPR-HE_900 | C2NC-1500-NHPR | Equipment | Non hazardous proces room Heater. Function: Heating | McMaster-Carr | Ceiling-&Wall-Mount Large-Space Electric Heater | [8 empty] | 9263 | 2H | BR-A-HE900 |  | 48 VAC | 0 | 5 | NA | Ambient air | Steel | 0 |  | Heater | [7 empty] | NA |  |  |  | 48 VAC | Ambient air | [5 empty] | Heater |  |  |  |  | Ambient air | [8 empty] | 48 VAC | Ambient air |  |  | Heater |  |  | HE
Caustic scrubber Level switch LS200 | C2NC-1500-CS-LS_200 | C2NC-1500-CS | Instruments | Caustic scrubber Level switch. Function: Protection of pumps from dry running | Endress & Hauser | Liquiphant M FTL51 | [8 empty] | 9263 | 2A | BR-A-LS200 |  | 24 VDC | 0.085 | NA | NA | Process water | AISI 316 | 2" 150# RF |  | Level switch | [7 empty] | NA |  |  |  | 24 VDC | Process water | [5 empty] | Level switch |  |  |  |  | Process water | [8 empty] | 24 VDC | Process water |  |  | Level switch |  | Analog | LS
Bioreactor and aeration Filter F510 | C2NC-1500-BR-F_510 | C2NC-1500-BR | Equipment | Bioreactor and aeration Filter. Function: Filter ingoing air | Aertzen | 0 | [8 empty] | 9263 | 2C | BR-A-F510 |  |  | NA | NA | NA | Air | AISI 316 / paper | G5" |  | Filter | [7 empty] | 0 |  |  |  |  | Air | [5 empty] | Filter |  |  |  |  | Air | [9 empty] | Air |  |  | Filter |  |  | F
Bioreactor and aeration Feed blower FB510 | C2NC-1500-BR-FB_510 | C2NC-1500-BR | Equipment | Bioreactor and aeration Feed blower. Function: Increase pressure of air for bioreactor aeration | Aertzen | AERZEN draaizuigerblower GM 10 S | [8 empty] | 9263 | 2C | BR-A-FB510 |  |  | NA | NA | NA | Air | Composition | 3" |  | Feed blower | [7 empty] | 0 |  |  |  |  | Air | [5 empty] | Feed blower |  |  |  |  | Air | [9 empty] | Air |  |  | Feed blower |  |  | FB
Bioreactor and aeration Motor FB510_M | C2NC-1500-BR-FB_510_M | C2NC-1500-BR | Equipment | Bioreactor and aeration Motor. Function: Drive FB510 | Aertzen | 0 | [8 empty] | 9263 | 2C | BR-A-FB510_M |  | 48 VAC | 15,6 | 0 | 14,8 | - | Composition | 0 |  | Motor | [7 empty] | NA |  |  |  | 48 VAC | - | [5 empty] | Motor |  |  |  |  | - | [8 empty] | 48 VAC | - |  |  | Motor |  | Analog | FB
Bioreactor and aeration Pressure safety valve PZV510 | C2NC-1500-BR-PZV_510 | C2NC-1500-BR | Valves | Bioreactor and aeration Pressure safety valve. Function: protection of overpressure | Aertzen | 0 | [8 empty] | 9263 | 2C | BR-A-PZV510 |  |  | 0 | 0 | 0 | Air | 0 | 0 |  | Pressure safety valve | [7 empty] | 0 |  |  |  |  | Air | [5 empty] | Pressure safety valve |  |  |  |  | Air | [9 empty] | Air |  |  | Pressure safety valve |  |  | PZV
Bioreactor and aeration Compensator BL510 | C2NC-1500-BR-BL_510 | C2NC-1500-BR | Equipment | Bioreactor and aeration Compensator. Function: Absorb shrinking and expanding of piping | Aertzen | 0 | [8 empty] | 9263 | 2C | BR-A-BL510 |  |  | 0 | 0 | 0 | Air | AISI 316 | 3" |  | Compensator | [7 empty] | 0 |  |  |  |  | Air | [5 empty] | Compensator |  |  |  |  | Air | [9 empty] | Air |  |  | Compensator |  |  | BL
Bioreactor and aeration Level switch LS400 | C2NC-1500-BR-LS_400 | C2NC-1500-BR | Instruments | Bioreactor and aeration Level switch. Function: Protection of pumps from dry running | Endress & Hauser | Liquiphant M FTL51 | [8 empty] | 9263 | 2C | BR-A-LS400 |  | 24 VDC | 0.085 | NA | NA | Process water | AISI 316 | 2" 150# RF |  | Level switch | [7 empty] | NA |  |  |  | 24 VDC | Process water | [5 empty] | Level switch |  |  |  |  | Process water | [8 empty] | 24 VDC | Process water |  |  | Level switch |  | Analog | LS
Settler and sludge pump Level switch LS451 | C2NC-1500-SLG-LS_451 | C2NC-1500-SLG | Instruments | Settler and sludge pump Level switch. Function: Protection of pumps from dry running | Endress & Hauser | Liquiphant M FTL51 | [8 empty] | 9263 | 2D | BR-A-LS451 |  | 24 VDC | 0.085 | NA | NA | Process water | AISI 316 | 2" 150# RF |  | Level switch | [7 empty] | NA |  |  |  | 24 VDC | Process water | [5 empty] | Level switch |  |  |  |  | Process water | [8 empty] | 24 VDC | Process water |  |  | Level switch |  | Analog | LS
Circulation pumps Needle valve NV603 | C2NC-1500-CIRC-NV_603 | C2NC-1500-CIRC | Valves | Circulation pumps Needle valve. Function: block water line | Swagelok | Stainless Steel Integral Bonnet Needle Valve, 0.73 Cv, 1/2 in. Swagelok Tube Fitting, Regulating Stem | [8 empty] | 9263 | 2B | BR-A-NV603 |  |  | NA | NA | NA | Water | AISI 316 | 1/2" |  | Needle valve | [7 empty] | 3435 PSIG |  |  |  |  | Water | [5 empty] | Needle valve |  |  |  |  | Water | [9 empty] | Water |  |  | Needle valve |  |  | NV
Circulation pumps Needle valve NV613 | C2NC-1500-CIRC-NV_613 | C2NC-1500-CIRC | Valves | Circulation pumps Needle valve. Function: block water line | Swagelok | Stainless Steel Integral Bonnet Needle Valve, 0.73 Cv, 1/2 in. Swagelok Tube Fitting, Regulating Stem | [8 empty] | 9263 | 2B | BR-A-NV613 |  |  | NA | NA | NA | Water | AISI 316 | 1/2" |  | Needle valve | [7 empty] | 3435 PSIG |  |  |  |  | Water | [5 empty] | Needle valve |  |  |  |  | Water | [9 empty] | Water |  |  | Needle valve |  |  | NV
Dilution water Needle valve NV650 | C2NC-1500-DIL-NV_650 | C2NC-1500-DIL | Valves | Dilution water Needle valve. Function: Control water flow | Swagelok | Stainless Steel Integral Bonnet Needle Valve, 0.73 Cv, 1/2 in. Swagelok Tube Fitting, Regulating Stem | [8 empty] | 9263 | 2E | BR-A-NV650 |  |  | NA | NA | NA | Water | AISI 316 | 1/2" |  | Needle valve | [7 empty] | 3435 PSIG |  |  |  |  | Water | [5 empty] | Needle valve |  |  |  |  | Water | [9 empty] | Water |  |  | Needle valve |  |  | NV
Bioreactor and aeration Filter F520 | C2NC-1500-BR-F_520 | C2NC-1500-BR | Equipment | Bioreactor and aeration Filter. Function: Filter ingoing air | Aertzen | 0 | [8 empty] | 9263 | 2C | BR-A-F520 |  |  | NA | NA | NA | Air | AISI 316 / paper | G5" |  | Filter | [7 empty] | 0 |  |  |  |  | Air | [5 empty] | Filter |  |  |  |  | Air | [9 empty] | Air |  |  | Filter |  |  | F
Bioreactor and aeration Feed blower FB520 | C2NC-1500-BR-FB_520 | C2NC-1500-BR | Equipment | Bioreactor and aeration Feed blower. Function: Increase pressure of air for bioreactor aeration | Aertzen | AERZEN draaizuigerblower GM 10 S | [8 empty] | 9263 | 2C | BR-A-FB520 |  |  | NA | NA | NA | Air | Composition | 3" |  | Feed blower | [7 empty] | 0 |  |  |  |  | Air | [5 empty] | Feed blower |  |  |  |  | Air | [9 empty] | Air |  |  | Feed blower |  |  | FB
Bioreactor and aeration Motor FB520_M | C2NC-1500-BR-FB_520_M | C2NC-1500-BR | Equipment | Bioreactor and aeration Motor. Function: Drive FB510 | Aertzen | 0 | [8 empty] | 9263 | 2C | BR-A-FB520_M |  | 48 VAC | 15,6 | 0 | 14,8 | - | Composition | 0 |  | Motor | [7 empty] | NA |  |  |  | 48 VAC | - | [5 empty] | Motor |  |  |  |  | - | [8 empty] | 48 VAC | - |  |  | Motor |  | Analog | FB
Bioreactor and aeration Pressure safety valve PZV520 | C2NC-1500-BR-PZV_520 | C2NC-1500-BR | Valves | Bioreactor and aeration Pressure safety valve. Function: protection of overpressure | Aertzen | 0 | [8 empty] | 9263 | 2C | BR-A-PZV520 |  |  | 0 | 0 | 0 | Air | 0 | 0 |  | Pressure safety valve | [7 empty] | 0 |  |  |  |  | Air | [5 empty] | Pressure safety valve |  |  |  |  | Air | [9 empty] | Air |  |  | Pressure safety valve |  |  | PZV
Bioreactor and aeration Compensator BL520 | C2NC-1500-BR-BL_520 | C2NC-1500-BR | Equipment | Bioreactor and aeration Compensator. Function: Absorb shrinking and expanding of piping | Aertzen | 0 | [8 empty] | 9263 | 2C | BR-A-BL520 |  |  | 0 | 0 | 0 | Air | AISI 316 | 3" |  | Compensator | [7 empty] | 0 |  |  |  |  | Air | [5 empty] | Compensator |  |  |  |  | Air | [9 empty] | Air |  |  | Compensator |  |  | BL
Dilution water Pressure control valve PCV600 | C2NC-1500-DIL-PCV_600 | C2NC-1500-DIL | Valves | Dilution water Pressure control valve . Function: Prevent high pressure water line | Eriks | Rvs reduceer type Eriks fig 1536 | [8 empty] | 9263 | 2E | BR-A-PCV600 |  |  | NA | NA | NA | Water | AISI 316 | 2" 150# |  | Pressure control valve | [7 empty] | 0 |  |  |  |  | Water | [5 empty] | Pressure control valve |  |  |  |  | Water | [9 empty] | Water |  |  | Pressure control valve |  |  | PCV
Dilution water Pressure control valve PCV650 | C2NC-1500-DIL-PCV_650 | C2NC-1500-DIL | Valves | Dilution water Pressure control valve . Function: Prevent high pressure water line | Eriks | Rvs reduceer type Eriks fig 1535 | [8 empty] | 9263 | 2E | BR-A-PCV650 |  |  | 0 | 0 | 0 | Water | AISI 316 | 1/2" NPT |  | Pressure control valve | [7 empty] | 0 |  |  |  |  | Water | [5 empty] | Pressure control valve |  |  |  |  | Water | [9 empty] | Water |  |  | Pressure control valve |  |  | PCV
Non hazardous proces room Pressure reducing valve PCV900 | C2NC-1500-NHPR-PCV_900 | C2NC-1500-NHPR | Valves | Non hazardous proces room Pressure reducing valve. Function: Adjust air supply pressure | Festo | MS6-LFR | [8 empty] | 9263 | 2H | BR-A-PCV900 |  |  | NA | NA | NA | Instrument Air | composition | 1" |  | Pressure reducing valve | [7 empty] | 0,8 - 20 bar |  |  |  |  | Instrument Air | [5 empty] | Pressure reducing valve |  |  |  |  | Instrument Air | [9 empty] | Instrument Air |  |  | Pressure reducing valve |  |  | PCV
Dilution water Pressure indicator PI600 | C2NC-1500-DIL-PI_600 | C2NC-1500-DIL | Instruments | Dilution water Pressure indicator. Function: Local pressure indication | Ashcroft | Process gauge T5500/T6500 Dual Scale 100mm Low | [8 empty] | 9263 | 2E | BR-A-PI600 |  |  | NA | NA | NA | Water | AISI 316L | 1/2" NPT (male) |  | Pressure indicator | [7 empty] | 0 - 6 bar |  |  |  |  | Water | [5 empty] | Pressure indicator |  |  |  |  | Water | [9 empty] | Water |  |  | Pressure indicator |  |  | PI
Settler and sludge pump Settler S450 | C2NC-1500-SLG-S_450 | C2NC-1500-SLG | Equipment | Settler and sludge pump Settler. Function: Removal of large particles | Midwestern Fabricators | According drawing DMT | [8 empty] | 9263 | 2D | BR-A-S450 |  |  | NA | NA | NA | Process water | FRP | diameter: 39" height:19'-9" |  | Settler | [7 empty] | 0 |  |  |  |  | Process water | [5 empty] | Settler |  |  |  |  | Process water | [9 empty] | Process water |  |  | Settler |  |  | S
Dilution water Pressure indicator PI650 | C2NC-1500-DIL-PI_650 | C2NC-1500-DIL | Instruments | Dilution water Pressure indicator. Function: Local pressure indication | Ashcroft | Process gauge T5500/T6500 Dual Scale 100mm Low | [8 empty] | 9263 | 2E | BR-A-PI650 |  |  | NA | NA | NA | Water | 0 | 1/2" NPT |  | Pressure indicator | [7 empty] | 0 - 6 bar |  |  |  |  | Water | [5 empty] | Pressure indicator |  |  |  |  | Water | [9 empty] | Water |  |  | Pressure indicator |  |  | PI
Bioreactor and aeration Pressure transmitter PIT400 | C2NC-1500-BR-PIT_400 | C2NC-1500-BR | Instruments | Bioreactor and aeration Pressure transmitter. Function: Pressure indication bioreactor for level control | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263 | 2C | BR-A-PIT400 |  | 24 VDC | 0.026 | NA | NA | Process water | SS316 | 2" 150# |  | Pressure transmitter | [7 empty] | 15 psi(g) sensor |  |  |  | 24 VDC | Process water | [5 empty] | Pressure transmitter |  |  |  |  | Process water | [8 empty] | 24 VDC | Process water |  |  | Pressure transmitter |  | Analog | PIT
Settler and sludge pump Pressure transmitter PIT452 | C2NC-1500-SLG-PIT_452 | C2NC-1500-SLG | Instruments | Settler and sludge pump Pressure transmitter. Function: Pressure indication sludge pump dicharge | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263 | 2D | BR-A-PIT452 |  | 24 VDC | 0.026 | NA | NA | Sludge | SS316 | 1/2" NPT |  | Pressure transmitter | [7 empty] | 150 psi(g) sensor |  |  |  | 24 VDC | Sludge | [5 empty] | Pressure transmitter |  |  |  |  | Sludge | [8 empty] | 24 VDC | Sludge |  |  | Pressure transmitter |  | Analog | PIT
Caustic scrubber Pressure transmitter PT100 | C2NC-1500-CS-PT_100 | C2NC-1500-CS | Instruments | Caustic scrubber Pressure transmitter. Function: Measure inlet pressure | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263 | 2A | BR-A-PT100 |  | 24 VDC | 0.026 | NA | NA | Raw biogas | AISI 316L | 1/2" NPT (male) |  | Pressure transmitter | [7 empty] | 15 psi(g) sensor |  |  |  | 24 VDC | Raw biogas | [5 empty] | Pressure transmitter |  |  |  |  | Raw biogas | [8 empty] | 24 VDC | Raw biogas |  |  | Pressure transmitter |  | Analog | PT
Caustic scrubber Pressure transmitter PT102 | C2NC-1500-CS-PT_102 | C2NC-1500-CS | Instruments | Caustic scrubber Pressure transmitter. Function: Pressure Indication of outlet biogas | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263 | 2A | BR-A-PT102 |  | 24 VDC | 0.026 | NA | NA | Clean biogas | SS316 | 1/2" NPT |  | Pressure transmitter | [7 empty] | 15 psi(g) sensor |  |  |  | 24 VDC | Clean biogas | [5 empty] | Pressure transmitter |  |  |  |  | Clean biogas | [8 empty] | 24 VDC | Clean biogas |  |  | Pressure transmitter |  | Analog | PT
Settler and sludge pump Peristaltic discharge pump P450 | C2NC-1500-SLG-P_450 | C2NC-1500-SLG | Equipment | Settler and sludge pump Peristaltic discharge pump . Function: Discharge of sulphur sludge | Verder | Dura 25 | [8 empty] | 9263 | 2D | BR-A-P450 |  |  | NA | NA | NA | Sludge | EPDM hose | 1" ANSI |  | Peristaltic discharge pump | [7 empty] | 2 - 6 barg / 29-86 Psig |  |  |  |  | Sludge | [5 empty] | Peristaltic discharge pump |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Peristaltic discharge pump |  |  | P
Settler and sludge pump Motor P450_M | C2NC-1500-SLG-P_450_M | C2NC-1500-SLG | Equipment | Settler and sludge pump Motor. Function: Drive P450 | Verder | Dura 25 | [8 empty] | 9263 | 2D | BR-A-P450_M |  | 48 VAC | 2,1 | 0 | 0 | - | composition | - |  | Motor | [7 empty] | 2 - 6 barg / 29-86 Psig |  |  |  | 48 VAC | - | [5 empty] | Motor |  |  |  |  | - | [8 empty] | 48 VAC | - |  |  | Motor |  |  | P
Bioreactor and aeration Pressure transmitter PT501 | C2NC-1500-BR-PT_501 | C2NC-1500-BR | Instruments | Bioreactor and aeration Pressure transmitter. Function: Pressure indication air discharge | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263 | 2C | BR-A-PT501 |  | 24 VDC | 0.026 | NA | NA | Air | SS316 | 1/2" NPT |  | Pressure transmitter | [7 empty] | 30 psi(g) sensor |  |  |  | 24 VDC | Air | [5 empty] | Pressure transmitter |  |  |  |  | Air | [8 empty] | 24 VDC | Air |  |  | Pressure transmitter |  | Analog | PT
Dilution water Pressure transmitter PT600 | C2NC-1500-DIL-PT_600 | C2NC-1500-DIL | Instruments | Dilution water Pressure transmitter. Function: Pressure indication supply water | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263 | 2E | BR-A-PT600 |  | 24 VDC | 0.026 | NA | NA | Water | SS316 | 1/2" NPT |  | Pressure transmitter | [7 empty] | 150 psi(g) sensor |  |  |  | 24 VDC | Water | [5 empty] | Pressure transmitter |  |  |  |  | Water | [8 empty] | 24 VDC | Water |  |  | Pressure transmitter |  | Analog | PT
Non hazardous proces room Pressure transmitter PT900 | C2NC-1500-NHPR-PT_900 | C2NC-1500-NHPR | Instruments | Non hazardous proces room Pressure transmitter. Function: Pressure indication instrument air | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263 | 2H | BR-A-PT900 |  | 24 VDC | 0.026 | NA | NA | Instrument Air | SS316 | 1/2" NPT |  | Pressure transmitter | [7 empty] | 150 psi(g) sensor |  |  |  | 24 VDC | Instrument Air | [5 empty] | Pressure transmitter |  |  |  |  | Instrument Air | [8 empty] | 24 VDC | Instrument Air |  |  | Pressure transmitter |  | Analog | PT
Measurement loop and GQA Quality measurement processing unit QITA360 | C2NC-1500-MEAS-QITA_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement processing unit. Function: Processing unit of quality measurement | Endress & Hauser | Liquiline CM444 | [8 empty] | 9263 | 2G | BR-A-QITA360 |  | 24 VDC | 3 | 0.068 | NA | - | composition | - |  | Quality measurement processing unit | [7 empty] | NA |  |  |  | 24 VDC | - | [5 empty] | Quality measurement processing unit |  |  |  |  | - | [8 empty] | 24 VDC | - |  |  | Quality measurement processing unit |  |  | QITA
Measurement loop and GQA Quality measurement (pH) QT360 | C2NC-1500-MEAS-QT_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (pH). Function: PH indication of process liquid | Endress & Hauser | pH meter: Orbipore CPS91D | [8 empty] | 9263 | 2G | BR-A-QT360 |  |  | NA | NA | NA | - | composition | - |  | Quality measurement (pH) | [7 empty] | 0 - 145 psi |  |  |  |  | - | [5 empty] | Quality measurement (pH) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (pH) |  | Analog | QT
Measurement loop and GQA Quality measurement (pH) QT360 | C2NC-1500-MEAS-QT_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (pH). Function: cable | Endress & Hauser | pH meter: cable CYK10 | [8 empty] | 9263 | 2G | BR-A-QT360 |  |  | NA | NA | NA | - | composition | - |  | Quality measurement (pH) | [7 empty] | NA |  |  |  |  | - | [5 empty] | Quality measurement (pH) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (pH) |  |  | QT
Measurement loop and GQA Quality measurement (pH) QT360 | C2NC-1500-MEAS-QT_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (pH). Function: buffer | Endress & Hauser | pH meter: pH7 buffer CPY20 | [8 empty] | 9263 | 2G | BR-A-QT360 |  |  | NA | NA | NA | - | composition | - |  | Quality measurement (pH) | [7 empty] | NA |  |  |  |  | - | [5 empty] | Quality measurement (pH) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (pH) |  |  | QT
Measurement loop and GQA Quality measurement (pH) QT360 | C2NC-1500-MEAS-QT_360 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (pH). Function: buffer | Endress & Hauser | pH meter: pH10 buffer CPY20 | [8 empty] | 9263 | 2G | BR-A-QT360 |  |  | NA | NA | NA | - | composition | - |  | Quality measurement (pH) | [7 empty] | NA |  |  |  |  | - | [5 empty] | Quality measurement (pH) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (pH) |  |  | QT
Measurement loop and GQA Quality measurement (Redox) QT361 | C2NC-1500-MEAS-QT_361 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Redox). Function: Redox indication of process liquid | Rust Automation & Controls - Knick | redox meter: SE 564 memosens ORP sensor | [8 empty] | 9263 | 2G | BR-A-QT361 |  |  | NA | NA | NA | Process water | composition | special |  | Quality measurement (Redox) | [7 empty] | 0 - 145 psi |  |  |  |  | Process water | [5 empty] | Quality measurement (Redox) |  |  |  |  | Process water | [9 empty] | Process water |  |  | Quality measurement (Redox) |  | Analog | QT
Measurement loop and GQA Quality measurement (Redox) QT361 | C2NC-1500-MEAS-QT_361 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Redox). Function: cable | Endress & Hauser | redox meter: cable CYK10 | [8 empty] | 9263 | 2G | BR-A-QT361 |  |  | NA | NA | NA | - | composition | - |  | Quality measurement (Redox) | [7 empty] | NA |  |  |  |  | - | [5 empty] | Quality measurement (Redox) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (Redox) |  |  | QT
Measurement loop and GQA Quality measurement (Redox) QT361 | C2NC-1500-MEAS-QT_361 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Redox). Function: Redox indication of process liquid | Endress & Hauser | redox meter: buffer for calibration CPY3 | [8 empty] | 9263 | 2G | BR-A-QT361 |  |  | NA | NA | NA | - | composition | - |  | Quality measurement (Redox) | [7 empty] | NA |  |  |  |  | - | [5 empty] | Quality measurement (Redox) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (Redox) |  |  | QT
Measurement loop and GQA Quality measurement (Conductivity) QT362 | C2NC-1500-MEAS-QT_362 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Conductivity). Function: Conductivity indication process liquid | Endress & Hauser | Conductivity meter: Indumax CLS50D | [8 empty] | 9263 | 2G | BR-A-QT362 |  |  | NA | NA | NA | Process water | composition | 1" NPT |  | Quality measurement (Conductivity) | [7 empty] | 0 - 290 psi |  |  |  |  | Process water | [5 empty] | Quality measurement (Conductivity) |  |  |  |  | Process water | [9 empty] | Process water |  |  | Quality measurement (Conductivity) |  | Analog | QT
Measurement loop and GQA Quality measurement (Conductivity) QT362 | C2NC-1500-MEAS-QT_362 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Conductivity). Function: Conductivity indication process liquid | Endress & Hauser | Calibration solutuin CLY11 | [8 empty] | 9263 | 2G | BR-A-QT362 |  |  | NA | NA | NA | - | composition | - |  | Quality measurement (Conductivity) | [7 empty] | NA |  |  |  |  | - | [5 empty] | Quality measurement (Conductivity) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (Conductivity) |  |  | QT
Measurement loop and GQA Quality measurement (Conductivity) QT362 | C2NC-1500-MEAS-QT_362 | C2NC-1500-MEAS | Instruments | Measurement loop and GQA Quality measurement (Conductivity). Function: Conductivity indication process liquid | Endress & Hauser | Calibration solutuin CLY11 | [8 empty] | 9263 | 2G | BR-A-QT362 |  |  | NA | NA | NA | - | composition | - |  | Quality measurement (Conductivity) | [7 empty] | NA |  |  |  |  | - | [5 empty] | Quality measurement (Conductivity) |  |  |  |  | - | [9 empty] | - |  |  | Quality measurement (Conductivity) |  |  | QT
Non hazardous proces room Sound indicator ( Horn ) SI900 | C2NC-1500-NHPR-SI_900 | C2NC-1500-NHPR | Instruments | Non hazardous proces room Sound indicator ( Horn ). Function: CREATE AUDIO WARNING SIGNAL | E2S Warning signals | D2xS1 AC115 AB1 A1R | [8 empty] | 9263 | 2H | BR-A-SI900 |  | 115 VAC | NA | NA | NA | AMBIENT AIR | Aluminium - Red - RAL3000 | 130x180x125mm (wxhxd) |  | Sound indicator ( Horn ) | [7 empty] | NA |  |  |  | 115 VAC | AMBIENT AIR | [5 empty] | Sound indicator ( Horn ) |  |  |  |  | AMBIENT AIR | [8 empty] | 115 VAC | AMBIENT AIR |  |  | Sound indicator ( Horn ) |  | Digital | SI
Circulation pumps Temperature indicator TI310 | C2NC-1500-CIRC-TI_310 | C2NC-1500-CIRC | Instruments | Circulation pumps Temperature indicator. Function: indicate temperature | ASHCROFT | EI Bimetal Thermometer D3" | [8 empty] | 9263 | 2B | BR-A-TI310 |  |  | NA | NA | NA | Process water | AISI 316 | 1/2" NPT |  | Temperature indicator | [7 empty] | NA |  |  |  |  | Process water | [5 empty] | Temperature indicator |  |  |  |  | Process water | [9 empty] | Process water |  |  | Temperature indicator |  |  | TI
Circulation pumps Thermowell TI310 | C2NC-1500-CIRC-TI_310 | C2NC-1500-CIRC | Instruments | Circulation pumps Thermowell. Function: protect temperature indicator | McMaster-Carr | for 2-1/2" x 1/4" Stem, 316 Stainless Steel, 1/2 NPT Connection | [8 empty] | 9263 | 2B | BR-A-TI310 |  |  | NA | NA | NA | Process water | AISI 316 | 1" NPT |  | Thermowell | [7 empty] | 7,000 psi @ 70° F |  |  |  |  | Process water | [5 empty] | Thermowell |  |  |  |  | Process water | [9 empty] | Process water |  |  | Thermowell |  |  | TI
Caustic scrubber Temperature transmitter TT100 | C2NC-1500-CS-TT_100 | C2NC-1500-CS | Instruments | Caustic scrubber Temperature transmitter. Function: Measure inlet temperature raw biogas | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263 | 2A | BR-A-TT100 |  | 24 VDC | 0.03 | NA | NA | Raw biogas | SS316 | 1/2" NPTM |  | Temperature transmitter | [7 empty] | NA |  |  |  | 24 VDC | Raw biogas | [5 empty] | Temperature transmitter |  |  |  |  | Raw biogas | [8 empty] | 24 VDC | Raw biogas |  |  | Temperature transmitter |  | Analog | TT
Caustic scrubber Temperature transmitter TT102 | C2NC-1500-CS-TT_102 | C2NC-1500-CS | Instruments | Caustic scrubber Temperature transmitter. Function: Temperature indication outlet biogas | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263 | 2A | BR-A-TT102 |  | 24 VDC | 0.03 | NA | NA | Clean biogas | SS316 | 1/2" NPTM |  | Temperature transmitter | [7 empty] | NA |  |  |  | 24 VDC | Clean biogas | [5 empty] | Temperature transmitter |  |  |  |  | Clean biogas | [8 empty] | 24 VDC | Clean biogas |  |  | Temperature transmitter |  | Analog | TT
Circulation pumps Temperature transmitter TT300 | C2NC-1500-CIRC-TT_300 | C2NC-1500-CIRC | Instruments | Circulation pumps Temperature transmitter. Function: Temperature indication bioreactor outlet | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263 | 2B | BR-A-TT300 |  | 24 VDC | 0.03 | NA | NA | Process water | SS316 | 1/2" NPTM |  | Temperature transmitter | [7 empty] | NA |  |  |  | 24 VDC | Process water | [5 empty] | Temperature transmitter |  |  |  |  | Process water | [8 empty] | 24 VDC | Process water |  |  | Temperature transmitter |  | Analog | TT
Bioreactor and aeration Temperature transmitter TT510 | C2NC-1500-BR-TT_510 | C2NC-1500-BR | Instruments | Bioreactor and aeration Temperature transmitter. Function: Temperature transmitter air discharge | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263 | 2C | BR-A-TT510 |  | 24 VDC | 0.03 | NA | NA | Air | SS316 | 1/2" NPTM |  | Temperature transmitter | [7 empty] | NA |  |  |  | 24 VDC | Air | [5 empty] | Temperature transmitter |  |  |  |  | Air | [8 empty] | 24 VDC | Air |  |  | Temperature transmitter |  | Analog | TT
Bioreactor and aeration Temperature transmitter TT520 | C2NC-1500-BR-TT_520 | C2NC-1500-BR | Instruments | Bioreactor and aeration Temperature transmitter. Function: Temperature indication air discharge | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263 | 2C | BR-A-TT520 |  | 24 VDC | 0.03 | NA | NA | Air | SS316 | 1/2" NPTM |  | Temperature transmitter | [7 empty] | NA |  |  |  | 24 VDC | Air | [5 empty] | Temperature transmitter |  |  |  |  | Air | [8 empty] | 24 VDC | Air |  |  | Temperature transmitter |  | Analog | TT
Non hazardous proces room Temperature transmitter TT900 | C2NC-1500-NHPR-TT_900 | C2NC-1500-NHPR | Instruments | Non hazardous proces room Temperature transmitter. Function: MEASURE AREA TEMPERATURE | Endress & Hauser | TST434-J1A4DW (inclusive TMT181-I PCP FM+CSA, Class I, Div 1+2 ) RTD Thermometer TST434 | [8 empty] | 9263 | 2H | BR-A-TT900 |  | 24 VDC | 0 | 0 | 0 | AMBIENT AIR | Composition of materials | NA |  | Temperature transmitter | [7 empty] | NA |  |  |  | 24 VDC | AMBIENT AIR | [5 empty] | Temperature transmitter |  |  |  |  | AMBIENT AIR | [8 empty] | 24 VDC | AMBIENT AIR |  |  | Temperature transmitter |  | Analog | TT
Caustic scrubber Butterfly valve V104 | C2NC-1500-CS-V_104 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Blow flow to scrubber | Apollo | 16 Apollo 215L-16SSP8TA8 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator and chain Wheel | [8 empty] | 9263 | 2A | BR-A-V104 |  |  | NA | NA | NA | Raw biogas | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Raw biogas | [5 empty] | Butterfly valve |  |  |  |  | Raw biogas | [9 empty] | Raw biogas |  |  | Butterfly valve |  |  | V
Caustic scrubber Butterfly valve V109 | C2NC-1500-CS-V_109 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Block flow after scrubber | Apollo | 16 Apollo 215L-16SSP8TA8 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator and Chain Wheel | [8 empty] | 9263 | 2A | BR-A-V109 |  |  | NA | NA | NA | Clean biogas | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Clean biogas | [5 empty] | Butterfly valve |  |  |  |  | Clean biogas | [9 empty] | Clean biogas |  |  | Butterfly valve |  |  | V
Caustic scrubber Butterfly valve V201 | C2NC-1500-CS-V_201 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: Fill or drain scrubber | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2A | BR-A-V201 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Circulation pumps Butterfly valve V202 | C2NC-1500-CIRC-V_202 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block circulation flow to scrubber | Apollo | 14 Apollo 215L-14SSP8TA8 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator and Chainwheel Operator | [8 empty] | 9263 | 2B | BR-A-V202 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 14" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Caustic scrubber Butterfly valve V204 | C2NC-1500-CS-V_204 | C2NC-1500-CS | Valves | Caustic scrubber Butterfly valve. Function: block flow to bioreactor | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2A | BR-A-V204 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Circulation pumps Butterfly valve V205 | C2NC-1500-CIRC-V_205 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block circulation flow to scrubber | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2B | BR-A-V205 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Circulation pumps Butterfly valve V301 | C2NC-1500-CIRC-V_301 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block in pump | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2B | BR-A-V301 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Circulation pumps Butterfly valve V302 | C2NC-1500-CIRC-V_302 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block in pump | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2B | BR-A-V302 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Circulation pumps Ball valve V303 | C2NC-1500-CIRC-V_303 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Vent | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V303 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V304 | C2NC-1500-CIRC-V_304 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Sample/Drain | Flotite | 1" 320-SS-1-FFF-L-025 | [8 empty] | 9263 | 2B | BR-A-V304 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V305 | C2NC-1500-CIRC-V_305 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block circulation flow to sprayer | Flotite | 2" F150-SS-FFG-L-060 | [8 empty] | 9263 | 2B | BR-A-V305 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 2" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V306 | C2NC-1500-CIRC-V_306 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Drain | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V306 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Butterfly valve V311 | C2NC-1500-CIRC-V_311 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block in pump | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2B | BR-A-V311 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Dosing skids Ball valve V710 | C2NC-1500-CHEM-V_710 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Block caustic suction line | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V710 |  |  | NA | NA | NA | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Caustic 20% | [5 empty] | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Dosing skids Ball valve V715 | C2NC-1500-CHEM-V_715 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V715 |  |  | NA | NA | NA | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Caustic 20% | [5 empty] | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Dosing skids Strainer F710 | C2NC-1500-CHEM-F_710 | C2NC-1500-CHEM | Equipment | Dosing skids Strainer. Function: Filter caustic | Georg Fischer | Type 305 | [8 empty] | 9263 | 2F | BR-A-F710 |  |  | NA | NA | NA | Caustic 20% | PP | 1/2" |  | Strainer | [7 empty] | 0 |  |  |  |  | Caustic 20% | [5 empty] | Strainer |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Strainer |  |  | F
Dosing skids Ball valve V712 | C2NC-1500-CHEM-V_712 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Block in filter | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V712 |  |  | NA | NA | NA | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Caustic 20% | [5 empty] | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Dosing skids Dosing Pump (local setpoint, no 4-20mA) P710 | C2NC-1500-CHEM-P_710 | C2NC-1500-CHEM | Equipment | Dosing skids Dosing Pump (local setpoint, no 4-20mA). Function: Pump caustic to Scrubber | Grundfos | DDA 200-4 AR-PVC/E/C-F-31A7A7BG | [8 empty] | 9263 | 2F | BR-A-P710 |  | 12 VAC | 0.2 | 0 | NA | Caustic 20% | PVC, EPDM, ceramic | 1 1/4" NPT (male) |  | Dosing Pump (local setpoint, no 4-20mA) | [7 empty] | 4 bar |  |  |  | 12 VAC | Caustic 20% | [5 empty] | Dosing Pump (local setpoint, no 4-20mA) |  |  |  |  | Caustic 20% | [8 empty] | 12 VAC | Caustic 20% |  |  | Dosing Pump (local setpoint, no 4-20mA) |  |  | P
Dosing skids Pressure control valve (backpressure) PCV710 | C2NC-1500-CHEM-PCV_710 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV710 |  |  | NA | NA | NA | Caustic 20% | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [7 empty] | 0 |  |  |  |  | Caustic 20% | [5 empty] | Pressure control valve (backpressure) |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V716 | C2NC-1500-CHEM-V_716 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Isolate PI710 | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V716 |  |  | NA | NA | NA | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Caustic 20% | [5 empty] | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Dosing skids Pressure gauge PI710 | C2NC-1500-CHEM-PI_710 | C2NC-1500-CHEM | Instruments | Dosing skids Pressure gauge. Function: Local pressure indication caustic | Ashcroft | Process gauge T5500/T6500 Dual Scale 100mm back | [8 empty] | 9263 | 2F | BR-A-PI710 |  |  | NA | NA | NA | Caustic 20% | AISI 316L | 1/2" NPT (male) |  | Pressure gauge | [7 empty] | 0 - 6 bar |  |  |  |  | Caustic 20% | [5 empty] | Pressure gauge |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Pressure gauge |  |  | PI
Dosing skids Pressure control valve (backpressure) PCV711 | C2NC-1500-CHEM-PCV_711 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV711 |  |  | NA | NA | NA | Caustic 20% | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [7 empty] | 0 |  |  |  |  | Caustic 20% | [5 empty] | Pressure control valve (backpressure) |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V717 | C2NC-1500-CHEM-V_717 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V717 |  |  | NA | NA | NA | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Caustic 20% | [5 empty] | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Circulation pumps Butterfly valve V312 | C2NC-1500-CIRC-V_312 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block in pump | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2B | BR-A-V312 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Dosing skids Level switch LS710 | C2NC-1500-CHEM-LS_710 | C2NC-1500-CHEM | Instruments | Dosing skids Level switch. Function: Leak detection | Eriks | EL10 | [8 empty] | 9263 | 2F | BR-A-LS710 |  | 24 VDC | NA | NA | NA | Caustic 20% | PVC-U | 1/2" |  | Level switch | [7 empty] | NA |  |  |  | 24 VDC | Caustic 20% | [5 empty] | Level switch |  |  |  |  | Caustic 20% | [8 empty] | 24 VDC | Caustic 20% |  |  | Level switch |  | Digital | LS
Dosing skids Ball valve V718 | C2NC-1500-CHEM-V_718 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Draining cabinet | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V718 |  |  | NA | NA | NA | Caustic 20% | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Caustic 20% | [5 empty] | Ball valve |  |  |  |  | Caustic 20% | [9 empty] | Caustic 20% |  |  | Ball valve |  |  | V
Dosing skids Vessel BV720 | C2NC-1500-CHEM-BV_720 | C2NC-1500-CHEM | Valves | Dosing skids Vessel. Function: Storage of nutrients | Grundfos | 300L tank | [8 empty] | 9263 | 2F | BR-A-BV720 |  |  | NA | NA | NA | Nutrients | PE | 300 Liter tank |  | Vessel | [7 empty] | 0 |  |  |  |  | Nutrients | [5 empty] | Vessel |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Vessel |  |  | BV
Dosing skids Strainer F720 | C2NC-1500-CHEM-F_720 | C2NC-1500-CHEM | Equipment | Dosing skids Strainer. Function: Filter influent nutrient pump | Grundfos | Part of suction lance RSL-1200-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-F720 |  |  | NA | NA | NA | Nutrients | PP / EPDM | special |  | Strainer | [7 empty] | 0 |  |  |  |  | Nutrients | [5 empty] | Strainer |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Strainer |  |  | F
Dosing skids Check valve CV720 | C2NC-1500-CHEM-CV_720 | C2NC-1500-CHEM | Valves | Dosing skids Check valve. Function: Prevent backflow of nutrients into storage vessel | Grundfos | Part of suction lance RSL-1200-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-CV720 |  |  | NA | NA | NA | Nutrients | PVC-U / EPDM | special |  | Check valve | [7 empty] | 0 |  |  |  |  | Nutrients | [5 empty] | Check valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Check valve |  |  | CV
Dosing skids Level switch LS720 | C2NC-1500-CHEM-LS_720 | C2NC-1500-CHEM | Instruments | Dosing skids Level switch. Function: Indicate LL level in storage vessel | Grundfos | Part of suction lance RSL-1200-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-LS720 |  | 24 VDC | NA | NA | NA | Nutrients | PVC-U | special |  | Level switch | [7 empty] | NA |  |  |  | 24 VDC | Nutrients | [5 empty] | Level switch |  |  |  |  | Nutrients | [8 empty] | 24 VDC | Nutrients |  |  | Level switch |  | Digital | LS
Dosing skids Level switch LS721 | C2NC-1500-CHEM-LS_721 | C2NC-1500-CHEM | Instruments | Dosing skids Level switch. Function: Indicate L level in storage vessel | Grundfos | Part of suction lance RSL-1200-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-LS721 |  | 24 VDC | NA | NA | NA | Nutrients | PVC-U | special |  | Level switch | [7 empty] | NA |  |  |  | 24 VDC | Nutrients | [5 empty] | Level switch |  |  |  |  | Nutrients | [8 empty] | 24 VDC | Nutrients |  |  | Level switch |  | Digital | LS
Dosing skids Ball valve V720 | C2NC-1500-CHEM-V_720 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Block nutrients suction line | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V720 |  |  | NA | NA | NA | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Nutrients | [5 empty] | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Ball valve V721 | C2NC-1500-CHEM-V_721 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V721 |  |  | NA | NA | NA | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Nutrients | [5 empty] | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Dosing Pump (local setpoint, no 4-20mA) P720 | C2NC-1500-CHEM-P_720 | C2NC-1500-CHEM | Equipment | Dosing skids Dosing Pump (local setpoint, no 4-20mA). Function: Pump nutrients to scrubber | Grundfos | DDA 7.5-16 AR-PVC/E/C-F-31U7U7BG | [8 empty] | 9263 | 2F | BR-A-P720 |  | 12 VAC | 0.2 | 0 | NA | Nutrients | PVC, EPDM, ceramic | 5/8" NPT (male) |  | Dosing Pump (local setpoint, no 4-20mA) | [7 empty] | 10 bar |  |  |  | 12 VAC | Nutrients | [5 empty] | Dosing Pump (local setpoint, no 4-20mA) |  |  |  |  | Nutrients | [8 empty] | 12 VAC | Nutrients |  |  | Dosing Pump (local setpoint, no 4-20mA) |  |  | P
Dosing skids Pressure control valve (backpressure) PCV720 | C2NC-1500-CHEM-PCV_720 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV720 |  |  | NA | NA | NA | Nutrients | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [7 empty] | 0 |  |  |  |  | Nutrients | [5 empty] | Pressure control valve (backpressure) |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V722 | C2NC-1500-CHEM-V_722 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Isolate PI720 | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V722 |  |  | NA | NA | NA | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Nutrients | [5 empty] | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Pressure gauge PI720 | C2NC-1500-CHEM-PI_720 | C2NC-1500-CHEM | Instruments | Dosing skids Pressure gauge. Function: Local pressure indication nutrients | Ashcroft | Process gauge T5500/T6500 Dual Scale 100mm Back | [8 empty] | 9263 | 2F | BR-A-PI720 |  |  | NA | NA | NA | Nutrients | AISI 316L | 1/2" NPT (male) |  | Pressure gauge | [7 empty] | 0 - 6 bar |  |  |  |  | Nutrients | [5 empty] | Pressure gauge |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Pressure gauge |  |  | PI
Dosing skids Pressure control valve (backpressure) PCV721 | C2NC-1500-CHEM-PCV_721 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV721 |  |  | NA | NA | NA | Nutrients | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [7 empty] | 0 |  |  |  |  | Nutrients | [5 empty] | Pressure control valve (backpressure) |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V723 | C2NC-1500-CHEM-V_723 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V723 |  |  | NA | NA | NA | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Nutrients | [5 empty] | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Ball valve V724 | C2NC-1500-CHEM-V_724 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Draining cabinet | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V724 |  |  | NA | NA | NA | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Nutrients | [5 empty] | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Ball valve V725 | C2NC-1500-CHEM-V_725 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Draining cabinet | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V725 |  |  | NA | NA | NA | Nutrients | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Nutrients | [5 empty] | Ball valve |  |  |  |  | Nutrients | [9 empty] | Nutrients |  |  | Ball valve |  |  | V
Dosing skids Vessel BV730 | C2NC-1500-CHEM-BV_730 | C2NC-1500-CHEM | Valves | Dosing skids Vessel. Function: Storage of antifoam | Grundfos | Tank 60ltr PE-transp./black | [8 empty] | 9263 | 2F | BR-A-BV730 |  |  | NA | NA | NA | Antifoam | PE | 60l (15 gallons) |  | Vessel | [7 empty] | 0 |  |  |  |  | Antifoam | [5 empty] | Vessel |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Vessel |  |  | BV
Dosing skids Strainer F730 | C2NC-1500-CHEM-F_730 | C2NC-1500-CHEM | Equipment | Dosing skids Strainer. Function: Filter influent antifoam pump | Grundfos | part of suction lance RSL-0500-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-F730 |  |  | NA | NA | NA | Antifoam | PVC-U | special |  | Strainer | [7 empty] | 0 |  |  |  |  | Antifoam | [5 empty] | Strainer |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Strainer |  |  | F
Dosing skids Check valve CV730 | C2NC-1500-CHEM-CV_730 | C2NC-1500-CHEM | Valves | Dosing skids Check valve. Function: Prevent backflow of antifoam into storage vessel | Grundfos | part of suction lance RSL-0500-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-CV730 |  |  | NA | NA | NA | Antifoam | PVC-U / EPDM | special |  | Check valve | [7 empty] | 0 |  |  |  |  | Antifoam | [5 empty] | Check valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Check valve |  |  | CV
Dosing skids Level switch LS730 | C2NC-1500-CHEM-LS_730 | C2NC-1500-CHEM | Instruments | Dosing skids Level switch. Function: Indicate LL level in storage vessel | Grundfos | part of suction lance RSL-0500-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-LS730 |  | 24 VDC | NA | NA | NA | Antifoam | PVC-U | special |  | Level switch | [7 empty] | NA |  |  |  | 24 VDC | Antifoam | [5 empty] | Level switch |  |  |  |  | Antifoam | [8 empty] | 24 VDC | Antifoam |  |  | Level switch |  | Digital | LS
Dosing skids Level switch LS731 | C2NC-1500-CHEM-LS_731 | C2NC-1500-CHEM | Instruments | Dosing skids Level switch. Function: Indicate L level in storage vessel | Grundfos | part of suction lance RSL-0500-2L-G5/8 PE/V,E/C U2 | [8 empty] | 9263 | 2F | BR-A-LS731 |  | 24 VDC | NA | NA | NA | Antifoam | PVC-U | special |  | Level switch | [7 empty] | NA |  |  |  | 24 VDC | Antifoam | [5 empty] | Level switch |  |  |  |  | Antifoam | [8 empty] | 24 VDC | Antifoam |  |  | Level switch |  | Digital | LS
Dosing skids Ball valve V730 | C2NC-1500-CHEM-V_730 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Block antifoam input | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V730 |  |  | NA | NA | NA | Antifoam | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Antifoam | [5 empty] | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V
Dosing skids Ball valve V731 | C2NC-1500-CHEM-V_731 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V731 |  |  | NA | NA | NA | Antifoam | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Antifoam | [5 empty] | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V
Dosing skids Dosing Pump (local setpoint, no 4-20mA) P730 | C2NC-1500-CHEM-P_730 | C2NC-1500-CHEM | Equipment | Dosing skids Dosing Pump (local setpoint, no 4-20mA). Function: Pump antifoam to scrubber | Grundfos | DDA 7.5-16 AR-PVC/E/C-F-31U7U7BG | [8 empty] | 9263 | 2F | BR-A-P730 |  | 12 VAC | 0.2 | 0 | NA | Antifoam | composition | 5/8" NPT (male) |  | Dosing Pump (local setpoint, no 4-20mA) | [7 empty] | 10 bar |  |  |  | 12 VAC | Antifoam | [5 empty] | Dosing Pump (local setpoint, no 4-20mA) |  |  |  |  | Antifoam | [8 empty] | 12 VAC | Antifoam |  |  | Dosing Pump (local setpoint, no 4-20mA) |  |  | P
Dosing skids Pressure control valve (backpressure) PCV730 | C2NC-1500-CHEM-PCV_730 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV730 |  |  | NA | NA | NA | Antifoam | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [7 empty] | 0 |  |  |  |  | Antifoam | [5 empty] | Pressure control valve (backpressure) |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V732 | C2NC-1500-CHEM-V_732 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Isolate PI730 | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V732 |  |  | NA | NA | NA | Antifoam | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Antifoam | [5 empty] | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V
Dosing skids Pressure gauge PI730 | C2NC-1500-CHEM-PI_730 | C2NC-1500-CHEM | Instruments | Dosing skids Pressure gauge. Function: Local pressure indication antifoam | Ashcroft | Process gauge T5500/T6500 Dual Scale 100mm Back | [8 empty] | 9263 | 2F | BR-A-PI730 |  |  | NA | NA | NA | Antifoam | AISI 316L | 1/2" NPT (male) |  | Pressure gauge | [7 empty] | 0 - 6 bar |  |  |  |  | Antifoam | [5 empty] | Pressure gauge |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Pressure gauge |  |  | PI
Dosing skids Pressure control valve (backpressure) PCV731 | C2NC-1500-CHEM-PCV_731 | C2NC-1500-CHEM | Valves | Dosing skids Pressure control valve (backpressure). Function: Prevent high pressure in dosing line | Georg Fischer | Type 586 | [8 empty] | 9263 | 2F | BR-A-PCV731 |  |  | NA | NA | NA | Antifoam | PP / EPDM | 1/2" |  | Pressure control valve (backpressure) | [7 empty] | 0 |  |  |  |  | Antifoam | [5 empty] | Pressure control valve (backpressure) |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Pressure control valve (backpressure) |  |  | PCV
Dosing skids Ball valve V733 | C2NC-1500-CHEM-V_733 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Purging/sampling | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V733 |  |  | NA | NA | NA | Antifoam | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Antifoam | [5 empty] | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V
Dosing skids Ball valve V734 | C2NC-1500-CHEM-V_734 | C2NC-1500-CHEM | Valves | Dosing skids Ball valve. Function: Draining cabinet | Georg Fischer | Type 546 | [8 empty] | 9263 | 2F | BR-A-V734 |  |  | NA | NA | NA | Antifoam | PP / EPDM | 1/2" |  | Ball valve | [7 empty] | 0 |  |  |  |  | Antifoam | [5 empty] | Ball valve |  |  |  |  | Antifoam | [9 empty] | Antifoam |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V313 | C2NC-1500-CIRC-V_313 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Vent | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V313 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V314 | C2NC-1500-CIRC-V_314 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Drain | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V314 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Butterfly valve V316 | C2NC-1500-CIRC-V_316 | C2NC-1500-CIRC | Valves | Circulation pumps Butterfly valve. Function: Block in heat exchanger | Apollo | 4 Apollo 215L-04SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2B | BR-A-V316 |  |  | NA | NA | NA | Cooling water (50% propylene glycol) | AISI316 / PTFE | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Cooling water (50% propylene glycol) | [5 empty] | Butterfly valve |  |  |  |  | Cooling water (50% propylene glycol) | [9 empty] | Cooling water (50% propylene glycol) |  |  | Butterfly valve |  |  | V
Circulation pumps Ball valve V320 | C2NC-1500-CIRC-V_320 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block flow to settler | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2B | BR-A-V320 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V330 | C2NC-1500-CIRC-V_330 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Block circulation flow to discharge | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2B | BR-A-V330 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V341 | C2NC-1500-CIRC-V_341 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: Sample/Drain | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V341 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Measurement loop and GQA Ball valve V360 | C2NC-1500-MEAS-V_360 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Ball valve. Function: Purging/ inertization/sampling | Flotite | 1" 320-SS-1-FFF-025 | [8 empty] | 9263 | 2G | BR-A-V360 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Measurement loop and GQA Ball valve V361 | C2NC-1500-MEAS-V_361 | C2NC-1500-MEAS | Valves | Measurement loop and GQA Ball valve. Function: Block analysis line | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2G | BR-A-V361 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Process water | [5 empty] | Ball valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Ball valve |  |  | V
Bioreactor and aeration Butterfly valve V400 | C2NC-1500-BR-V_400 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Fill or drain bioreactor | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V400 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V401 | C2NC-1500-BR-V_401 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block circulation flow to pumps | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2C | BR-A-V401 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V402 | C2NC-1500-BR-V_402 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block pressure transmitter | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V402 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V405 | C2NC-1500-BR-V_405 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block circulation flow from scrubber | Apollo | 16 Apollo 215L-16SSP8TA7 150# 316SS Lug Body Butterfly Valve with Locking Gear Operator | [8 empty] | 9263 | 2C | BR-A-V405 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 16" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Settler and sludge pump Butterfly valve V406 | C2NC-1500-SLG-V_406 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Overflow of settler to bioreactor | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2D | BR-A-V406 |  |  | NA | NA | NA | Process water | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Process water | [5 empty] | Butterfly valve |  |  |  |  | Process water | [9 empty] | Process water |  |  | Butterfly valve |  |  | V
Settler and sludge pump Butterfly valve V450 | C2NC-1500-SLG-V_450 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Fill / drain settler | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2D | BR-A-V450 |  |  | NA | NA | NA | Sludge | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Sludge | [5 empty] | Butterfly valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Butterfly valve |  |  | V
Settler and sludge pump Butterfly valve V451 | C2NC-1500-SLG-V_451 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Block settler outlet | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2D | BR-A-V451 |  |  | NA | NA | NA | Sludge | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Sludge | [5 empty] | Butterfly valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Butterfly valve |  |  | V
Settler and sludge pump Butterfly valve V453 | C2NC-1500-SLG-V_453 | C2NC-1500-SLG | Valves | Settler and sludge pump Butterfly valve. Function: Block settler inlet | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2D | BR-A-V453 |  |  | NA | NA | NA | Sludge | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Sludge | [5 empty] | Butterfly valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Butterfly valve |  |  | V
Settler and sludge pump Ball valve V456 | C2NC-1500-SLG-V_456 | C2NC-1500-SLG | Valves | Settler and sludge pump Ball valve. Function: Sample/Drain | Flotite | 1" 320-SS-1-FFF-025 | [8 empty] | 9263 | 2D | BR-A-V456 |  |  | NA | NA | NA | Sludge | AISI316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Sludge | [5 empty] | Ball valve |  |  |  |  | Sludge | [9 empty] | Sludge |  |  | Ball valve |  |  | V
Bioreactor and aeration Butterfly valve V510 | C2NC-1500-BR-V_510 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V510 |  |  | NA | NA | NA | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | [5 empty] | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V514 | C2NC-1500-BR-V_514 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V514 |  |  | NA | NA | NA | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | [5 empty] | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V515 | C2NC-1500-BR-V_515 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V515 |  |  | NA | NA | NA | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | [5 empty] | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V516 | C2NC-1500-BR-V_516 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V516 |  |  | NA | NA | NA | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | [5 empty] | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V517 | C2NC-1500-BR-V_517 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V517 |  |  | NA | NA | NA | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | [5 empty] | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V518 | C2NC-1500-BR-V_518 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V518 |  |  | NA | NA | NA | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | [5 empty] | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V519 | C2NC-1500-BR-V_519 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet aeration line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V519 |  |  | NA | NA | NA | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | [5 empty] | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Bioreactor and aeration Butterfly valve V520 | C2NC-1500-BR-V_520 | C2NC-1500-BR | Valves | Bioreactor and aeration Butterfly valve. Function: Block inlet airation line | Apollo | 3 Apollo 215L-03SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2C | BR-A-V520 |  |  | NA | NA | NA | Air | AISI316 / PTFE | 3" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Air | [5 empty] | Butterfly valve |  |  |  |  | Air | [9 empty] | Air |  |  | Butterfly valve |  |  | V
Dilution water Butterfly valve V600 | C2NC-1500-DIL-V_600 | C2NC-1500-DIL | Valves | Dilution water Butterfly valve. Function: Block dilution water flow | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2E | BR-A-V600 |  |  | NA | NA | NA | Water | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Water | [5 empty] | Butterfly valve |  |  |  |  | Water | [9 empty] | Water |  |  | Butterfly valve |  |  | V
Dilution water Ball valve V601 | C2NC-1500-DIL-V_601 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Drain | Flotite | 1" 320-SS-1-FFF-025 | [8 empty] | 9263 | 2E | BR-A-V601 |  |  | NA | NA | NA | Water | AISI316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Water | [5 empty] | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V602 | C2NC-1500-CIRC-V_602 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: block water line | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V602 |  |  | NA | NA | NA | Water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Water | [5 empty] | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Dilution water Ball valve V610 | C2NC-1500-DIL-V_610 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Block water to bioreactor / settler | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2E | BR-A-V610 |  |  | NA | NA | NA | Water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Water | [5 empty] | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Circulation pumps Ball valve V612 | C2NC-1500-CIRC-V_612 | C2NC-1500-CIRC | Valves | Circulation pumps Ball valve. Function: block water line | Flotite | 1/2" 320-SS-2-FFF-L-015 | [8 empty] | 9263 | 2B | BR-A-V612 |  |  | NA | NA | NA | Water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Water | [5 empty] | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Dilution water Ball valve V620 | C2NC-1500-DIL-V_620 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Block water to sulphur discharge | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2E | BR-A-V620 |  |  | NA | NA | NA | Water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Water | [5 empty] | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Dilution water Butterfly valve V630 | C2NC-1500-DIL-V_630 | C2NC-1500-DIL | Valves | Dilution water Butterfly valve. Function: Block dilution water to Scrubber | Apollo | 2 Apollo 215L-02SSP8TA1 150# 316SS Lug Butterfly Valve with Lever Handle | [8 empty] | 9263 | 2E | BR-A-V630 |  |  | NA | NA | NA | Water | AISI316 / PTFE | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | Water | [5 empty] | Butterfly valve |  |  |  |  | Water | [9 empty] | Water |  |  | Butterfly valve |  |  | V
Dilution water Ball valve V640 | C2NC-1500-DIL-V_640 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Block flow measurement loop | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2E | BR-A-V640 |  |  | NA | NA | NA | Water | AISI316 / PTFE | 1" |  | Ball valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Water | [5 empty] | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Dilution water Ball valve V650 | C2NC-1500-DIL-V_650 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Block water flow | Flotite | 1/2" 320-SS-2-FFF-L-015 | [8 empty] | 9263 | 2E | BR-A-V650 |  |  | NA | NA | NA | Water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Water | [5 empty] | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Dilution water Ball valve V651 | C2NC-1500-DIL-V_651 | C2NC-1500-DIL | Valves | Dilution water Ball valve. Function: Deaerate system | Flotite | 1/2" 320-SS-1-FFF-L-016 | [8 empty] | 9263 | 2E | BR-A-V651 |  |  | NA | NA | NA | Water | AISI316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Water | [5 empty] | Ball valve |  |  |  |  | Water | [9 empty] | Water |  |  | Ball valve |  |  | V
Non hazardous proces room Ball Valve V900 | C2NC-1500-NHPR-V_900 | C2NC-1500-NHPR | Valves | Non hazardous proces room Ball Valve. Function: Block air flow | Flotite | 1" 320-SS-2-FFF-025 | [8 empty] | 9263 | 2H | BR-A-V900 |  |  | NA | NA | NA | Instrument Air | AISI316 / PTFE | 1" |  | Ball Valve | [7 empty] | 63 Bar - 913 Psig |  |  |  |  | Instrument Air | [5 empty] | Ball Valve |  |  |  |  | Instrument Air | [9 empty] | Instrument Air |  |  | Ball Valve |  |  | V
Non hazardous proces room Ball valve V901 | C2NC-1500-NHPR-V_901 | C2NC-1500-NHPR | Valves | Non hazardous proces room Ball valve. Function: Isolate PT900 | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2H | BR-A-V901 |  |  | NA | NA | NA | Instrument Air | AISI316 / PTFE | 1/2" |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Instrument Air | [5 empty] | Ball valve |  |  |  |  | Instrument Air | [9 empty] | Instrument Air |  |  | Ball valve |  |  | V
Non hazardous proces room Ball valve V902 | C2NC-1500-NHPR-V_902 | C2NC-1500-NHPR | Valves | Non hazardous proces room Ball valve. Function: sampling | Flotite | 1/2" 320-SS-1-FFF-L-015 | [8 empty] | 9263 | 2H | BR-A-V902 |  |  | NA | NA | NA | Instrument Air | AISI316 / PTFE | 1/2" |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | Instrument Air | [5 empty] | Ball valve |  |  |  |  | Instrument Air | [9 empty] | Instrument Air |  |  | Ball valve |  |  | V
Non hazardous proces room Manual valve V910 | C2NC-1500-NHPR-V_910 | C2NC-1500-NHPR | Valves | Non hazardous proces room Manual valve. Function: block air flow | Grainger | Included in Louvre GR910 | [8 empty] | 9263 | 2H | BR-A-V910 |  |  | 0 | 0 | 0 | Ambient air | Aluminium | 0 |  | Manual valve | [7 empty] | 0 |  |  |  |  | Ambient air | [5 empty] | Manual valve |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Manual valve |  |  | V
Non hazardous proces room Manual valve V911 | C2NC-1500-NHPR-V_911 | C2NC-1500-NHPR | Valves | Non hazardous proces room Manual valve. Function: block air flow | Grainger | Included in Louvre GR911 | [8 empty] | 9263 | 2H | BR-A-V911 |  |  | 0 | 0 | 0 | Ambient air | Aluminium | 0 |  | Manual valve | [7 empty] | 0 |  |  |  |  | Ambient air | [5 empty] | Manual valve |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Manual valve |  |  | V
Non hazardous proces room Manual valve V912 | C2NC-1500-NHPR-V_912 | C2NC-1500-NHPR | Valves | Non hazardous proces room Manual valve. Function: block air flow | Grainger | Included in Louvre GR912 | [8 empty] | 9263 | 2H | BR-A-V912 |  |  | 0 | 0 | 0 | Ambient air | Aluminium | 0 |  | Manual valve | [7 empty] | 0 |  |  |  |  | Ambient air | [5 empty] | Manual valve |  |  |  |  | Ambient air | [9 empty] | Ambient air |  |  | Manual valve |  |  | V
Pre-Treatment Ball valve V101 | C2NC-1500-PRE-V_101 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V101 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Flow indicator transmitter FIT110 | C2NC-1500-PRE-FIT_110 | C2NC-1500-PRE | Instruments | Pre-Treatment Flow indicator transmitter. Function: Measure biogas flow | Endress & Hauser | T-mass 65I | [8 empty] | 9263-3A | 3A | MS-A-FIT110 |  | 0 | 0 | 0 | 0 | BIOGAS | Composition of materials | 1" MNPT in 16" pipe |  | Flow indicator transmitter | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Flow indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Flow indicator transmitter |  | Analog | FIT
Pre-Treatment Heat exchanger HE110 | C2NC-1500-PRE-HE_110 | C2NC-1500-PRE | Equipment | Pre-Treatment Heat exchanger. Function: COOL DOWN GAS | Xchanger | Model C-450 | [8 empty] | 9263-3A | 3A | MS-A-HE110 |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 | 12" 150# (process) 2" (service) |  | Heat exchanger | [7 empty] | 15 lb/in2 |  |  |  |  | BIOGAS | [5 empty] | Heat exchanger |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Heat exchanger |  |  | HE
Pre-Treatment Ball valve V120 | C2NC-1500-PRE-V_120 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: Block drain | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V120 |  | NA | NA | NA | NA | CONDENSATE | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | CONDENSATE | [5 empty] | Ball valve |  |  |  |  | CONDENSATE | [8 empty] | NA | CONDENSATE |  |  | Ball valve |  |  | V
Pre-Treatment Ball valve V121 | C2NC-1500-PRE-V_121 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: Block drain | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V121 |  | NA | NA | NA | NA | CONDENSATE | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | CONDENSATE | [5 empty] | Ball valve |  |  |  |  | CONDENSATE | [8 empty] | NA | CONDENSATE |  |  | Ball valve |  |  | V
Pre-Treatment Water separator WS110 | C2NC-1500-PRE-WS_110 | C2NC-1500-PRE | Equipment | Pre-Treatment Water separator. Function: SEPARATE CONDENSED WATER | DMT | according to drawing DMT | [8 empty] | 9263-3A | 3A | MS-A-WS110 |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 | 1" |  | Water separator | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Water separator |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Water separator |  |  | WS
Pre-Treatment Level switch LS110 | C2NC-1500-PRE-LS_110 | C2NC-1500-PRE | Instruments | Pre-Treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-3A | 3A | MS-A-LS110 |  | 24 VDC | NA | NA | NA | BIOGAS | Composition of materials | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | BIOGAS | [5 empty] | Level switch |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Level switch |  | Analog | LS
Pre-Treatment Level switch LS111 | C2NC-1500-PRE-LS_111 | C2NC-1500-PRE | Instruments | Pre-Treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-3A | 3A | MS-A-LS111 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | BIOGAS | [5 empty] | Level switch |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Level switch |  | Analog | LS
Pre-Treatment Ball valve V130 | C2NC-1500-PRE-V_130 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V130 |  | NA | NA | NA | NA | CONDENSATE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | CONDENSATE | [5 empty] | Ball valve |  |  |  |  | CONDENSATE | [8 empty] | NA | CONDENSATE |  |  | Ball valve |  |  | V
Pre-Treatment Ball valve AV110 | C2NC-1500-PRE-AV_110 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: CONTROL CONDENSATE DRAIN | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-AV110 |  | NA | NA | NA | NA | CONDENSATE | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | CONDENSATE | [5 empty] | Ball valve |  |  |  |  | CONDENSATE | [8 empty] | NA | CONDENSATE |  |  | Ball valve |  |  | AV
Pre-Treatment Pneumatic actuator AV110 | C2NC-1500-PRE-AV_110 | C2NC-1500-PRE | Valves | Pre-Treatment Pneumatic actuator. Function: CONTROL CONDENSATE DRAIN | FLO-TITE | AIR-CON | [8 empty] | 9263-3A | 3A | MS-A-AV110 |  | NA | NA | NA | NA | CONDENSATE | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | CONDENSATE | [5 empty] | Pneumatic actuator |  |  |  |  | CONDENSATE | [8 empty] | NA | CONDENSATE |  |  | Pneumatic actuator |  |  | AV
Pre-Treatment Solenoid valve AV110 | C2NC-1500-PRE-AV_110 | C2NC-1500-PRE | Valves | Pre-Treatment Solenoid valve. Function: CONTROL CONDENSATE DRAIN | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-3A | 3A | MS-A-AV110 |  | 24 VDC | NA | NA | NA | CONDENSATE | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | CONDENSATE | [5 empty] | Solenoid valve |  |  |  |  | CONDENSATE | [8 empty] | 24 VDC | CONDENSATE |  |  | Solenoid valve |  | Digital | AV
Pre-Treatment Temperature transmitter TT110 | C2NC-1500-PRE-TT_110 | C2NC-1500-PRE | Instruments | Pre-Treatment Temperature transmitter. Function: MEASURE INLET TEMPERATURE BIOGAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-3A | 3A | MS-A-TT110 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Pre-Treatment Ball valve V102 | C2NC-1500-PRE-V_102 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: BLOCK GAS MEASUREMENT LINE | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V102 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Ball valve V110 | C2NC-1500-PRE-V_110 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V110 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Ball valve V103 | C2NC-1500-PRE-V_103 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: BLOCK PRESSURE TRANSMITTER | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-V103 |  | 24 VDC | NA | NA | NA | BIOGAS | - | - |  | Ball valve | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Pressure transmitter PT110 | C2NC-1500-PRE-PT_110 | C2NC-1500-PRE | Instruments | Pre-Treatment Pressure transmitter. Function: MEASURE INLET PRESSURE | Aerzen | PMC21-FA1V1HFVWJA+Z1 (E+H) | [8 empty] | 9263-3A | 3A | MS-A-PT110 |  | 24 VDC | NA | NA | NA | BIOGAS | - | - |  | Pressure transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Pre-Treatment Ball valve V104 | C2NC-1500-PRE-V_104 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: SAMPLE/DRAIN | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-V104 |  | NA | NA | NA | NA | BIOGAS | - | - |  | Ball valve | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Compensator BL110 | C2NC-1500-PRE-BL_110 | C2NC-1500-PRE | Equipment | Pre-Treatment Compensator. Function: PREVENT VIBRATIONS TO AFFECT BLOWER'S PIPE | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-BL110 |  | NA | NA | NA | NA | BIOGAS | - | - |  | Compensator | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Compensator |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Compensator |  |  | BL
Pre-Treatment Feed blower FB110 | C2NC-1500-PRE-FB_110 | C2NC-1500-PRE | Equipment | Pre-Treatment Feed blower. Function: BOOST BIOGAS PRESSURE | Aerzen | AERZEN GM 240 S Special Gas Blower | [8 empty] | 9263-3A | 3A | MS-A-FB110 |  | 480 VAC | NA | NA | NA | BIOGAS | 0 | 16" 150# |  | Feed blower | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Feed blower |  |  |  |  | BIOGAS | [8 empty] | 480 VAC | BIOGAS |  |  | Feed blower |  | Analog | FB
Pre-Treatment Check valve CV110 | C2NC-1500-PRE-CV_110 | C2NC-1500-PRE | Valves | Pre-Treatment Check valve. Function: PREVENT BACKFLOW | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-CV110 |  | NA | NA | NA | NA | BIOGAS | - | - |  | Check valve | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Pre-Treatment Compensator BL111 | C2NC-1500-PRE-BL_111 | C2NC-1500-PRE | Equipment | Pre-Treatment Compensator. Function: PREVENT VIBRATIONS TO AFFECT BLOWER'S PIPE | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-BL111 |  | NA | NA | NA | NA | BIOGAS | - | - |  | Compensator | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Compensator |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Compensator |  |  | BL
Pre-Treatment Temperature transmitter TT111 | C2NC-1500-PRE-TT_111 | C2NC-1500-PRE | Instruments | Pre-Treatment Temperature transmitter. Function: MEASURE INLET TEMPERATURE BIOGAS | Aerzen | TH13-2A11E1EBX1AK+A (E+H) | [8 empty] | 9263-3A | 3A | MS-A-TT111 |  | 24 VDC | NA | NA | NA | BIOGAS | - | - |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Pre-Treatment Ball valve V131 | C2NC-1500-PRE-V_131 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: BLOCK PRESSURE TRANSMITTER | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-V131 |  | NA | NA | NA | NA | BIOGAS | - | - |  | Ball valve | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Pressure transmitter PT130 | C2NC-1500-PRE-PT_130 | C2NC-1500-PRE | Instruments | Pre-Treatment Pressure transmitter. Function: MEASURE PRESSURE AFTER FEEDBLOWERS | Aerzen | PMC21-FA1V1KFVWJA+Z1 (E+H) | [8 empty] | 9263-3A | 3A | MS-A-PT130 |  | 24 VDC | NA | NA | NA | BIOGAS | - | - |  | Pressure transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Pre-Treatment Ball valve V132 | C2NC-1500-PRE-V_132 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: SAMPLE/DRAIN | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-V132 |  | NA | NA | NA | NA | BIOGAS | - | - |  | Ball valve | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Dry cooler heat exchanger HE130 | C2NC-1500-PRE-HE_130 | C2NC-1500-PRE | Equipment | Pre-Treatment Dry cooler heat exchanger. Function: COOL DOWN GAS | AXH Air-coolers | 93AZF | [8 empty] | 9263-3A | 3A | MS-A-HE130 |  | 0 | 0 | 0 | 0 | BIOGAS | AISI316 | 10" 150# |  | Dry cooler heat exchanger | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Dry cooler heat exchanger |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Dry cooler heat exchanger |  |  | HE
Pre-Treatment Enclosure fan FA110 | C2NC-1500-PRE-FA_110 | C2NC-1500-PRE | Equipment | Pre-Treatment Enclosure fan. Function: 0 | Toshiba | EQP Global 841, XT | [8 empty] | 9263-3A | 3A | MS-A-FA110 |  | 480 VAC | 0 | 0 | 0 | AIR | Composition of materials | NA |  | Enclosure fan | [7 empty] | 0 |  |  |  |  | AIR | [5 empty] | Enclosure fan |  |  |  |  | AIR | [8 empty] | 480 VAC | AIR |  |  | Enclosure fan |  | Digital | FA
Pre-Treatment Temperature transmitter TT120 | C2NC-1500-PRE-TT_120 | C2NC-1500-PRE | Instruments | Pre-Treatment Temperature transmitter. Function: MEASURE GAS TEMPERATURE | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-3A | 3A | MS-A-TT120 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Pre-Treatment Dry cooler fan FA130 | C2NC-1500-PRE-FA_130 | C2NC-1500-PRE | Equipment | Pre-Treatment Dry cooler fan. Function: COOL DOWN GAS | Aerzen | GM 10S 3" air package | [8 empty] | 9263-3A | 3A | MS-A-FA130 |  | 480 VAC | 0 | 0 | 0 | BIOGAS | Composition of materials | 10" 150# |  | Dry cooler fan | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Dry cooler fan |  |  |  |  | BIOGAS | [8 empty] | 480 VAC | BIOGAS |  |  | Dry cooler fan |  | Analog | FA
Pre-Treatment Vibration switch VS130 | C2NC-1500-PRE-VS_130 | C2NC-1500-PRE | Instruments | Pre-Treatment Vibration switch. Function: 0 | Murphy | Murphy VS 2EX, XP | [8 empty] | 9263-3A | 3A | MS-A-VS130 |  | 24 VDC | 0 | 0 | 0 | NA | Composition of materials | - |  | Vibration switch | [7 empty] | 0 |  |  |  |  | NA | [5 empty] | Vibration switch |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Vibration switch |  | Digital | VS
Pre-Treatment Ball valve V133 | C2NC-1500-PRE-V_133 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V133 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Heat exchanger HE140 | C2NC-1500-PRE-HE_140 | C2NC-1500-PRE | Equipment | Pre-Treatment Heat exchanger. Function: COOL DOWN GAS | Xchanger | Model C-425 | [8 empty] | 9263-3A | 3A | MS-A-HE140 |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 | 12" 150# (process) 1.1/2" (service) |  | Heat exchanger | [7 empty] | 15 lb/in2 |  |  |  |  | BIOGAS | [5 empty] | Heat exchanger |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Heat exchanger |  |  | HE
Pre-Treatment CONTROL VALVE AV130 | C2NC-1500-PRE-AV_130 | C2NC-1500-PRE | Valves | Pre-Treatment CONTROL VALVE. Function: Control recycle | FlowServe Valtek | GS General Purpose Control Valve / Flow Under / Cv: 208 / with Hood and Positioner | [8 empty] | 9263-3A | 3A | MS-A-AV130 |  | 0 | 0 | 0 | 0 | BIOGAS | A351-CF8M (SS) / PTFE Pack. | 4" 150# |  | CONTROL VALVE | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | CONTROL VALVE |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | CONTROL VALVE |  |  | AV
Pre-Treatment PNEUMATIC ACTUATOR AV130 | C2NC-1500-PRE-AV_130 | C2NC-1500-PRE | Valves | Pre-Treatment PNEUMATIC ACTUATOR. Function: Control recycle | FlowServe Valtek | 0 | [8 empty] | 9263-3A | 3A | MS-A-AV130 |  | 0 | 0 | 0 | 0 | AIR | ALU | NA |  | PNEUMATIC ACTUATOR | [7 empty] | 0 |  |  |  |  | AIR | [5 empty] | PNEUMATIC ACTUATOR |  |  |  |  | AIR | [8 empty] | 0 | AIR |  |  | PNEUMATIC ACTUATOR |  |  | AV
Pre-Treatment POSITIONER AV130 | C2NC-1500-PRE-AV_130 | C2NC-1500-PRE | Valves | Pre-Treatment POSITIONER. Function: Control recycle | FlowServe Logix 400 | Logix 400 Series Digital Positioner, Model 420-40-W1 D-11 | [8 empty] | 9263-3A | 3A | MS-A-AV130 |  | 24 VDC | 0 | 0 | 0 | AIR | ALU | NA |  | POSITIONER | [7 empty] | 0 |  |  |  |  | AIR | [5 empty] | POSITIONER |  |  |  |  | AIR | [8 empty] | 24 VDC | AIR |  |  | POSITIONER |  | Analog | AV
Pre-Treatment Pressure safety valve PZV130 | C2NC-1500-PRE-PZV_130 | C2NC-1500-PRE | Valves | Pre-Treatment Pressure safety valve. Function: SAFEGUARD PRESSURE | Leser | 5262T6654 | [8 empty] | 9263-3A | 3A | MS-A-PZV130 |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 | 6" 150# in / 8" 150# out |  | Pressure safety valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Pressure safety valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Pressure safety valve |  |  | PZV
Pre-Treatment Compensator BL130 | C2NC-1500-PRE-BL_130 | C2NC-1500-PRE | Equipment | Pre-Treatment Compensator. Function: PREVENT VIBRATIONS TO AFFECT BLOWER'S PIPE | Aerzen | - | [8 empty] | 9263-3A | 3A | MS-A-BL130 |  | NA | NA | NA | NA | BIOGAS | - | 16" 150# |  | Compensator | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Compensator |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Compensator |  |  | BL
Pre-Treatment Ball valve V138 | C2NC-1500-PRE-V_138 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V138 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Pre-Treatment Butterfly valve AV140 | C2NC-1500-PRE-AV_140 | C2NC-1500-PRE | Valves | Pre-Treatment Butterfly valve. Function: BLOCK OFF GAS FLOW | Emerson | Keystone Series GR RSBV; ASME 150 DI Lug Body | [8 empty] | 9263-3A | 3A | MS-A-AV140 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / HNBR | 14" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Butterfly valve |  |  | AV
Pre-Treatment Pneumatic actuator AV140 | C2NC-1500-PRE-AV_140 | C2NC-1500-PRE | Valves | Pre-Treatment Pneumatic actuator. Function: BLOCK OFF GAS FLOW | Emerson | Keystone F89U Rack and Pinion Actuator; | [8 empty] | 9263-3A | 3A | MS-A-AV140 |  | NA | NA | NA | NA | BIOGAS | Composition of materials | NA 150# |  | Pneumatic actuator | [7 empty] | 10 Barg - 140 Psig |  |  |  |  | BIOGAS | [5 empty] | Pneumatic actuator |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Pneumatic actuator |  |  | AV
Pre-Treatment Solenoid valve AV140 | C2NC-1500-PRE-AV_140 | C2NC-1500-PRE | Valves | Pre-Treatment Solenoid valve. Function: BLOCK OFF GAS FLOW | Asco | ASCO 8551 Solenoid Valve; 3-Way Aluminum Body | [8 empty] | 9263-3A | 3A | MS-A-AV140 |  | 24 VDC | NA | NA | NA | BIOGAS | Composition of materials | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Solenoid valve |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Solenoid valve |  | Digital | AV
Pre-Treatment Ball valve V135 | C2NC-1500-PRE-V_135 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V135 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Ball valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Pre-Treatment Butterfly valve V752 | C2NC-1500-PRE-V_752 | C2NC-1500-PRE | Valves | Pre-Treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Emerson | FIG 320 WAFER TRIM 112 | [8 empty] | 9263-3A | 3A | MS-A-V752 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Pre-Treatment Dearation valve DAV750 | C2NC-1500-PRE-DAV_750 | C2NC-1500-PRE | Equipment | Pre-Treatment Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO NPT | [8 empty] | 9263-3A | 3A | MS-A-DAV750 |  | NA | NA | NA | NA | GLYCOL MIXTURE | Brass | 1/2" FNPT |  | Dearation valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Dearation valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Dearation valve |  |  | DAV
Pre-Treatment Ball valve V753 | C2NC-1500-PRE-V_753 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V753 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Ball valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Pre-Treatment Butterfly valve V751 | C2NC-1500-PRE-V_751 | C2NC-1500-PRE | Valves | Pre-Treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Emerson | FIG 320 WAFER TRIM 112 | [8 empty] | 9263-3A | 3A | MS-A-V751 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Pre-Treatment Ball valve V743 | C2NC-1500-PRE-V_743 | C2NC-1500-PRE | Valves | Pre-Treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-3A | 3A | MS-A-V743 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Ball valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Pre-Treatment Butterfly valve V744 | C2NC-1500-PRE-V_744 | C2NC-1500-PRE | Valves | Pre-Treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Emerson | FIG 320 WAFER TRIM 112 | [8 empty] | 9263-3A | 3A | MS-A-V744 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Pre-Treatment Dearation valve DAV740 | C2NC-1500-PRE-DAV_740 | C2NC-1500-PRE | Equipment | Pre-Treatment Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO NPT | [8 empty] | 9263-3A | 3A | MS-A-DAV740 |  | NA | NA | NA | NA | GLYCOL MIXTURE | Brass | 1/2" FNPT |  | Dearation valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Dearation valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Dearation valve |  |  | DAV
Pre-Treatment Butterfly valve V745 | C2NC-1500-PRE-V_745 | C2NC-1500-PRE | Valves | Pre-Treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Emerson | FIG 320 WAFER TRIM 112 | [8 empty] | 9263-3A | 3A | MS-A-V745 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Active carbon vessels Pressure indicator transmitter PIT131 | C2NC-1500-ACV-PIT_131 | C2NC-1500-ACV | Instruments | Active carbon vessels Pressure indicator transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-3B | 3B | MS-A-PIT131 |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Active carbon vessels Temperature transmitter TT130 | C2NC-1500-ACV-TT_130 | C2NC-1500-ACV | Instruments | Active carbon vessels Temperature transmitter. Function: MEASURE INLET TEMPERATURE BIOGAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-3B | 3B | MS-A-TT130 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Active carbon vessels Butterfly valve V150A | C2NC-1500-ACV-V_150A | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V150A |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Ball valve V151A | C2NC-1500-ACV-V_151A | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: SAMPLE/DRAIN | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V151A |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Spectacle flange SF150A | C2NC-1500-ACV-SF_150A | C2NC-1500-ACV | Equipment | Active carbon vessels Spectacle flange. Function: BLOCK IN CARBON VESSEL | DMT | Spectacle blind flange | [8 empty] | 9263-3B | 3B | MS-A-SF150A |  | NA | NA | NA | NA | BIOGAS | AISI 316 | 20" 150# |  | Spectacle flange | [7 empty] | 10.3 Barg - 150 Psig |  |  |  |  | BIOGAS | [5 empty] | Spectacle flange |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Spectacle flange |  |  | SF
Active carbon vessels Ball valve V154A | C2NC-1500-ACV-V_154A | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: DRAIN | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V154A |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 2" NPT |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Carbon vessel CF150A | C2NC-1500-ACV-CF_150A | C2NC-1500-ACV | Tanks | Active carbon vessels Carbon vessel. Function: REMOVING POLLUTANTS FROM BIOGAS | Kuipers | according to drawing DMT | [8 empty] | 9263-3B | 3B | MS-A-CF150A |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 | 20" 150# |  | Carbon vessel | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Carbon vessel |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Carbon vessel |  |  | CF
Active carbon vessels Spectacle flange SF160A | C2NC-1500-ACV-SF_160A | C2NC-1500-ACV | Equipment | Active carbon vessels Spectacle flange. Function: BLOCK IN CARBON VESSEL | DMT | Spectacle blind flange | [8 empty] | 9263-3B | 3B | MS-A-SF160A |  | NA | NA | NA | NA | BIOGAS | AISI 316 | 20" 150# |  | Spectacle flange | [7 empty] | 10.3 Barg - 150 Psig |  |  |  |  | BIOGAS | [5 empty] | Spectacle flange |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Spectacle flange |  |  | SF
Active carbon vessels Ball valve V152A | C2NC-1500-ACV-V_152A | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK PRESSURE TRANSMITTER | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V152A |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Pressure transmitter PT150A | C2NC-1500-ACV-PT_150A | C2NC-1500-ACV | Instruments | Active carbon vessels Pressure transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-3B | 3B | MS-A-PT150A |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Active carbon vessels Pressure safety valve PZV150A | C2NC-1500-ACV-PZV_150A | C2NC-1500-ACV | Valves | Active carbon vessels Pressure safety valve. Function: SAFEGUARD PRESSURE | Leser | 52626652 | [8 empty] | 9263-3B | 3B | MS-A-PZV150A |  | 0 | 0 | 0 | 0 | BIOGAS | CS with SS internals | 6" 150# in / 8" 150# out |  | Pressure safety valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Pressure safety valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Pressure safety valve |  |  | PZV
Active carbon vessels Ball valve V155A | C2NC-1500-ACV-V_155A | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK INERTISATION LINE | Emerson | F155 three piece body ball valve | [8 empty] | 9263-3B | 3B | MS-A-V155A |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 2" NPT |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Ball valve V156A | C2NC-1500-ACV-V_156A | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK GAS MEASUREMENT LINE | Emerson | F120 two piece body ball valve | [8 empty] | 9263-3B | 3B | MS-A-V156A |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Butterfly valve V158A | C2NC-1500-ACV-V_158A | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V158A |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Butterfly valve V160A | C2NC-1500-ACV-V_160A | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V160A |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Butterfly valve V150B | C2NC-1500-ACV-V_150B | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V150B |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Ball valve V151B | C2NC-1500-ACV-V_151B | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: SAMPLE/DRAIN | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V151B |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Spectacle flange SF150B | C2NC-1500-ACV-SF_150B | C2NC-1500-ACV | Equipment | Active carbon vessels Spectacle flange. Function: BLOCK IN CARBON VESSEL | DMT | Spectacle blind flange | [8 empty] | 9263-3B | 3B | MS-A-SF150B |  | NA | NA | NA | NA | BIOGAS | AISI 316 | 20" 150# |  | Spectacle flange | [7 empty] | 10.3 Barg - 150 Psig |  |  |  |  | BIOGAS | [5 empty] | Spectacle flange |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Spectacle flange |  |  | SF
Active carbon vessels Ball valve V154B | C2NC-1500-ACV-V_154B | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: DRAIN | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V154B |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 2" NPT |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Carbon vessel CF150B | C2NC-1500-ACV-CF_150B | C2NC-1500-ACV | Tanks | Active carbon vessels Carbon vessel. Function: REMOVING POLLUTANTS FROM BIOGAS | Kuipers | according to drawing DMT | [8 empty] | 9263-3B | 3B | MS-A-CF150B |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 | 20" 150# |  | Carbon vessel | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Carbon vessel |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Carbon vessel |  |  | CF
Active carbon vessels Spectacle flange SF160B | C2NC-1500-ACV-SF_160B | C2NC-1500-ACV | Equipment | Active carbon vessels Spectacle flange. Function: BLOCK IN CARBON VESSEL | DMT | Spectacle blind flange | [8 empty] | 9263-3B | 3B | MS-A-SF160B |  | NA | NA | NA | NA | BIOGAS | AISI 316 | 20" 150# |  | Spectacle flange | [7 empty] | 10.3 Barg - 150 Psig |  |  |  |  | BIOGAS | [5 empty] | Spectacle flange |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Spectacle flange |  |  | SF
Active carbon vessels Ball valve V152B | C2NC-1500-ACV-V_152B | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK PRESSURE TRANSMITTER | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V152B |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Pressure transmitter PT150B | C2NC-1500-ACV-PT_150B | C2NC-1500-ACV | Instruments | Active carbon vessels Pressure transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-3B | 3B | MS-A-PT150B |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Active carbon vessels Pressure safety valve PZV150B | C2NC-1500-ACV-PZV_150B | C2NC-1500-ACV | Valves | Active carbon vessels Pressure safety valve. Function: SAFEGUARD PRESSURE | Leser | 52626652 | [8 empty] | 9263-3B | 3B | MS-A-PZV150B |  | 0 | 0 | 0 | 0 | BIOGAS | CS with SS internals | 6" 150# in / 8" 150# out |  | Pressure safety valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Pressure safety valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Pressure safety valve |  |  | PZV
Active carbon vessels Ball valve V155B | C2NC-1500-ACV-V_155B | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK INERTISATION LINE | Emerson | F155 three piece body ball valve | [8 empty] | 9263-3B | 3B | MS-A-V155B |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 2" NPT |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Ball valve V156B | C2NC-1500-ACV-V_156B | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK GAS MEASUREMENT LINE | Emerson | F120 two piece body ball valve | [8 empty] | 9263-3B | 3B | MS-A-V156B |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Butterfly valve V158B | C2NC-1500-ACV-V_158B | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V158B |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Butterfly valve V160B | C2NC-1500-ACV-V_160B | C2NC-1500-ACV | Valves | Active carbon vessels Butterfly valve. Function: BLOCK IN CARBON VESSEL | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-3B | 3B | MS-A-V160B |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Butterfly valve |  |  | V
Active carbon vessels Ball valve V160 | C2NC-1500-ACV-V_160 | C2NC-1500-ACV | Valves | Active carbon vessels Ball valve. Function: BLOCK PRESSURE TRANSMITTER | Emerson | K-Ball 2 piece ball valve F120 | [8 empty] | 9263-3B | 3B | MS-A-V160 |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 1/2" NPT (Female) |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Active carbon vessels Pressure transmitter PT160 | C2NC-1500-ACV-PT_160 | C2NC-1500-ACV | Instruments | Active carbon vessels Pressure transmitter. Function: MEASURE OUTLET PRESSURE | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-3B | 3B | MS-A-PT160 |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Active carbon vessels Temperature transmitter TT160 | C2NC-1500-ACV-TT_160 | C2NC-1500-ACV | Instruments | Active carbon vessels Temperature transmitter. Function: MEASURE OUTLET TEMPERATURE BIOGAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-3B | 3B | MS-A-TT160 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Feed gas compressor Ball valve V200 | C2NC-1500-FGC-V_200 | C2NC-1500-FGC | Valves | Feed gas compressor Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4A | 4A | MS-A-V200 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Feed gas compressor Butterfly valve V201 | C2NC-1500-FGC-V_201 | C2NC-1500-FGC | Valves | Feed gas compressor Butterfly valve. Function: Block Filter | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-4A | 4A | MS-A-V201 |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Butterfly valve |  |  | V
Feed gas compressor Filter F200 | C2NC-1500-FGC-F_200 | C2NC-1500-FGC | Equipment | Feed gas compressor Filter. Function: FILTER PARTICLES | Omega Air | GBF 3000 DN500 ASME - including filter elements 20 pcs. (76090 GP) 3µm | [8 empty] | 9263-4A | 4A | MS-A-F200 |  | 0 | 0 | 0 | 0 | BIOGAS | CS | 12" 150# |  | Filter | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Filter |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Filter |  |  | F
Feed gas compressor Gas compressor GC200 | C2NC-1500-FGC-GC_200 | C2NC-1500-FGC | Equipment | Feed gas compressor Gas compressor. Function: COMPRESS BIOGAS | Vilter | 0 | [8 empty] | 9263-4A | 4A | MS-A-GC200 |  | 4160 VAC | NA | NA | NA | BIOGAS | 0 | 0 |  | Gas compressor | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Gas compressor |  |  |  |  | BIOGAS | [8 empty] | 4160 VAC | BIOGAS |  |  | Gas compressor |  | Analog | GC
Feed gas compressor Check valve CV202 | C2NC-1500-FGC-CV_202 | C2NC-1500-FGC | Valves | Feed gas compressor Check valve. Function: 0 | Titan | CV 44-CS | [8 empty] | 9263-4A | 4A | MS-A-CV202 |  | 0 | 0 | 0 | 0 | BIOGAS | CS | 4" 300# |  | Check valve | [7 empty] | 740 Psi |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Check valve |  |  | CV
Feed gas compressor Butterfly valve V202 | C2NC-1500-FGC-V_202 | C2NC-1500-FGC | Valves | Feed gas compressor Butterfly valve. Function: 0 | ABZ valve | ABZolute 400 series lugged ANSI 300 | [8 empty] | 9263-4A | 4A | MS-A-V202 |  | 0 | 0 | 0 | 0 | BIOGAS | CS | 4" 300# |  | Butterfly valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Butterfly valve |  |  | V
Feed gas compressor Heat exchanger gas compressor HE200 | C2NC-1500-FGC-HE_200 | C2NC-1500-FGC | Equipment | Feed gas compressor Heat exchanger gas compressor. Function: COOL DOWND COOLING MEDIUM | Vilter | TTA545-6-90-1F78H-D | [8 empty] | 9263-4A | 4A | MS-A-HE200 |  | 0 | 0 | 0 | 0 | OIL | 0 | 0 |  | Heat exchanger gas compressor | [7 empty] | 0 |  |  |  |  | OIL | [5 empty] | Heat exchanger gas compressor |  |  |  |  | OIL | [8 empty] | 0 | OIL |  |  | Heat exchanger gas compressor |  |  | HE
Feed gas compressor Butterfly valve V211 | C2NC-1500-FGC-V_211 | C2NC-1500-FGC | Valves | Feed gas compressor Butterfly valve. Function: Block Filter | Emerson | Keystone GRL resilient seated butterfly valve | [8 empty] | 9263-4A | 4A | MA-A-V211 |  | 0 | 0 | 0 | 0 | BIOGAS | AISI 316 / NBR | 20" 150# |  | Butterfly valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Butterfly valve |  |  | V
Feed gas compressor Filter F210 | C2NC-1500-FGC-F_210 | C2NC-1500-FGC | Equipment | Feed gas compressor Filter. Function: FILTER PARTICLES | Omega Air | GBF 3000 DN500 ASME - including filter elements 20 pcs. (76090 GP) 3µm | [8 empty] | 9263-4A | 4A | MS-A-F210 |  | 0 | 0 | 0 | 0 | BIOGAS | CS | 12" 150# |  | Filter | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Filter |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Filter |  |  | F
Feed gas compressor Gas compressor GC210 | C2NC-1500-FGC-GC_210 | C2NC-1500-FGC | Equipment | Feed gas compressor Gas compressor. Function: COMPRESS BIOGAS | Vilter | 0 | [8 empty] | 9263-4A | 4A | MS-A-GC210 |  | 4160 VAC | NA | NA | NA | BIOGAS | 0 | 0 |  | Gas compressor | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Gas compressor |  |  |  |  | BIOGAS | [8 empty] | 4160 VAC | BIOGAS |  |  | Gas compressor |  | Analog | GC
Feed gas compressor Check valve CV212 | C2NC-1500-FGC-CV_212 | C2NC-1500-FGC | Valves | Feed gas compressor Check valve. Function: 0 | Titan | CV 44-CS | [8 empty] | 9263-4A | 4A | MS-A-CV212 |  | 0 | 0 | 0 | 0 | BIOGAS | CS | 4" 300# |  | Check valve | [7 empty] | 740 Psi |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Check valve |  |  | CV
Feed gas compressor Butterfly valve V212 | C2NC-1500-FGC-V_212 | C2NC-1500-FGC | Valves | Feed gas compressor Butterfly valve. Function: 0 | ABZ valve | ABZolute 400 series lugged ANSI 300 | [8 empty] | 9263-4A | 4A | MS-A-V212 |  | 0 | 0 | 0 | 0 | BIOGAS | CS | 4" 300# |  | Butterfly valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Butterfly valve |  |  | V
Feed gas compressor Heat exchanger gas compressor HE210 | C2NC-1500-FGC-HE_210 | C2NC-1500-FGC | Equipment | Feed gas compressor Heat exchanger gas compressor. Function: COOL DOWND COOLING MEDIUM | Vilter | TTA545-6-90-1F78H-D | [8 empty] | 9263-4A | 4A | MS-A-HE210 |  | 0 | 0 | 0 | 0 | OIL | 0 | 0 |  | Heat exchanger gas compressor | [7 empty] | 0 |  |  |  |  | OIL | [5 empty] | Heat exchanger gas compressor |  |  |  |  | OIL | [8 empty] | 0 | OIL |  |  | Heat exchanger gas compressor |  |  | HE
Compressed gas treatment Ball valve AV304 | C2NC-1500-CGT-AV_304 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN CONDENSATE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-AV304 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | AV
Compressed gas treatment Pneumatic actuator AV304 | C2NC-1500-CGT-AV_304 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: DRAIN CONDENSATE | Air Con | Air Con CSR63 | [8 empty] | 9263-4B | 4B | MS-A-AV304 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Solenoid valve AV304 | C2NC-1500-CGT-AV_304 | C2NC-1500-CGT | Valves | Compressed gas treatment Solenoid valve. Function: DRAIN CONDENSATE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4B | 4B | MS-A-AV304 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Compressed gas treatment Ball valve V306 | C2NC-1500-CGT-V_306 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V306 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Dry cooler heat exchanger HE300 | C2NC-1500-CGT-HE_300 | C2NC-1500-CGT | Equipment | Compressed gas treatment Dry cooler heat exchanger. Function: COOL DOWN GAS | Vilter | TTS440-8-123-1F78H-P | [8 empty] | 9263-4B | 4B | MS-A-HE300 |  | 0 | NA | NA | NA | BIOGAS | 0 | 6" 300# |  | Dry cooler heat exchanger | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Dry cooler heat exchanger |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Dry cooler heat exchanger |  |  | HE
Compressed gas treatment Dry Cooler Fan (in Vilter package) FA300 | C2NC-1500-CGT-FA_300 | C2NC-1500-CGT | Equipment | Compressed gas treatment Dry Cooler Fan (in Vilter package). Function: COOL DOWN GAS | Vilter | STAMP | [8 empty] | 9263-4B | 4B | MS-A-FA300 |  | 480 VAC | NA | NA | NA | BIOGAS | 0 | NA |  | Dry Cooler Fan (in Vilter package) | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Dry Cooler Fan (in Vilter package) |  |  |  |  | BIOGAS | [8 empty] | 480 VAC | BIOGAS |  |  | Dry Cooler Fan (in Vilter package) |  | Analog | FA
Compressed gas treatment Temperature transmitter TT300 | C2NC-1500-CGT-TT_300 | C2NC-1500-CGT | Instruments | Compressed gas treatment Temperature transmitter. Function: Measure inlet temperature | Vilter | - | [8 empty] | 9263-4B | 4B | MS-A-TT300 |  | 24 VDC | 0 | 0 | 0 | BIOGAS | - | - |  | Temperature transmitter | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Compressed gas treatment Temperature transmitter TT310 | C2NC-1500-CGT-TT_310 | C2NC-1500-CGT | Instruments | Compressed gas treatment Temperature transmitter. Function: Measure outlet temperature | Vilter | - | [8 empty] | 9263-4B | 4B | MS-A-TT310 |  | 24 VDC | 0 | 0 | 0 | BIOGAS | - | - |  | Temperature transmitter | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Compressed gas treatment Ball valve AV310 | C2NC-1500-CGT-AV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN CONDENSATE TO CLIENT | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-AV310 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | AV
Compressed gas treatment Pneumatic actuator AV310 | C2NC-1500-CGT-AV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: DRAIN CONDENSATE TO CLIENT | Air Con | Air Con CSR63 | [8 empty] | 9263-4B | 4B | MS-A-AV310 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Solenoid valve AV310 | C2NC-1500-CGT-AV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Solenoid valve. Function: DRAIN CONDENSATE TO CLIENT | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4B | 4B | MS-A-AV310 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Compressed gas treatment Ball valve AV314 | C2NC-1500-CGT-AV_314 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN CONDENSATE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-AV314 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | AV
Compressed gas treatment Pneumatic actuator AV314 | C2NC-1500-CGT-AV_314 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: DRAIN CONDENSATE | Air Con | Air Con CSR63 | [8 empty] | 9263-4B | 4B | MS-A-AV314 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Water separator WS300 | C2NC-1500-CGT-WS_300 | C2NC-1500-CGT | Equipment | Compressed gas treatment Water separator. Function: SEPARATE CONDENSED WATER | Omega Air | SFH SS 088 PN20 6" Cl.300 SS304 - ASME - Including filter element SFH 088 SS : cyclone is welded inside | [8 empty] | 9263-4B | 4B | MS-A-WS300 |  | NA | NA | NA | NA | BIOGAS | AISI 304 | 6" #300 |  | Water separator | [7 empty] | 360 PSIG @212°F |  |  |  |  | BIOGAS | [5 empty] | Water separator |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Water separator |  |  | WS
Compressed gas treatment Filter (Water separator) F310 | C2NC-1500-CGT-F_310 | C2NC-1500-CGT | Equipment | Compressed gas treatment Filter (Water separator). Function: SEPARATE CONDENSED WATER | Omega Air | WHFIF 900 6" SS304 - ASME - Including filter elements: 1 x 3 pcs.(PN 3030) 5µm | [8 empty] | 9263-4B | 4B | MS-A-F310 |  | NA | NA | NA | NA | BIOGAS | AISI 304 | 6" #300 |  | Filter (Water separator) | [7 empty] | 360 PSIG @212°F |  |  |  |  | BIOGAS | [5 empty] | Filter (Water separator) |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Filter (Water separator) |  |  | F
Compressed gas treatment Filter F320 | C2NC-1500-CGT-F_320 | C2NC-1500-CGT | Equipment | Compressed gas treatment Filter. Function: FILTER PARTICLES | Omega Air | WHFIF 900 6" SS304 - ASME - Including filter elements : 2 x 3 pcs. (PR 3030) 1µm | [8 empty] | 9263-4B | 4B | MS-A-F320 |  | NA | NA | NA | NA | BIOGAS | AISI 304 | 6" #300 |  | Filter | [7 empty] | 290 PSIG @212°F |  |  |  |  | BIOGAS | [5 empty] | Filter |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Filter |  |  | F
Compressed gas treatment Filter F330 | C2NC-1500-CGT-F_330 | C2NC-1500-CGT | Equipment | Compressed gas treatment Filter. Function: FILTER PARTICLES | Omega Air | WHFIF 900 6" SS304 - ASME - Including filter elements : 2 x 3 pcs. (PM 3030) 0,1µm | [8 empty] | 9263-4B | 4B | MS-A-F330 |  | NA | NA | NA | NA | BIOGAS | AISI 304 | 6" #300 |  | Filter | [7 empty] | 290 PSIG @212°F |  |  |  |  | BIOGAS | [5 empty] | Filter |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Filter |  |  | F
Compressed gas treatment Solenoid valve AV314 | C2NC-1500-CGT-AV_314 | C2NC-1500-CGT | Valves | Compressed gas treatment Solenoid valve. Function: DRAIN CONDENSATE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4B | 4B | MS-A-AV314 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Compressed gas treatment Control valve AV340 | C2NC-1500-CGT-AV_340 | C2NC-1500-CGT | Valves | Compressed gas treatment Control valve. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | Conovalve | S803 - D Control Valve 6"- ANSI CLASS 300 AV340 | [8 empty] | 9263-4B | 4B | MS-A-AV340 |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 6" #300 |  | Control valve | [7 empty] | ASME CLASS 300 |  |  |  |  | BIOGAS | [5 empty] | Control valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Control valve |  |  | AV
Compressed gas treatment Pneumatic actuator AV340 | C2NC-1500-CGT-AV_340 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | S430/I | [8 empty] | 9263-4B | 4B | MS-A-AV340 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Control unit/ positioner AV340 | C2NC-1500-CGT-AV_340 | C2NC-1500-CGT | Valves | Compressed gas treatment Control unit/ positioner. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | V200E-IS (using Non Incendive Field Wiring for use without barrier in Class I Div.2 !! | [8 empty] | 9263-4B | 4B | MS-A-AV340 |  | 24 VDC | NA | NA | NA | COMPRESSED AIR | NA | NA |  | Control unit/ positioner | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Control unit/ positioner |  |  |  |  | COMPRESSED AIR | [8 empty] | 24 VDC | COMPRESSED AIR |  |  | Control unit/ positioner |  | Analog | AV
Compressed gas treatment Ball valve AV324 | C2NC-1500-CGT-AV_324 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN CONDENSATE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-AV324 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | AV
Compressed gas treatment Pneumatic actuator AV324 | C2NC-1500-CGT-AV_324 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: DRAIN CONDENSATE | Air Con | Air Con CSR63 | [8 empty] | 9263-4B | 4B | MS-A-AV324 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Solenoid valve AV324 | C2NC-1500-CGT-AV_324 | C2NC-1500-CGT | Valves | Compressed gas treatment Solenoid valve. Function: DRAIN CONDENSATE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4B | 4B | MS-A-AV324 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Compressed gas treatment Ball valve AV334 | C2NC-1500-CGT-AV_334 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN CONDENSATE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-AV334 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | AV
Compressed gas treatment Filter F350 | C2NC-1500-CGT-F_350 | C2NC-1500-CGT | Equipment | Compressed gas treatment Filter. Function: FILTER PARTICLES | Omega Air | WHFIF 900 6"SS304 - ASME - Including filter elements : 2 x 3 pcs. (PR 3030) 1µm | [8 empty] | 9263-4B | 4B | MS-A-F350 |  | NA | NA | NA | NA | BIOGAS | AISI 304 | 6" #300 |  | Filter | [7 empty] | 290 PSIG @212°F |  |  |  |  | BIOGAS | [5 empty] | Filter |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Filter |  |  | F
Compressed gas treatment Pneumatic actuator AV334 | C2NC-1500-CGT-AV_334 | C2NC-1500-CGT | Valves | Compressed gas treatment Pneumatic actuator. Function: DRAIN CONDENSATE | Air Con | Air Con CSR63 | [8 empty] | 9263-4B | 4B | MS-A-AV334 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Compressed gas treatment Filter F360 | C2NC-1500-CGT-F_360 | C2NC-1500-CGT | Equipment | Compressed gas treatment Filter. Function: FILTER PARTICLES | Omega Air | WHFIF 900 6" SS304 - ASME - Including filter elements : 2 x 3 pcs. (PS 3030) 0,01µm | [8 empty] | 9263-4B | 4B | MS-A-F360 |  | NA | NA | NA | NA | BIOGAS | AISI 304 | 6" #300 |  | Filter | [7 empty] | 290 PSIG @212°F |  |  |  |  | BIOGAS | [5 empty] | Filter |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Filter |  |  | F
Compressed gas treatment Solenoid valve AV334 | C2NC-1500-CGT-AV_334 | C2NC-1500-CGT | Valves | Compressed gas treatment Solenoid valve. Function: DRAIN CONDENSATE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4B | 4B | MS-A-AV334 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV400 | C2NC-1500-MBR-AV_400 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANES | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV400 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV400 | C2NC-1500-MBR-AV_400 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANES | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV400 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV400 | C2NC-1500-MBR-AV_400 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANES | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV400 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV401 | C2NC-1500-MBR-AV_401 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: ISOLATE PERMEATE SIDE MEMBRANES | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV401 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV401 | C2NC-1500-MBR-AV_401 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: ISOLATE PERMEATE SIDE MEMBRANES | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV401 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV401 | C2NC-1500-MBR-AV_401 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: ISOLATE PERMEATE SIDE MEMBRANES | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV401 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.01 | C2NC-1500-MBR-AV_411.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.01 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.01 | C2NC-1500-MBR-AV_411.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.01 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.01 | C2NC-1500-MBR-AV_411.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.01 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.02 | C2NC-1500-MBR-AV_411.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.02 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.02 | C2NC-1500-MBR-AV_411.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.02 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.02 | C2NC-1500-MBR-AV_411.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.02 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.03 | C2NC-1500-MBR-AV_411.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.03 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.03 | C2NC-1500-MBR-AV_411.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.03 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.03 | C2NC-1500-MBR-AV_411.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.03 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.04 | C2NC-1500-MBR-AV_411.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.04 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.04 | C2NC-1500-MBR-AV_411.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.04 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.04 | C2NC-1500-MBR-AV_411.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.04 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.05 | C2NC-1500-MBR-AV_411.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.05 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.05 | C2NC-1500-MBR-AV_411.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.05 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.05 | C2NC-1500-MBR-AV_411.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.05 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.06 | C2NC-1500-MBR-AV_411.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.06 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.06 | C2NC-1500-MBR-AV_411.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.06 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.06 | C2NC-1500-MBR-AV_411.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.06 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.07 | C2NC-1500-MBR-AV_411.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.07 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.07 | C2NC-1500-MBR-AV_411.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.07 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.07 | C2NC-1500-MBR-AV_411.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.07 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.08 | C2NC-1500-MBR-AV_411.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.08 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.08 | C2NC-1500-MBR-AV_411.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.08 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.08 | C2NC-1500-MBR-AV_411.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.08 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV411.09 | C2NC-1500-MBR-AV_411.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: PRESSURIZE MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.09 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV411.09 | C2NC-1500-MBR-AV_411.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: PRESSURIZE MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.09 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV411.09 | C2NC-1500-MBR-AV_411.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: PRESSURIZE MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV411.09 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.01 | C2NC-1500-MBR-AV_412.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.01 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.01 | C2NC-1500-MBR-AV_412.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.01 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.01 | C2NC-1500-MBR-AV_412.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.01 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.02 | C2NC-1500-MBR-AV_412.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.02 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.02 | C2NC-1500-MBR-AV_412.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.02 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.02 | C2NC-1500-MBR-AV_412.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.02 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.03 | C2NC-1500-MBR-AV_412.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.03 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.03 | C2NC-1500-MBR-AV_412.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.03 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.03 | C2NC-1500-MBR-AV_412.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.03 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.04 | C2NC-1500-MBR-AV_412.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.04 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.04 | C2NC-1500-MBR-AV_412.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.04 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.04 | C2NC-1500-MBR-AV_412.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.04 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.05 | C2NC-1500-MBR-AV_412.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.05 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.05 | C2NC-1500-MBR-AV_412.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.05 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.05 | C2NC-1500-MBR-AV_412.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.05 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.06 | C2NC-1500-MBR-AV_412.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.06 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.06 | C2NC-1500-MBR-AV_412.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.06 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.06 | C2NC-1500-MBR-AV_412.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.06 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.07 | C2NC-1500-MBR-AV_412.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.07 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.07 | C2NC-1500-MBR-AV_412.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.07 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.07 | C2NC-1500-MBR-AV_412.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.07 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.08 | C2NC-1500-MBR-AV_412.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.08 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.08 | C2NC-1500-MBR-AV_412.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.08 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.08 | C2NC-1500-MBR-AV_412.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.08 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes stage 1 Ball valve AV412.09 | C2NC-1500-MBR-AV_412.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: BLOCK MEMBRANE | FLO-TITE | Multi-Choice 300 Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.09 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" SW / BW |  | Ball valve | [7 empty] | 69 Barg - 1000 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes stage 1 Pneumatic actuator AV412.09 | C2NC-1500-MBR-AV_412.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Pneumatic actuator. Function: BLOCK MEMBRANE | Air Con | Air Con CSR63 | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.09 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes stage 1 Solenoid valve AV412.09 | C2NC-1500-MBR-AV_412.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Solenoid valve. Function: BLOCK MEMBRANE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C1 | 4C1 | MS-A-AV412.09 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Membranes Butterfly valve AV551 | C2NC-1500-MBR-AV_551 | C2NC-1500-MBR | Valves | Membranes Butterfly valve. Function: PROTECT FLARE | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C | 4C | MS-A-AV551 |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 6" 300# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Butterfly valve |  |  | AV
Membranes Pneumatic actuator AV551 | C2NC-1500-MBR-AV_551 | C2NC-1500-MBR | Valves | Membranes Pneumatic actuator. Function: PROTECT FLARE | Xomox | SR-FC | [8 empty] | 9263-4C | 4C | MS-A-AV551 |  | NA | NA | NA | NA | BIOGAS | ALU | NA |  | Pneumatic actuator | [7 empty] | 10 Barg - 140 Psig |  |  |  |  | BIOGAS | [5 empty] | Pneumatic actuator |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Pneumatic actuator |  |  | AV
Membranes Solenoid valve AV551 | C2NC-1500-MBR-AV_551 | C2NC-1500-MBR | Valves | Membranes Solenoid valve. Function: PROTECT FLARE | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C | 4C | MS-A-AV551 |  | 24 VDC | NA | NA | NA | BIOGAS | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Solenoid valve |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Solenoid valve |  | Digital | AV
Membranes Ball valve AV620 | C2NC-1500-MBR-AV_620 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK BY PASS | FLO-TITE | FULL-FLO SERIES | [8 empty] | 9263-4C | 4C | MS-A-AV620 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 2" 150# |  | Ball valve | [7 empty] | 280 Psig |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | AV
Membranes Pneumatic actuator AV620 | C2NC-1500-MBR-AV_620 | C2NC-1500-MBR | Valves | Membranes Pneumatic actuator. Function: BLOCK BY PASS | Air Con | CSR52 | [8 empty] | 9263-4C | 4C | MS-A-AV620 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | 10 Barg - 140 Psig |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes Solenoid valve AV620 | C2NC-1500-MBR-AV_620 | C2NC-1500-MBR | Valves | Membranes Solenoid valve. Function: BLOCK BY PASS | Asco | solenoid EF8551G401MO.24/DC (FM - Explosion Proof) | [8 empty] | 9263-4C | 4C | MS-A-AV620 |  | 24 VDC | NA | NA | NA | NA | ALU | NA |  | Solenoid valve | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Solenoid valve |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Solenoid valve |  | Digital | AV
Compressed gas treatment Buffer vessel BV310 | C2NC-1500-CGT-BV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Buffer vessel. Function: COLLECT CONDENSATE | Fabricator | according to drawing DMT | [8 empty] | 9263-4B | 4B | MS-A-BV310 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 | 6" sch 80 |  | Buffer vessel | [7 empty] | 300 PSIG |  |  |  |  | PROCESSS WATER | [5 empty] | Buffer vessel |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Buffer vessel |  |  | BV
Compressed gas treatment Carbon filter CF340 | C2NC-1500-CGT-CF_340 | C2NC-1500-CGT | Tanks | Compressed gas treatment Carbon filter. Function: REMOVE RESIDUAL OIL | Apache | according to drawing DMT | [8 empty] | 9263-4B | 4B | MS-A-CF340 |  | NA | NA | NA | NA | BIOGAS | AISI 304 | 6" #300 |  | Carbon filter | [7 empty] | 300 Psig |  |  |  |  | BIOGAS | [5 empty] | Carbon filter |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Carbon filter |  |  | CF
Compressed gas treatment Check valve CV310 | C2NC-1500-CGT-CV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Check valve. Function: PREVENT BACKFLOW | Swagelok | C Series | [8 empty] | 9263-4B | 4B | MS-A-CV310 |  | NA | NA | NA | NA | PROCESS WATER | AISI 316L / FKM | 1/2" SWAGELOK |  | Check valve | [7 empty] | 3000 PSIG @ 100°F |  |  |  |  | PROCESS WATER | [5 empty] | Check valve |  |  |  |  | PROCESS WATER | [8 empty] | NA | PROCESS WATER |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.01 | C2NC-1500-MBR-CV_413.01 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.01 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.02 | C2NC-1500-MBR-CV_413.02 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.02 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.03 | C2NC-1500-MBR-CV_413.03 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.03 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.04 | C2NC-1500-MBR-CV_413.04 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.04 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.05 | C2NC-1500-MBR-CV_413.05 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.05 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.06 | C2NC-1500-MBR-CV_413.06 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.06 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.07 | C2NC-1500-MBR-CV_413.07 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.07 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.08 | C2NC-1500-MBR-CV_413.08 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.08 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.09 | C2NC-1500-MBR-CV_413.09 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.09 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.10 | C2NC-1500-MBR-CV_413.10 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.10 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.11 | C2NC-1500-MBR-CV_413.11 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.11 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.12 | C2NC-1500-MBR-CV_413.12 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.12 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.13 | C2NC-1500-MBR-CV_413.13 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.13 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes stage 1 Check valve CV413.14 | C2NC-1500-MBR-CV_413.14 | C2NC-1500-MBR | Valves | Membranes stage 1 Check valve. Function: PREVENT BACKFLOW TO MEMBRANES | Swagelok | CH Series | [8 empty] | 9263-4C1 | 4C1 | MS-A-CV413.14 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1" Swagelok |  | Check valve | [7 empty] | 4700PSIG @ 100 ºF |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes Check valve CV510 | C2NC-1500-MBR-CV_510 | C2NC-1500-MBR | Valves | Membranes Check valve. Function: PREVENT BACKFLOW FROM PRODUCT GAS | Champion Valves Inc | Double disc spring loaded wafer check valve | [8 empty] | 9263-4C | 4C | MS-A-CV510 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / NBR | 6" #300 |  | Check valve | [7 empty] | 300 PSIG |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes Check valve CV520 | C2NC-1500-MBR-CV_520 | C2NC-1500-MBR | Valves | Membranes Check valve. Function: PREVENT BACKFLOW | Champion Valves Inc | Double disc spring loaded wafer check valve | [8 empty] | 9263-4C | 4C | MS-A-CV520 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / NBR | 8" #300 |  | Check valve | [7 empty] | 300 PSIG |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Membranes Check valve CV631 | C2NC-1500-MBR-CV_631 | C2NC-1500-MBR | Valves | Membranes Check valve. Function: PREVENT BACKFLOW | Champion Valves Inc | CV 12-SS | [8 empty] | 9263-4C | 4C | MS-A-CV631 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / NBR | 12" 150# |  | Check valve | [7 empty] | 300 PSIG |  |  |  |  | BIOGAS | [5 empty] | Check valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Check valve |  |  | CV
Compressed gas treatment Dearation valve DAV741 | C2NC-1500-CGT-DAV_741 | C2NC-1500-CGT | Equipment | Compressed gas treatment Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO NPT | [8 empty] | 9263-4B | 4B | MS-A-DAV741 |  | NA | NA | NA | NA | GLYCOL MIXTURE | Brass | 1/2" FNPT |  | Dearation valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Dearation valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Dearation valve |  |  | DAV
Container unit Emergency stop ES912 | C2NC-1500-CU-ES_912 | C2NC-1500-CU | Instruments | Container unit Emergency stop. Function: STOP INSTALLATION | Square D Schneider | Mushroom type, color Red, manual pull-release | [8 empty] | 9263-4F | 4F | MS-A-ES912 |  | 24 VDC | NA | NA | NA | NA | NA | NA |  | Emergency stop | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Emergency stop |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Emergency stop |  |  | ES
Container unit Emergency stop ES913 | C2NC-1500-CU-ES_913 | C2NC-1500-CU | Instruments | Container unit Emergency stop. Function: STOP INSTALLATION | Square D Schneider | Mushroom type, color Red, manual pull-release | [8 empty] | 9263-4F | 4F | MS-A-ES913 |  | 24 VDC | NA | NA | NA | NA | NA | NA |  | Emergency stop | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Emergency stop |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Emergency stop |  |  | ES
Container unit Fan FA910 | C2NC-1500-CU-FA_910 | C2NC-1500-CU | Equipment | Container unit Fan. Function: AIR VENTILATION CONTAINER | PennBarry | Penn Barry DX18B with 1/3 HP and 675 RPM | [8 empty] | 9263-4F | 4F | MS-A-FA910 |  | 480 VAC | NA | NA | NA | AMBIENT AIR | Composition of materials | 0 |  | Fan | [7 empty] | 0 |  |  |  |  | AMBIENT AIR | [5 empty] | Fan |  |  |  |  | AMBIENT AIR | [8 empty] | 480 VAC | AMBIENT AIR |  |  | Fan |  |  | FA
Membranes Flow indicator transmitter FIT500 | C2NC-1500-MBR-FIT_500 | C2NC-1500-MBR | Instruments | Membranes Flow indicator transmitter. Function: MEASURE FLOW OF PRODUCT GAS | Endress & Hauser | Promass 40E50 | [8 empty] | 9263-4C | 4C | MS-A-FIT500 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316 | 2" 300# |  | Flow indicator transmitter | [7 empty] | 1450 PSIG |  |  |  |  | BIOGAS | [5 empty] | Flow indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Flow indicator transmitter |  | Analog | FIT
Membranes Flow indicator transmitter FIT520 | C2NC-1500-MBR-FIT_520 | C2NC-1500-MBR | Instruments | Membranes Flow indicator transmitter. Function: MEASURE FLOW TO STACK | Endress & Hauser | T-mass 65I | [8 empty] | 9263-4C | 4C | MS-A-FIT520 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316 | 1" NPT in 8" pipe |  | Flow indicator transmitter | [7 empty] | 290 PSIG |  |  |  |  | BIOGAS | [5 empty] | Flow indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Flow indicator transmitter |  | Analog | FIT
Container unit Flow switch FS910 | C2NC-1500-CU-FS_910 | C2NC-1500-CU | Instruments | Container unit Flow switch. Function: CONFIRM AIR FLOW | Ameritrol | FX-1000-D, 1 MNPT, 1.8 probe | [8 empty] | 9263-4F | 4F | MS-A-FS910 |  | 24 VDC | NA | NA | NA | AMBIENT AIR | NA | NA |  | Flow switch | [7 empty] | 0 |  |  |  |  | AMBIENT AIR | [5 empty] | Flow switch |  |  |  |  | AMBIENT AIR | [8 empty] | 24 VDC | AMBIENT AIR |  |  | Flow switch |  | Digital | FS
Container unit Grid GR910 | C2NC-1500-CU-GR_910 | C2NC-1500-CU | Equipment | Container unit Grid. Function: Air outlet | PennBarry | part of FA910 | [8 empty] | 9263-4F | 4F | MS-A-GR910 |  | NA | NA | NA | NA | Ambient air | Aluminium | 0 |  | Grid | [7 empty] | NA |  |  |  |  | Ambient air | [5 empty] | Grid |  |  |  |  | Ambient air | [8 empty] | NA | Ambient air |  |  | Grid |  |  | GR
Container unit Grid GR911 | C2NC-1500-CU-GR_911 | C2NC-1500-CU | Equipment | Container unit Grid. Function: Air outlet | PennBarry | part of FA910 | [8 empty] | 9263-4F | 4F | MS-A-GR911 |  | NA | NA | NA | NA | Ambient air | Aluminium | 0 |  | Grid | [7 empty] | NA |  |  |  |  | Ambient air | [5 empty] | Grid |  |  |  |  | Ambient air | [8 empty] | NA | Ambient air |  |  | Grid |  |  | GR
Container unit Grid GR914 | C2NC-1500-CU-GR_914 | C2NC-1500-CU | Equipment | Container unit Grid. Function: Air inlet | Greenhack | EACA-601 24x24" | [8 empty] | 9263-4F | 4F | MS-A-GR914 |  | NA | NA | NA | NA | Ambient air | Aluminium | 24x24" |  | Grid | [7 empty] | NA |  |  |  |  | Ambient air | [5 empty] | Grid |  |  |  |  | Ambient air | [8 empty] | NA | Ambient air |  |  | Grid |  |  | GR
Container unit Grid GR915 | C2NC-1500-CU-GR_915 | C2NC-1500-CU | Equipment | Container unit Grid. Function: Air inlet | Greenhack | EACA-601 24x24" | [8 empty] | 9263-4F | 4F | MS-A-GR915 |  | NA | NA | NA | NA | Ambient air | Aluminium | 24x24" |  | Grid | [7 empty] | NA |  |  |  |  | Ambient air | [5 empty] | Grid |  |  |  |  | Ambient air | [8 empty] | NA | Ambient air |  |  | Grid |  |  | GR
Compressed gas treatment Heat exchanger HE310 | C2NC-1500-CGT-HE_310 | C2NC-1500-CGT | Equipment | Compressed gas treatment Heat exchanger. Function: COOL DOWN GAS | Swep | B427Lx314/1P-SC-S 4x4"VIC + 28259 SUPPORT LEGS + 22266 | [8 empty] | 9263-4B | 4B | MS-A-HE310 |  | NA | NA | NA | NA | BIOGAS | 0 | 4" VIC |  | Heat exchanger | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Heat exchanger |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Heat exchanger |  |  | HE
Compressed gas treatment Heat exchanger HE340 | C2NC-1500-CGT-HE_340 | C2NC-1500-CGT | Equipment | Compressed gas treatment Heat exchanger. Function: COOL DOWN GAS | Swep | B65Lx242/1P-SC-S 4x4"VIC + SUPPORT LEG + 22266 ASME U | [8 empty] | 9263-4B | 4B | MS-A-HE340 |  | NA | NA | NA | NA | BIOGAS | 0 | 4" VIC |  | Heat exchanger | [7 empty] | 30 Barg - 435 Psig |  |  |  |  | BIOGAS | [5 empty] | Heat exchanger |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Heat exchanger |  |  | HE
Compressed gas treatment Heat exchanger HE460 | C2NC-1500-CGT-HE_460 | C2NC-1500-CGT | Equipment | Compressed gas treatment Heat exchanger. Function: COOL DOWN GAS | Swep | B65Lx248/1P-SC-S 4x4"VIC + SUPPORT LEGS + 22266 ASME U | [8 empty] | 9263-4B | 4B | MS-A-HE460 |  | NA | NA | NA | NA | BIOGAS | 0 | 4" VIC |  | Heat exchanger | [7 empty] | 30 Barg - 435 Psig |  |  |  |  | BIOGAS | [5 empty] | Heat exchanger |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Heat exchanger |  |  | HE
Container unit Heater (switches as one with /912 & /913) HE911 | C2NC-1500-CU-HE_911 | C2NC-1500-CU | Equipment | Container unit Heater (switches as one with /912 & /913). Function: HEATING CONTROL ROOM | Markel | Hazardous Location WALL CONVECTOR heaters | [8 empty] | 9263-4F | 4F | MS-A-HE911 |  | 480 VAC | NA | NA | NA | AMBIENT AIR | 0 | 0 |  | Heater (switches as one with /912 & /913) | [7 empty] | 0 |  |  |  |  | AMBIENT AIR | [5 empty] | Heater (switches as one with /912 & /913) |  |  |  |  | AMBIENT AIR | [8 empty] | 480 VAC | AMBIENT AIR |  |  | Heater (switches as one with /912 & /913) |  |  | HE
Container unit Heater (switches as one with /911 & /913) HE912 | C2NC-1500-CU-HE_912 | C2NC-1500-CU | Equipment | Container unit Heater (switches as one with /911 & /913). Function: HEATING CONTROL ROOM | Markel | Hazardous Location WALL CONVECTOR heaters | [8 empty] | 9263-4F | 4F | MS-A-HE912 |  | 480 VAC | NA | NA | NA | AMBIENT AIR | 0 | 0 |  | Heater (switches as one with /911 & /913) | [7 empty] | 0 |  |  |  |  | AMBIENT AIR | [5 empty] | Heater (switches as one with /911 & /913) |  |  |  |  | AMBIENT AIR | [8 empty] | 480 VAC | AMBIENT AIR |  |  | Heater (switches as one with /911 & /913) |  |  | HE
Container unit Heater (switches as one with /911 & /912) HE913 | C2NC-1500-CU-HE_913 | C2NC-1500-CU | Equipment | Container unit Heater (switches as one with /911 & /912). Function: HEATING CONTROL ROOM | Markel | Hazardous Location WALL CONVECTOR heaters | [8 empty] | 9263-4F | 4F | MS-A-HE913 |  | 480 VAC | NA | NA | NA | AMBIENT AIR | 0 | 0 |  | Heater (switches as one with /911 & /912) | [7 empty] | 0 |  |  |  |  | AMBIENT AIR | [5 empty] | Heater (switches as one with /911 & /912) |  |  |  |  | AMBIENT AIR | [8 empty] | 480 VAC | AMBIENT AIR |  |  | Heater (switches as one with /911 & /912) |  |  | HE
Container unit LEL TRANSMITTER LEL910 | C2NC-1500-CU-LEL_910 | C2NC-1500-CU | Instruments | Container unit LEL TRANSMITTER. Function: DETECTION OF FLAMMABLE GASSES AND VAPORS | Dräger | Polytron® 5700 IR (incl. magnetic wand) | [8 empty] | 9263-4F | 4F | MS-A-LEL910 |  | 24 VDC | NA | NA | NA | AMBIENT AIR | AISI 316 L | NA |  | LEL TRANSMITTER | [7 empty] | NA |  |  |  |  | AMBIENT AIR | [5 empty] | LEL TRANSMITTER |  |  |  |  | AMBIENT AIR | [8 empty] | 24 VDC | AMBIENT AIR |  |  | LEL TRANSMITTER |  | Analog | LEL
Compressed gas treatment Level switch LS300 | C2NC-1500-CGT-LS_300 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS300 |  | 24 VDC | NA | NA | NA | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | [5 empty] | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Compressed gas treatment Level switch LS310 | C2NC-1500-CGT-LS_310 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS310 |  | 24 VDC | NA | NA | NA | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | [5 empty] | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Compressed gas treatment Level switch LS312 | C2NC-1500-CGT-LS_312 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: HIGH LEVEL GUARD FUNCTIONING OF BV310 | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS312 |  | 24 VDC | NA | NA | NA | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | [5 empty] | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Compressed gas treatment Level switch LS313 | C2NC-1500-CGT-LS_313 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: LOW LEVEL GUARD FUNCTIONING OF BV310 | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS313 |  | 24 VDC | NA | NA | NA | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | [5 empty] | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Compressed gas treatment Level switch LS320 | C2NC-1500-CGT-LS_320 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS320 |  | 24 VDC | NA | NA | NA | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | [5 empty] | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Compressed gas treatment Level switch LS330 | C2NC-1500-CGT-LS_330 | C2NC-1500-CGT | Instruments | Compressed gas treatment Level switch. Function: ENSURE WATER LEVEL | Endress & Hauser | Liquiphant M FTL50 | [8 empty] | 9263-4B | 4B | MS-A-LS330 |  | 24 VDC | NA | NA | NA | PROCESSS WATER | AISI 316L | 3/4" NPT (male) |  | Level switch | [7 empty] | -1/64Barg -14.5/928Psig |  |  |  |  | PROCESSS WATER | [5 empty] | Level switch |  |  |  |  | PROCESSS WATER | [8 empty] | 24 VDC | PROCESSS WATER |  |  | Level switch |  | Analog | LS
Membranes stage 1 Needle valve NV400 | C2NC-1500-MBR-NV_400 | C2NC-1500-MBR | Valves | Membranes stage 1 Needle valve. Function: CONTROL FLOW TO MEMBRANES | Swagelok | Stainless Steel Integral Bonnet Needle Valve, 0.73 Cv, 1/2 in. Swagelok Tube Fitting, Regulating Stem | [8 empty] | 9263-4C1 | 4C1 | MS-A-NV400 |  | 0 | 0 | 0 | 0 | Biogas | ASI 316 | 1/2" swagelok |  | Needle valve | [7 empty] | 3435 PSIG |  |  |  |  | Biogas | [5 empty] | Needle valve |  |  |  |  | Biogas | [8 empty] | 0 | Biogas |  |  | Needle valve |  |  | NV
Membranes stage 1 Orifice OF400 | C2NC-1500-MBR-OF_400 | C2NC-1500-MBR | Equipment | Membranes stage 1 Orifice. Function: REDUCE FLOW AND PRESSURE TO MEMBRANES | DMT | Dia 2,5 mm / 0,1" | [8 empty] | 9263-4C1 | 4C1 | MS-A-OF400 |  | NA | NA | NA | NA | BIOGAS | ASI 316 | 1/2" #300 |  | Orifice | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Orifice |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Orifice |  |  | OF
Membranes Orifice OF550 | C2NC-1500-MBR-OF_550 | C2NC-1500-MBR | Equipment | Membranes Orifice. Function: REDUCE FLOW AND PRESSURE TO FLARE | DMT | Dia 5mm / 0.2" according drawing DMT | [8 empty] | 9263-4C | 4C | MS-A-OF550 |  | NA | NA | NA | NA | BIOGAS | ASI 316 | 6" #300 |  | Orifice | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Orifice |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Orifice |  |  | OF
Membranes stage 1 Membrane stage 1, 1st row M1.1.01 | C2NC-1500-MBR-M_1.1.01 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.01 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.02 | C2NC-1500-MBR-M_1.1.02 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.02 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.03 | C2NC-1500-MBR-M_1.1.03 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.03 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.04 | C2NC-1500-MBR-M_1.1.04 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.04 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.04 | C2NC-1500-MBR-M_1.1.04 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.04 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.06 | C2NC-1500-MBR-M_1.1.06 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.06 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.07 | C2NC-1500-MBR-M_1.1.07 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.07 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.08 | C2NC-1500-MBR-M_1.1.08 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.08 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.09 | C2NC-1500-MBR-M_1.1.09 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.09 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.10 | C2NC-1500-MBR-M_1.1.10 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.10 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.11 | C2NC-1500-MBR-M_1.1.11 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.11 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.12 | C2NC-1500-MBR-M_1.1.12 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.12 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.13 | C2NC-1500-MBR-M_1.1.13 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.13 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Membranes stage 1 Membrane stage 1, 1st row M1.1.14 | C2NC-1500-MBR-M_1.1.14 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.1.14 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 1st row |  |  | M
Compressed gas treatment Back pressure regulator PCV310 | C2NC-1500-CGT-PCV_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Back pressure regulator. Function: REDUCE PRESSURE ON CONDENSATE TANK | Swagelok | Stainless Steel BP Regulator, 0 to 100 psig (3.4 bar), A Configuration, PCTFE Seal, 1/4 in. FNPT, 0.20 Cv | [8 empty] | 9263-4B | 4B | MS-A-PCV310 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316L / PTFE | 1/4" NPT (FEMALE) |  | Back pressure regulator | [7 empty] | 248 Barg - 3600 Psig |  |  |  |  | PROCESSS WATER | [5 empty] | Back pressure regulator |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Back pressure regulator |  |  | PCV
Membranes Back pressure regulator PCV500 | C2NC-1500-MBR-PCV_500 | C2NC-1500-MBR | Valves | Membranes Back pressure regulator. Function: REDUCE PRESSURE TO GASANALYZER | Swagelok | Stainless Steel PR Regulator, 0 to 25 psig (1.7 bar), 3600 psig (248 bar) inlet, C Config, PCTFE Seat, 1/4 in. FNPT, 0.06 Cv | [8 empty] | 9263-4C | 4C | MS-A-PCV500 |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 1/4" NPT (FEMALE) |  | Back pressure regulator | [7 empty] | 248 Barg - 3600 Psig |  |  |  |  | BIOGAS | [5 empty] | Back pressure regulator |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Back pressure regulator |  |  | PCV
Container unit Pressure reducing valve PCV910 | C2NC-1500-CU-PCV_910 | C2NC-1500-CU | Valves | Container unit Pressure reducing valve. Function: Adjust air supply pressure | Festo | MS6-LFR size 9 | [8 empty] | 9263-4F | 4F | MS-A-PCV910 |  | NA | NA | NA | NA | Instrument Air | composition | 1" |  | Pressure reducing valve | [7 empty] | 0,8 - 20 bar |  |  |  |  | Instrument Air | [5 empty] | Pressure reducing valve |  |  |  |  | Instrument Air | [8 empty] | NA | Instrument Air |  |  | Pressure reducing valve |  |  | PCV
Compressed gas treatment Pressure indicator PI310 | C2NC-1500-CGT-PI_310 | C2NC-1500-CGT | Instruments | Compressed gas treatment Pressure indicator. Function: INDICATE PRESSURE | Ashcroft | 1008S Pressure Gauge D63mm | [8 empty] | 9263-4B | 4B | MS-A-PI310 |  | NA | NA | NEMA 4 / IP65 | NA | PROCESSS WATER | AISI 316 | 1/4"NPT (MALE) |  | Pressure indicator | [7 empty] | 0-60 Psig |  |  |  |  | PROCESSS WATER | [5 empty] | Pressure indicator |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Pressure indicator |  |  | PI
Membranes Pressure indicator PI500 | C2NC-1500-MBR-PI_500 | C2NC-1500-MBR | Instruments | Membranes Pressure indicator. Function: INDICATE SET PRESSURE TO GAS ANLYZER | Ashcroft | 1008S Pressure Gauge D63mm | [8 empty] | 9263-4C | 4C | MS-A-PI500 |  | NA | NA | NEMA 4 / IP65 | NA | BIOGAS | AISI 316 | 1/4"NPT (MALE) |  | Pressure indicator | [7 empty] | 0-30 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure indicator |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Pressure indicator |  |  | PI
Compressed gas treatment Pressure indicator transmitter PIT320 | C2NC-1500-CGT-PIT_320 | C2NC-1500-CGT | Instruments | Compressed gas treatment Pressure indicator transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4B | 4B | MS-A-PIT320 |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Compressed gas treatment Pressure indicator transmitter PIT340 | C2NC-1500-CGT-PIT_340 | C2NC-1500-CGT | Instruments | Compressed gas treatment Pressure indicator transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4B | 4B | MS-A-PIT340 |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Membranes Pressure indicator transmitter PIT370 | C2NC-1500-MBR-PIT_370 | C2NC-1500-MBR | Instruments | Membranes Pressure indicator transmitter. Function: MEASURE INLET PRESSURE | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4C | 4C | MS-A-PIT370 |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Membranes Pressure indicator transmitter PIT500 | C2NC-1500-MBR-PIT_500 | C2NC-1500-MBR | Instruments | Membranes Pressure indicator transmitter. Function: MEASSURE PRESSURE AFTER STAGE 2B | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4C | 4C | MS-A-PIT500 |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Membranes Pressure indicator transmitter PIT510 | C2NC-1500-MBR-PIT_510 | C2NC-1500-MBR | Instruments | Membranes Pressure indicator transmitter. Function: MEASSURE PRESSURE AFTER AV400 | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4C | 4C | MS-A-PIT510 |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Membranes Pressure indicator transmitter PIT550 | C2NC-1500-MBR-PIT_550 | C2NC-1500-MBR | Instruments | Membranes Pressure indicator transmitter. Function: MEASSURE PRESSURE AFTER AV400 | Endress & Hauser | Cerabar PMC51 | [8 empty] | 9263-4C | 4C | MS-A-PIT550 |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure indicator transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure indicator transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure indicator transmitter |  | Analog | PIT
Compressed gas treatment Pressure transmitter PT310 | C2NC-1500-CGT-PT_310 | C2NC-1500-CGT | Instruments | Compressed gas treatment Pressure transmitter. Function: MEASURE PRESSURE IN BV310 | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-4B | 4B | MS-A-PT310 |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Membranes stage 1 Pressure transmitter PT400 | C2NC-1500-MBR-PT_400 | C2NC-1500-MBR | Instruments | Membranes stage 1 Pressure transmitter. Function: MEASSURE PRESSURE AFTER AV400 | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-4C1 | 4C1 | MS-A-PT400 |  | 24 VDC | NA | NA | NA | BIOGAS | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | BIOGAS | [5 empty] | Pressure transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Pressure transmitter |  | Analog | PT
Container unit Pressure transmitter PT910 | C2NC-1500-CU-PT_910 | C2NC-1500-CU | Instruments | Container unit Pressure transmitter. Function: MONITOR PRESSURE | Endress & Hauser | Cerabar PMC21 | [8 empty] | 9263-4F | 4F | MS-A-PT910 |  | 24 VDC | NA | NA | NA | INSTRUMENT AIR | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | INSTRUMENT AIR | [5 empty] | Pressure transmitter |  |  |  |  | INSTRUMENT AIR | [8 empty] | 24 VDC | INSTRUMENT AIR |  |  | Pressure transmitter |  | Analog | PT
Membranes stage 1 Spectacle flange SF420 | C2NC-1500-MBR-SF_420 | C2NC-1500-MBR | Equipment | Membranes stage 1 Spectacle flange. Function: BLOCK IN MEMBRANES | Fabricator MS | according to drawing DMT | [8 empty] | 9263-4C1 | 4C1 | MS-A-SF420 |  | NA | NA | NA | NA | BIOGAS | AISI 316 | 8" #300 |  | Spectacle flange | [7 empty] | 20.7 Barg - 300 Psig |  |  |  |  | BIOGAS | [5 empty] | Spectacle flange |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Spectacle flange |  |  | SF
Membranes stage 1 Spectacle flange SF421 | C2NC-1500-MBR-SF_421 | C2NC-1500-MBR | Equipment | Membranes stage 1 Spectacle flange. Function: BLOCK IN MEMBRANES | Fabricator MS | according to drawing DMT | [8 empty] | 9263-4C1 | 4C1 | MS-A-SF421 |  | NA | NA | NA | NA | BIOGAS | AISI 316 | 6" #300 |  | Spectacle flange | [7 empty] | 20.7 Barg - 300 Psig |  |  |  |  | BIOGAS | [5 empty] | Spectacle flange |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Spectacle flange |  |  | SF
Membranes Spectacle flange SF512 | C2NC-1500-MBR-SF_512 | C2NC-1500-MBR | Equipment | Membranes Spectacle flange. Function: BLOCK STACK DURING START-UP | DMT | according to drawing DMT | [8 empty] | 9263-4C | 4C | MS-A-SF512 |  | NA | NA | NA | NA | BIOGAS | AISI 316 | 6" #300 |  | Spectacle flange | [7 empty] | 20.7 Barg - 300 Psig |  |  |  |  | BIOGAS | [5 empty] | Spectacle flange |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Spectacle flange |  |  | SF
Membranes stage 1 Membrane stage 1, 2nd row M1.2.01 | C2NC-1500-MBR-M_1.2.01 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 2nd row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.2.01 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 2nd row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 2nd row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 2nd row |  |  | M
Membranes stage 1 Membrane stage 1, 2nd row M1.2.02 | C2NC-1500-MBR-M_1.2.02 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 2nd row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.2.02 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 2nd row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 2nd row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 2nd row |  |  | M
Membranes stage 1 Membrane stage 1, 2nd row M1.2.03 | C2NC-1500-MBR-M_1.2.03 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 2nd row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.2.03 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 2nd row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 2nd row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 2nd row |  |  | M
Membranes stage 1 Membrane stage 1, 2nd row M1.2.04 | C2NC-1500-MBR-M_1.2.04 | C2NC-1500-MBR | Equipment | Membranes stage 1 Membrane stage 1, 2nd row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C1 | 4C1 | MS-A-M1.2.04 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 1, 2nd row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 1, 2nd row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 1, 2nd row |  |  | M
Container unit Sound indicator ( Horn ) SI910 | C2NC-1500-CU-SI_910 | C2NC-1500-CU | Instruments | Container unit Sound indicator ( Horn ). Function: CREATE AUDIO WARNING SIGNAL | E2S Warning signals | D2xS1 AC115 AB1 A1R | [8 empty] | 9263-4F | 4F | MS-A-SI910 |  | 115 VAC | NA | NA | NA | AMBIENT AIR | Aluminium - Red - RAL3000 | 130x180x125mm (wxhxd) |  | Sound indicator ( Horn ) | [7 empty] | NA |  |  |  |  | AMBIENT AIR | [5 empty] | Sound indicator ( Horn ) |  |  |  |  | AMBIENT AIR | [8 empty] | 115 VAC | AMBIENT AIR |  |  | Sound indicator ( Horn ) |  | Digital | SI
Container unit Sound indicator ( Horn ) SI912 | C2NC-1500-CU-SI_912 | C2NC-1500-CU | Instruments | Container unit Sound indicator ( Horn ). Function: CREATE AUDIO WARNING SIGNAL | E2S Warning signals | D2xS1 AC115 AB1 A1R | [8 empty] | 9263-4F | 4F | MS-A-SI912 |  | 115 VAC | NA | NA | NA | AMBIENT AIR | Aluminium - Red - RAL3000 | 130x180x125mm (wxhxd) |  | Sound indicator ( Horn ) | [7 empty] | NA |  |  |  |  | AMBIENT AIR | [5 empty] | Sound indicator ( Horn ) |  |  |  |  | AMBIENT AIR | [8 empty] | 115 VAC | AMBIENT AIR |  |  | Sound indicator ( Horn ) |  | Digital | SI
Container unit Signal lamp SL910 | C2NC-1500-CU-SL_910 | C2NC-1500-CU | Instruments | Container unit Signal lamp. Function: CREATE VISUAL WARNING | Edwards Signaling | 105 Series (Blue High Intensity Beacon) | [8 empty] | 9263-4F | 4F | MS-A-SL910 |  | 120 VAC | NA | NA | NA | AMBIENT AIR | NA | Diam. 4,5' |  | Signal lamp | [7 empty] | NA |  |  |  |  | AMBIENT AIR | [5 empty] | Signal lamp |  |  |  |  | AMBIENT AIR | [8 empty] | 120 VAC | AMBIENT AIR |  |  | Signal lamp |  | Digital | SL
Membranes Control valve AV460 | C2NC-1500-MBR-AV_460 | C2NC-1500-MBR | Valves | Membranes Control valve. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | Conovalve | S803 - D Control Valve 4"- ANSI CLASS 300 AV460 CV160 | [8 empty] | 9263-4C | 4C | MS-A-AV460 |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 4" #300 |  | Control valve | [7 empty] | ASME CLASS 300 |  |  |  |  | BIOGAS | [5 empty] | Control valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Control valve |  |  | AV
Membranes Pneumatic actuator AV460 | C2NC-1500-MBR-AV_460 | C2NC-1500-MBR | Valves | Membranes Pneumatic actuator. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | S340/I | [8 empty] | 9263-4C | 4C | MS-A-AV460 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes Control unit/ positioner AV460 | C2NC-1500-MBR-AV_460 | C2NC-1500-MBR | Valves | Membranes Control unit/ positioner. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | V200E-IS (using Non Incendive Field Wiring for use without barrier in Class I Div.2 !! | [8 empty] | 9263-4C | 4C | MS-A-AV460 |  | 24 VDC | NA | NA | NA | COMPRESSED AIR | NA | NA |  | Control unit/ positioner | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Control unit/ positioner |  |  |  |  | COMPRESSED AIR | [8 empty] | 24 VDC | COMPRESSED AIR |  |  | Control unit/ positioner |  | Analog | AV
Container unit Signal lamp SL911 | C2NC-1500-CU-SL_911 | C2NC-1500-CU | Instruments | Container unit Signal lamp. Function: CREATE VISUAL WARNING | Edwards Signaling | 105 Series (Blue High Intensity Beacon) | [8 empty] | 9263-4F | 4F | MS-A-SL911 |  | 120 VAC | NA | NA | NA | AMBIENT AIR | NA | Diam. 4,5' |  | Signal lamp | [7 empty] | NA |  |  |  |  | AMBIENT AIR | [5 empty] | Signal lamp |  |  |  |  | AMBIENT AIR | [8 empty] | 120 VAC | AMBIENT AIR |  |  | Signal lamp |  | Digital | SL
Membranes stage 2A Membrane stage 2A, 1st row M2.1.01 | C2NC-1500-MBR-M_2.1.01 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.01 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2A, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2A, 1st row |  |  | M
Membranes stage 2A Membrane stage 2A, 1st row M2.1.02 | C2NC-1500-MBR-M_2.1.02 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.02 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2A, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2A, 1st row |  |  | M
Membranes stage 2A Membrane stage 2A, 1st row M2.1.03 | C2NC-1500-MBR-M_2.1.03 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.03 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2A, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2A, 1st row |  |  | M
Membranes stage 2A Membrane stage 2A, 1st row M2.1.04 | C2NC-1500-MBR-M_2.1.04 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.04 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2A, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2A, 1st row |  |  | M
Membranes stage 2A Membrane stage 2A, 1st row M2.1.05 | C2NC-1500-MBR-M_2.1.05 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.05 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2A, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2A, 1st row |  |  | M
Membranes stage 2A Membrane stage 2A, 1st row M2.1.06 | C2NC-1500-MBR-M_2.1.06 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.06 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2A, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2A, 1st row |  |  | M
Membranes stage 2A Membrane stage 2A, 1st row M2.1.07 | C2NC-1500-MBR-M_2.1.07 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.07 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2A, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2A, 1st row |  |  | M
Membranes stage 2A Membrane stage 2A, 1st row M2.1.08 | C2NC-1500-MBR-M_2.1.08 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.08 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2A, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2A, 1st row |  |  | M
Membranes stage 2A Membrane stage 2A, 1st row M2.1.09 | C2NC-1500-MBR-M_2.1.09 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.09 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2A, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2A, 1st row |  |  | M
Membranes stage 2A Membrane stage 2A, 1st row M2.1.10 | C2NC-1500-MBR-M_2.1.10 | C2NC-1500-MBR | Equipment | Membranes stage 2A Membrane stage 2A, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green G5X 150 x 1310 Membrane module (cartridge + housing) SAP Material 99109931 | [8 empty] | 9263-4C2 | 4C2 | MS-A-M2.1.10 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2A, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2A, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2A, 1st row |  |  | M
Compressed gas treatment Temperature transmitter TT320 | C2NC-1500-CGT-TT_320 | C2NC-1500-CGT | Instruments | Compressed gas treatment Temperature transmitter. Function: MEASURE INLET TEMPERATURE BIOGAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4B | 4B | MS-A-TT320 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Membranes stage 2B Membrane stage 2B, 1st row M2.3.01 | C2NC-1500-MBR-M_2.3.01 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.01 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.3.02 | C2NC-1500-MBR-M_2.3.02 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.02 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.3.03 | C2NC-1500-MBR-M_2.3.03 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.03 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.3.04 | C2NC-1500-MBR-M_2.3.04 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.04 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.3.05 | C2NC-1500-MBR-M_2.3.05 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.05 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.3.06 | C2NC-1500-MBR-M_2.3.06 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.06 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.3.07 | C2NC-1500-MBR-M_2.3.07 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.07 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.3.08 | C2NC-1500-MBR-M_2.3.08 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.3.08 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Compressed gas treatment Temperature transmitter TT340 | C2NC-1500-CGT-TT_340 | C2NC-1500-CGT | Instruments | Compressed gas treatment Temperature transmitter. Function: MEASURE INLET TEMPERATURE BIOGAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4B | 4B | MS-A-TT340 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Membranes Temperature transmitter TT370 | C2NC-1500-MBR-TT_370 | C2NC-1500-MBR | Instruments | Membranes Temperature transmitter. Function: MEASURE INLET AFTER FILTERS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4C | 4C | MS-A-TT370 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Membranes stage 2B Membrane stage 2B, 1st row M2.4.01 | C2NC-1500-MBR-M_2.4.01 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.01 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.4.02 | C2NC-1500-MBR-M_2.4.02 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.02 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.4.03 | C2NC-1500-MBR-M_2.4.03 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.03 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.4.04 | C2NC-1500-MBR-M_2.4.04 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.04 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.4.05 | C2NC-1500-MBR-M_2.4.05 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.05 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.4.06 | C2NC-1500-MBR-M_2.4.06 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.06 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.4.07 | C2NC-1500-MBR-M_2.4.07 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.07 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes stage 2B Membrane stage 2B, 1st row M2.4.08 | C2NC-1500-MBR-M_2.4.08 | C2NC-1500-MBR | Equipment | Membranes stage 2B Membrane stage 2B, 1st row. Function: INITIAL SEPARATION OF CH4 AND CO2, WASTE CO2 TO DISCHARGE | EVONIK | 6" Sepuran green S2F 150 x 1310 Membrane module (cartridge + housing) SAP Material 99127444 | [8 empty] | 9263-4C3 | 4C3 | MS-A-M2.4.08 |  | NA | NA | NA | NA | BIOGAS | AISI 316L | 2 x 1" G/BSPP (feed&retentate), 1 x 2" VIC (permeate) |  | Membrane stage 2B, 1st row | [7 empty] | max 25 bar - 362 Psig |  |  |  |  | BIOGAS | [5 empty] | Membrane stage 2B, 1st row |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Membrane stage 2B, 1st row |  |  | M
Membranes Temperature transmitter TT460 | C2NC-1500-MBR-TT_460 | C2NC-1500-MBR | Instruments | Membranes Temperature transmitter. Function: MEASURE TEMPERATURE BEFORE HE460 | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4C | 4C | MS-A-TT460 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316L / ALU | 1/2" NPT |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Membranes Temperature transmitter TT500 | C2NC-1500-MBR-TT_500 | C2NC-1500-MBR | Instruments | Membranes Temperature transmitter. Function: MEASURE OUTLET TEMPERATURE PRODUCT GAS | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4C | 4C | MS-A-TT500 |  | 24 VDC | NA | NA | NA | BIOGAS | AISI 316L / ALU | 1/2" NPT, 2,5" |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | BIOGAS | [5 empty] | Temperature transmitter |  |  |  |  | BIOGAS | [8 empty] | 24 VDC | BIOGAS |  |  | Temperature transmitter |  | Analog | TT
Container unit Temperature transmitter TT910 | C2NC-1500-CU-TT_910 | C2NC-1500-CU | Instruments | Container unit Temperature transmitter. Function: MEASURE AREA TEMPERATURE | Endress & Hauser | TST434-J1A4DW (inclusive TMT181-I PCP FM+CSA, Class I, Div 1+2 ) RTD Thermometer TST434 | [8 empty] | 9263-4F | 4F | MS-A-TT910 |  | 24 VDC | NA | NA | NA | AMBIENT AIR | Composition of materials | NA |  | Temperature transmitter | [7 empty] | 0 |  |  |  |  | AMBIENT AIR | [5 empty] | Temperature transmitter |  |  |  |  | AMBIENT AIR | [8 empty] | 24 VDC | AMBIENT AIR |  |  | Temperature transmitter |  | Analog | TT
Compressed gas treatment Ball valve V301 | C2NC-1500-CGT-V_301 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: FILTER DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V301 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V302 | C2NC-1500-CGT-V_302 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V302 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V303 | C2NC-1500-CGT-V_303 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V303 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V304 | C2NC-1500-CGT-V_304 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V304 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V305 | C2NC-1500-CGT-V_305 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V305 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Control valve AV500 | C2NC-1500-MBR-AV_500 | C2NC-1500-MBR | Valves | Membranes Control valve. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | Conovalve | S800 Control valve 2" - ANSI CLASS 300 AV500 | [8 empty] | 9263-4C | 4C | MS-A-AV500 |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 2" #300 |  | Control valve | [7 empty] | ASME CLASS 300 |  |  |  |  | BIOGAS | [5 empty] | Control valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Control valve |  |  | AV
Membranes Pneumatic actuator AV500 | C2NC-1500-MBR-AV_500 | C2NC-1500-MBR | Valves | Membranes Pneumatic actuator. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | S275/I | [8 empty] | 9263-4C | 4C | MS-A-AV500 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membranes Control unit/ positioner AV500 | C2NC-1500-MBR-AV_500 | C2NC-1500-MBR | Valves | Membranes Control unit/ positioner. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | V200E-IS (using Non Incendive Field Wiring for use without barrier in Class I Div.2 !! | [8 empty] | 9263-4C | 4C | MS-A-AV500 |  | 24 VDC | NA | NA | NA | COMPRESSED AIR | NA | NA |  | Control unit/ positioner | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Control unit/ positioner |  |  |  |  | COMPRESSED AIR | [8 empty] | 24 VDC | COMPRESSED AIR |  |  | Control unit/ positioner |  | Analog | AV
Compressed gas treatment Ball valve V307 | C2NC-1500-CGT-V_307 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V307 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V309 | C2NC-1500-CGT-V_309 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V309 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V310 | C2NC-1500-CGT-V_310 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V310 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V311 | C2NC-1500-CGT-V_311 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: FILTER DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V311 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V312 | C2NC-1500-CGT-V_312 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V312 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V313 | C2NC-1500-CGT-V_313 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V313 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Membrane Separation Control valve AV550 | C2NC-1500-MBR-AV_550 | C2NC-1500-MBR | Valves | Membrane Separation Control valve. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | Conovalve | S800 Control valve 2 1/2" - ANSI CLASS 300 AV550 CV28 | [8 empty] | 9263-4C | 4C | MS-A-AV550 |  | NA | NA | NA | NA | BIOGAS | AISI 316L / PTFE | 2.5" #300 |  | Control valve | [7 empty] | ASME CLASS 300 |  |  |  |  | BIOGAS | [5 empty] | Control valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Control valve |  |  | AV
Membrane Separation Pneumatic actuator AV550 | C2NC-1500-MBR-AV_550 | C2NC-1500-MBR | Valves | Membrane Separation Pneumatic actuator. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | S275/I | [8 empty] | 9263-4C | 4C | MS-A-AV550 |  | NA | NA | NA | NA | COMPRESSED AIR | ALU | NA |  | Pneumatic actuator | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Pneumatic actuator |  |  |  |  | COMPRESSED AIR | [8 empty] | NA | COMPRESSED AIR |  |  | Pneumatic actuator |  |  | AV
Membrane Separation Control unit/ positioner AV550 | C2NC-1500-MBR-AV_550 | C2NC-1500-MBR | Valves | Membrane Separation Control unit/ positioner. Function: CONTROL PRESSURE OF MEMBRANE SYSTEM | VAC | V200E-IS (using Non Incendive Field Wiring for use without barrier in Class I Div.2 !! | [8 empty] | 9263-4C | 4C | MS-A-AV550 |  | 24 VDC | NA | NA | NA | COMPRESSED AIR | NA | NA |  | Control unit/ positioner | [7 empty] | NA |  |  |  |  | COMPRESSED AIR | [5 empty] | Control unit/ positioner |  |  |  |  | COMPRESSED AIR | [8 empty] | 24 VDC | COMPRESSED AIR |  |  | Control unit/ positioner |  | Analog | AV
Compressed gas treatment Ball valve V320 | C2NC-1500-CGT-V_320 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: Block PT | FLO-TITE | 0 | [8 empty] | 9263-4B | 4B | MS-A-V320 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V321 | C2NC-1500-CGT-V_321 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: FILTER DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V321 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V322 | C2NC-1500-CGT-V_322 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V322 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V323 | C2NC-1500-CGT-V_323 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V323 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V331 | C2NC-1500-CGT-V_331 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: FILTER DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V331 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 3/4" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V332 | C2NC-1500-CGT-V_332 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V332 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V333 | C2NC-1500-CGT-V_333 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: BLOCK CONDENSATE LINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V333 |  | NA | NA | NA | NA | PROCESSS WATER | AISI 316 / PTFE | 1/2" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | PROCESSS WATER | [5 empty] | Ball valve |  |  |  |  | PROCESSS WATER | [8 empty] | NA | PROCESSS WATER |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V340 | C2NC-1500-CGT-V_340 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: Block PT | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V340 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V342 | C2NC-1500-CGT-V_342 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V342 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V350 | C2NC-1500-CGT-V_350 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V350 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Ball valve V360 | C2NC-1500-CGT-V_360 | C2NC-1500-CGT | Valves | Compressed gas treatment Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4B | 4B | MS-A-V360 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Butterfly valve V370 | C2NC-1500-CGT-V_370 | C2NC-1500-CGT | Valves | Compressed gas treatment Butterfly valve. Function: BLOCK COMPRESSED GAS TREATMENT | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4B | 4B | MS-A-V370 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes Ball valve V371 | C2NC-1500-MBR-V_371 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V371 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes stage 1 Ball valve V400 | C2NC-1500-MBR-V_400 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: ISOLATE PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C1 | 4C1 | MS-A-V400 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V401 | C2NC-1500-MBR-V_401 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V401 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes stage 1 Ball valve V402 | C2NC-1500-MBR-V_402 | C2NC-1500-MBR | Valves | Membranes stage 1 Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C1 | 4C1 | MS-A-V402 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V405 | C2NC-1500-MBR-V_405 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V405 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V408 | C2NC-1500-MBR-V_408 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V408 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Butterfly valve V409 | C2NC-1500-MBR-V_409 | C2NC-1500-MBR | Valves | Membranes Butterfly valve. Function: BLOCK MEMBRANE STAGE 2A | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C | 4C | MS-A-V409 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 8" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes Ball valve V410 | C2NC-1500-MBR-V_410 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V410 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes stage 2B Ball valve V412 | C2NC-1500-MBR-V_412 | C2NC-1500-MBR | Valves | Membranes stage 2B Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C3 | 4C3 | MS-A-V412 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Cooling skid Chiller CH720 | C2NC-1500-CLG-CH_720 | C2NC-1500-CLG | Equipment | Cooling skid Chiller. Function: COOL DOWN COOLING FLUID | York | YORK Model YLAA0155SE Packaged Scroll Chillers | [8 empty] | 9263-4D | 4D | MS-A-CH720 |  | 480 VAC | NA | NA | NA | GLYCOL MIXTURE | 0 | 4 " 150# |  | Chiller | [7 empty] | 0 |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Chiller |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 480 VAC | GLYCOL MIXTURE |  |  | Chiller |  | Digital | CH
Cooling skid Compensator BL720 | C2NC-1500-CLG-BL_720 | C2NC-1500-CLG | Equipment | Cooling skid Compensator. Function: 0 | Mason | Mason Model SFEJ Neoprene Flexible Pipe Connection Isolators | [8 empty] | 9263-4D | 4D | MS-A-BL720 |  | 0 | 0 | 0 | 0 | GLYCOL MIXTURE | 0 | 4 " 150# |  | Compensator | [7 empty] | 0 |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Compensator |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 0 | GLYCOL MIXTURE |  |  | Compensator |  |  | BL
Cooling skid Butterfly valve V726 | C2NC-1500-CLG-V_726 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V726 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Temperature transmitter TT720 | C2NC-1500-CLG-TT_720 | C2NC-1500-CLG | Instruments | Cooling skid Temperature transmitter. Function: MEASURE TEMPERATURE IN CIRCUIT | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4D | 4D | MS-A-TT720 |  | 24 VDC | NA | NA | NA | GLYCOL MIXTURE | AISI 316L / ALU | 1/2" NPT, 2,5" |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Temperature transmitter |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 24 VDC | GLYCOL MIXTURE |  |  | Temperature transmitter |  | Analog | TT
Cooling skid Ball valve V724 | C2NC-1500-CLG-V_724 | C2NC-1500-CLG | Valves | Cooling skid Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4D | 4D | MS-A-V724 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Ball valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Cooling skid Butterfly valve V730 | C2NC-1500-CLG-V_730 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V730 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Compensator BL731 | C2NC-1500-CLG-BL_731 | C2NC-1500-CLG | Equipment | Cooling skid Compensator. Function: 0 | Mason | Mason Model SFEJ Neoprene Flexible Pipe Connection Isolators | [8 empty] | 9263-4D | 4D | MS-A-BL731 |  | 0 | 0 | 0 | 0 | GLYCOL MIXTURE | 0 | 4 " 150# |  | Compensator | [7 empty] | 0 |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Compensator |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 0 | GLYCOL MIXTURE |  |  | Compensator |  |  | BL
Cooling skid Dearation valve DAV730 | C2NC-1500-CLG-DAV_730 | C2NC-1500-CLG | Equipment | Cooling skid Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO | [8 empty] | 9263-4D | 4D | MS-A-DAV730 |  | NA | NA | NA | NA | GLYCOL MIXTURE | Brass | 1/2"NPT in, G3/4"out |  | Dearation valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Dearation valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Dearation valve |  |  | DAV
Cooling skid Chiller CH730 | C2NC-1500-CLG-CH_730 | C2NC-1500-CLG | Equipment | Cooling skid Chiller. Function: COOL DOWN COOLING FLUID | York | YORK Model YLAA0155SE Packaged Scroll Chillers | [8 empty] | 9263-4D | 4D | MS-A-CH730 |  | 480 VAC | NA | NA | NA | GLYCOL MIXTURE | 0 | 4 " 150# |  | Chiller | [7 empty] | 0 |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Chiller |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 480 VAC | GLYCOL MIXTURE |  |  | Chiller |  | Digital | CH
Cooling skid Compensator BL730 | C2NC-1500-CLG-BL_730 | C2NC-1500-CLG | Equipment | Cooling skid Compensator. Function: 0 | Mason | Mason Model SFEJ Neoprene Flexible Pipe Connection Isolators | [8 empty] | 9263-4D | 4D | MS-A-BL730 |  | 0 | 0 | 0 | 0 | GLYCOL MIXTURE | 0 | 4 " 150# |  | Compensator | [7 empty] | 0 |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Compensator |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 0 | GLYCOL MIXTURE |  |  | Compensator |  |  | BL
Cooling skid Butterfly valve V732 | C2NC-1500-CLG-V_732 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V732 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Butterfly valve V731 | C2NC-1500-CLG-V_731 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V731 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Flow indicator transmitter FIT710 | C2NC-1500-CLG-FIT_710 | C2NC-1500-CLG | Instruments | Cooling skid Flow indicator transmitter. Function: GUARDING CIRCULATION FLOW | Endress & Hauser | Promag W 400, 5W4C80, DN80 3" | [8 empty] | 9263-4D | 4D | MS-A-FIT710 |  | 120 VAC | 0.15 | 0.01 | 0.01 | GLYCOL MIXTURE | Composition of materials | 3" 150# |  | Flow indicator transmitter | [7 empty] | 73-101 psi |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Flow indicator transmitter |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 120 VAC | GLYCOL MIXTURE |  |  | Flow indicator transmitter |  | Analog | FIT
Cooling skid Pressure transmitter PT710 | C2NC-1500-CLG-PT_710 | C2NC-1500-CLG | Instruments | Cooling skid Pressure transmitter. Function: MEASURE PRESSURE IN CIRCUIT | Endress & Hauser | Cerabar PMP21 | [8 empty] | 9263-4D | 4D | MS-A-PT710 |  | 24 VDC | NA | NA | NA | GLYCOL MIXTURE | 316L / FKM | 1/2" NPT |  | Pressure transmitter | [7 empty] | 40 Barg -600 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Pressure transmitter |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 24 VDC | GLYCOL MIXTURE |  |  | Pressure transmitter |  | Analog | PT
Cooling skid Temperature transmitter TT730 | C2NC-1500-CLG-TT_730 | C2NC-1500-CLG | Instruments | Cooling skid Temperature transmitter. Function: MEASURE TEMPERATURE IN CIRCUIT | Endress & Hauser | RTD temperaturesensor, TH13, U.S. Style | [8 empty] | 9263-4D | 4D | MS-A-TT730 |  | 24 VDC | NA | NA | NA | GLYCOL MIXTURE | AISI 316L / ALU | 1/2" NPT, 2,5" |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Temperature transmitter |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 24 VDC | GLYCOL MIXTURE |  |  | Temperature transmitter |  | Analog | TT
Cooling skid Butterfly valve V721 | C2NC-1500-CLG-V_721 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE PUMP | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V721 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Strainer ST720 | C2NC-1500-CLG-ST_720 | C2NC-1500-CLG | Equipment | Cooling skid Strainer. Function: PROTECT PUMP AND CHILLER | Titan | YS 61-SS Strainer, Flanged ends, Raised Face | [8 empty] | 9263-4D | 4D | MS-A-ST720 |  | NA | NA | NA | NA | GLYCOL MIXTURE | Composition of materials | 2" 150# |  | Strainer | [7 empty] | 275 Psig @ 100ºF |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Strainer |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Strainer |  |  | ST
Cooling skid Pump P720 | C2NC-1500-CLG-P_720 | C2NC-1500-CLG | Equipment | Cooling skid Pump. Function: CIRCULATING OF GLYCOL | Carver | GH ? General Horizontal Series | [8 empty] | 9263-4D | 4D | MS-A-P720 |  | 480 VAC | NA | NA | NA | GLYCOL MIXTURE | AISI 316 | 2.1/2" inlet 2"outlet NPT |  | Pump | [7 empty] | 36 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Pump |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 480 VAC | GLYCOL MIXTURE |  |  | Pump |  | Analog | P
Cooling skid Butterfly valve V722 | C2NC-1500-CLG-V_722 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE PUMP | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V722 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Butterfly valve V723 | C2NC-1500-CLG-V_723 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE BUFFER VESSEL | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V723 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 2" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Butterfly valve V710 | C2NC-1500-CLG-V_710 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE BUFFER VESSEL | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V710 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Buffer vessel BV710 | C2NC-1500-CLG-BV_710 | C2NC-1500-CLG | Valves | Cooling skid Buffer vessel. Function: STABILIZING TEMPERATURE OF COOLING SYSTEM | DMT | according to drawing DMT | [8 empty] | 9263-4D | 4D | MS-A-BV710 |  | 0 | 0 | 0 | 0 | GLYCOL MIXTURE | AISI 304 | 4" 150# |  | Buffer vessel | [7 empty] | 0 |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Buffer vessel |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 0 | GLYCOL MIXTURE |  |  | Buffer vessel |  |  | BV
Cooling skid Pressure safety valve PZV710 | C2NC-1500-CLG-PZV_710 | C2NC-1500-CLG | Valves | Cooling skid Pressure safety valve. Function: 0 | Apollo valves | Cast Bronze Adjustable Relief Valve, MNPT Inlet Type, FNPT Outlet Type | [8 empty] | 9263-4D | 4D | MS-A-PZV710 |  | 0 | 0 | 0 | 0 | GLYCOL MIXTURE | Cast Bronze | 1/2" MNPT |  | Pressure safety valve | [7 empty] | 0 |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Pressure safety valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 0 | GLYCOL MIXTURE |  |  | Pressure safety valve |  |  | PZV
Cooling skid Ball valve V714 | C2NC-1500-CLG-V_714 | C2NC-1500-CLG | Valves | Cooling skid Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4D | 4D | MS-A-V714 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / PTFE | 1" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Ball valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Cooling skid Dearation valve DAV710 | C2NC-1500-CLG-DAV_710 | C2NC-1500-CLG | Equipment | Cooling skid Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO | [8 empty] | 9263-4D | 4D | MS-A-DAV710 |  | NA | NA | NA | NA | GLYCOL MIXTURE | Brass | 1/2"NPT in, G3/4"out |  | Dearation valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Dearation valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Dearation valve |  |  | DAV
Cooling skid Expansion vessel EV710 | C2NC-1500-CLG-EV_710 | C2NC-1500-CLG | Equipment | Cooling skid Expansion vessel. Function: REDUCE PRESSURE FLUCTUATIONS COOLING CIRCUIT | Amtrol | Extrol AX-120V 68 gallons vertical | [8 empty] | 9263-4D | 4D | MS-A-EV710 |  | 0 | 0 | 0 | 0 | GLYCOL MIXTURE | Carbon steel | 1" FNPT |  | Expansion vessel | [7 empty] | 125 Psi |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Expansion vessel |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 0 | GLYCOL MIXTURE |  |  | Expansion vessel |  |  | EV
Cooling skid Butterfly valve V711 | C2NC-1500-CLG-V_711 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE BUFFER VESSEL | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V711 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Ball valve V713 | C2NC-1500-CLG-V_713 | C2NC-1500-CLG | Valves | Cooling skid Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4D | 4D | MS-A-V713 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Ball valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Ball valve |  |  | V
Cooling skid Pressure indicator PI710 | C2NC-1500-CLG-PI_710 | C2NC-1500-CLG | Instruments | Cooling skid Pressure indicator. Function: INDICATE PRESSURE COOLING CIRCUIT | Ashcroft | 1008S Pressure Gauge D63mm | [8 empty] | 9263-4D | 4D | MS-A-PI710 |  | NA | NA | NEMA 4 / IP65 | NA | GLYCOL MIXTURE | AISI 316 | 1/4"NPT (MALE) |  | Pressure indicator | [7 empty] | 0-60 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Pressure indicator |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Pressure indicator |  |  | PI
Cooling skid Strainer ST710 | C2NC-1500-CLG-ST_710 | C2NC-1500-CLG | Equipment | Cooling skid Strainer. Function: PROTECT PUMP AND CHILLER | Titan | YS 61-SS Strainer, Flanged ends, Raised Face | [8 empty] | 9263-4D | 4D | MS-A-ST710 |  | NA | NA | NA | NA | GLYCOL MIXTURE | Composition of materials | 4" 150# |  | Strainer | [7 empty] | 275 Psig @ 100ºF |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Strainer |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Strainer |  |  | ST
Cooling skid Butterfly valve V715 | C2NC-1500-CLG-V_715 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE BUFFER VESSEL | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V715 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Pump P710 | C2NC-1500-CLG-P_710 | C2NC-1500-CLG | Equipment | Cooling skid Pump. Function: CIRCULATING OF GLYCOL | Carver | GH ? General Horizontal Series | [8 empty] | 9263-4D | 4D | MS-A-P710 |  | 480 VAC | NA | NA | NA | GLYCOL MIXTURE | AISI 316 | 3" inlet 2,5"outlet - 150# |  | Pump | [7 empty] | 65 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Pump |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 480 VAC | GLYCOL MIXTURE |  |  | Pump |  | Analog | P
Cooling skid Dearation valve DAV711 | C2NC-1500-CLG-DAV_711 | C2NC-1500-CLG | Equipment | Cooling skid Dearation valve. Function: DEARATE GLYCOL MIXTURE SYSTEM | FLAMCO | FLEXVENT PRO | [8 empty] | 9263-4D | 4D | MS-A-DAV711 |  | NA | NA | NA | NA | GLYCOL MIXTURE | Brass | 1/2"NPT in, G3/4"out |  | Dearation valve | [7 empty] | 10 Barg - 145 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Dearation valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Dearation valve |  |  | DAV
Cooling skid Butterfly valve V712 | C2NC-1500-CLG-V_712 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V712 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Butterfly valve V720 | C2NC-1500-CLG-V_720 | C2NC-1500-CLG | Valves | Cooling skid Butterfly valve. Function: ISOLATE CHILLER | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4D | 4D | MS-A-V720 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Cooling skid Compensator BL721 | C2NC-1500-CLG-BL_721 | C2NC-1500-CLG | Equipment | Cooling skid Compensator. Function: 0 | Mason | Mason Model SFEJ Neoprene Flexible Pipe Connection Isolators | [8 empty] | 9263-4D | 4D | MS-A-BL721 |  | 0 | 0 | 0 | 0 | GLYCOL MIXTURE | 0 | 4 " 150# |  | Compensator | [7 empty] | 0 |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Compensator |  |  |  |  | GLYCOL MIXTURE | [8 empty] | 0 | GLYCOL MIXTURE |  |  | Compensator |  |  | BL
Gas analyser Gas Quality Analyser Board GQA800 | C2NC-1500-GA-GQA_800 | C2NC-1500-GA | Instruments | Gas analyser Gas Quality Analyser Board. Function: ANALYSE GAS QUALITY | GE sensing | CH4, CO2,O2, H2S Biogas measurement panel | [8 empty] | 9263-4E | 4E | MS-A-GQA800 |  | 0 | NA | NA | NA | BIOGAS | 0 | 0 |  | Gas Quality Analyser Board | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Gas Quality Analyser Board |  |  |  |  | BIOGAS | [8 empty] | 0 | BIOGAS |  |  | Gas Quality Analyser Board |  |  | GQA
Gas analyser Three-way valve AV800 | C2NC-1500-GA-AV_800 | C2NC-1500-GA | Valves | Gas analyser Three-way valve. Function: Switch Routing on Analyser Board | GE sensing | ?? | [8 empty] | 9263-4E | 4E | MS-A-AV800 |  | 120 VAC | 0 | 0 | 0 | BIOGAS | 0 | 0 |  | Three-way valve | [7 empty] | 0 |  |  |  |  | BIOGAS | [5 empty] | Three-way valve |  |  |  |  | BIOGAS | [8 empty] | 120 VAC | BIOGAS |  |  | Three-way valve |  | Digital | AV
Gas analyser Gas quality analyser QT841 | C2NC-1500-GA-QT_841 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : CH4 : 0-10% | GE sensing | 0 | [8 empty] | 9263-4E | 4E | MS-A-QT841 |  | 24 VDC | 0 | 0 | 0 | 0 | 0 | 0 |  | Gas quality analyser | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Gas quality analyser |  |  |  |  | 0 | [8 empty] | 24 VDC | 0 |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Gas quality analyser QT814 | C2NC-1500-GA-QT_814 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : H2S : 0-300ppm | GE sensing | 0 | [8 empty] | 9263-4E | 4E | MS-A-QT814 |  | 24 VDC | 0 | 0 | 0 | 0 | 0 | 0 |  | Gas quality analyser | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Gas quality analyser |  |  |  |  | 0 | [8 empty] | 24 VDC | 0 |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Pump P810 | C2NC-1500-GA-P_810 | C2NC-1500-GA | Equipment | Gas analyser Pump. Function: 0 | GE sensing | 0 | [8 empty] | 9263-4E | 4E | MS-A-P810 |  | 115 VAC | 0 | 0 | 0 | 0 | 0 | 0 |  | Pump | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Pump |  |  |  |  | 0 | [8 empty] | 115 VAC | 0 |  |  | Pump |  |  | P
Gas analyser Gas quality analyser QT823 | C2NC-1500-GA-QT_823 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : O2 : 0-2% | GE sensing | 0 | [8 empty] | 9263-4E | 4E | MS-A-QT823 |  | 24 VDC | 0 | 0 | 0 | 0 | 0 | 0 |  | Gas quality analyser | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Gas quality analyser |  |  |  |  | 0 | [8 empty] | 24 VDC | 0 |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Gas quality analyser QT824 | C2NC-1500-GA-QT_824 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : H2S : 0-50ppm | GE sensing | 0 | [8 empty] | 9263-4E | 4E | MS-A-QT824 |  | 24 VDC | 0 | 0 | 0 | 0 | 0 | 0 |  | Gas quality analyser | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Gas quality analyser |  |  |  |  | 0 | [8 empty] | 24 VDC | 0 |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Gas quality analyser QT831 | C2NC-1500-GA-QT_831 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : CH4 : 90-100% | GE sensing | 0 | [8 empty] | 9263-4E | 4E | MS-A-QT831 |  | 24 VDC | 0 | 0 | 0 | 0 | 0 | 0 |  | Gas quality analyser | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Gas quality analyser |  |  |  |  | 0 | [8 empty] | 24 VDC | 0 |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Gas quality analyser QT832 | C2NC-1500-GA-QT_832 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : CO2 : 0-10% | GE sensing | 0 | [8 empty] | 9263-4E | 4E | MS-A-QT832 |  | 24 VDC | 0 | 0 | 0 | 0 | 0 | 0 |  | Gas quality analyser | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Gas quality analyser |  |  |  |  | 0 | [8 empty] | 24 VDC | 0 |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Gas quality analyser QT833 | C2NC-1500-GA-QT_833 | C2NC-1500-GA | Instruments | Gas analyser Gas quality analyser. Function: GQA800 : O2 : 0-2% | GE sensing | 0 | [8 empty] | 9263-4E | 4E | MS-A-QT833 |  | 24 VDC | 0 | 0 | 0 | 0 | 0 | 0 |  | Gas quality analyser | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Gas quality analyser |  |  |  |  | 0 | [8 empty] | 24 VDC | 0 |  |  | Gas quality analyser |  | Analog | QT
Gas analyser Pump P820 | C2NC-1500-GA-P_820 | C2NC-1500-GA | Equipment | Gas analyser Pump. Function: 0 | GE sensing | 0 | [8 empty] | 9263-4E | 4E | MS-A-P820 |  | 115 VAC | 0 | 0 | 0 | 0 | 0 | 0 |  | Pump | [7 empty] | 0 |  |  |  |  | 0 | [5 empty] | Pump |  |  |  |  | 0 | [8 empty] | 115 VAC | 0 |  |  | Pump |  |  | P
Membranes stage 2B Ball valve V413 | C2NC-1500-MBR-V_413 | C2NC-1500-MBR | Valves | Membranes stage 2B Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C3 | 4C3 | MS-A-V413 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes stage 1 Butterfly valve V420 | C2NC-1500-MBR-V_420 | C2NC-1500-MBR | Valves | Membranes stage 1 Butterfly valve. Function: BLOCK IN MEMBRANES | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C1 | 4C1 | MS-A-V420 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 8" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes stage 1 Butterfly valve V421 | C2NC-1500-MBR-V_421 | C2NC-1500-MBR | Valves | Membranes stage 1 Butterfly valve. Function: BLOCK IN MEMBRANES | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C1 | 4C1 | MS-A-V421 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes stage 2B Butterfly valve V430 | C2NC-1500-MBR-V_430 | C2NC-1500-MBR | Valves | Membranes stage 2B Butterfly valve. Function: BLOCK OUTLET MEMBRANE SYSTEM | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C3 | 4C3 | MS-A-V430 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes stage 2B Butterfly valve V431 | C2NC-1500-MBR-V_431 | C2NC-1500-MBR | Valves | Membranes stage 2B Butterfly valve. Function: BLOCK OUTLET MEMBRANE SYSTEM | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C3 | 4C3 | MS-A-V431 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes Ball valve V500 | C2NC-1500-MBR-V_500 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V500 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V501 | C2NC-1500-MBR-V_501 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: ISOLATE SAMPLE LINE | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V501 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V510 | C2NC-1500-MBR-V_510 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V510 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V511 | C2NC-1500-MBR-V_511 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V511 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Butterfly valve V512 | C2NC-1500-MBR-V_512 | C2NC-1500-MBR | Valves | Membranes Butterfly valve. Function: BLOCK START-UP LINE | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C | 4C | MS-A-V512 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes Butterfly valve V513 | C2NC-1500-MBR-V_513 | C2NC-1500-MBR | Valves | Membranes Butterfly valve. Function: BLOCK OUTLET MEMBRANE SYSTEM | Apollo valves | Double Offset High Performance | [8 empty] | 9263-4C | 4C | MS-A-V513 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 6" #300 |  | Butterfly valve | [7 empty] | 725 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Butterfly valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Butterfly valve |  |  | V
Membranes Ball valve V521 | C2NC-1500-MBR-V_521 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: ISOLATE SAMPLE LINE | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V521 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V522 | C2NC-1500-MBR-V_522 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V522 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V550 | C2NC-1500-MBR-V_550 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: BLOCK PRESSURE TRANSMITTER | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V550 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V631 | C2NC-1500-MBR-V_631 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: SAMPLE/DRAIN | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V631 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Membranes Ball valve V632 | C2NC-1500-MBR-V_632 | C2NC-1500-MBR | Valves | Membranes Ball valve. Function: ISOLATE SAMPLE LINE | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4C | 4C | MS-A-V632 |  | NA | NA | NA | NA | BIOGAS | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | BIOGAS | [5 empty] | Ball valve |  |  |  |  | BIOGAS | [8 empty] | NA | BIOGAS |  |  | Ball valve |  |  | V
Compressed gas treatment Butterfly valve V740 | C2NC-1500-CGT-V_740 | C2NC-1500-CGT | Valves | Compressed gas treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Apollo valves | 215 | [8 empty] | 9263-4B | 4B | MS-A-V740 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Compressed gas treatment Butterfly valve V741 | C2NC-1500-CGT-V_741 | C2NC-1500-CGT | Valves | Compressed gas treatment Butterfly valve. Function: ISOLATE HEAT EXCHANGER | Apollo valves | 215 | [8 empty] | 9263-4B | 4B | MS-A-V741 |  | NA | NA | NA | NA | GLYCOL MIXTURE | AISI 316 / EPDM | 4" 150# |  | Butterfly valve | [7 empty] | 16 Barg - 230 Psig |  |  |  |  | GLYCOL MIXTURE | [5 empty] | Butterfly valve |  |  |  |  | GLYCOL MIXTURE | [8 empty] | NA | GLYCOL MIXTURE |  |  | Butterfly valve |  |  | V
Container unit Ball valve V910 | C2NC-1500-CU-V_910 | C2NC-1500-CU | Valves | Container unit Ball valve. Function: ISOLATE INSTRUMENT AIRLINE | FLO-TITE | Model 300 - 3 PC Full Port Ball Valves | [8 empty] | 9263-4F | 4F | MS-A-V910 |  | NA | NA | NA | NA | INSTRUMENT AIR | AISI 316 / PTFE | 1" SW |  | Ball valve | [7 empty] | 1500 @ 150ºF |  |  |  |  | INSTRUMENT AIR | [5 empty] | Ball valve |  |  |  |  | INSTRUMENT AIR | [8 empty] | NA | INSTRUMENT AIR |  |  | Ball valve |  |  | V
Container unit Ball valve V911 | C2NC-1500-CU-V_911 | C2NC-1500-CU | Valves | Container unit Ball valve. Function: SAMPLE/DRAIN/CLEANING | FLO-TITE | Model T82SS - 2 PC Full Bore Economical Ball Valves | [8 empty] | 9263-4F | 4F | MS-A-V911 |  | NA | NA | NA | NA | INSTRUMENT AIR | AISI 316 / PTFE | 1/2" NPT |  | Ball valve | [7 empty] | 1000 Psig @ 100°F |  |  |  |  | INSTRUMENT AIR | [5 empty] | Ball valve |  |  |  |  | INSTRUMENT AIR | [8 empty] | NA | INSTRUMENT AIR |  |  | Ball valve |  |  | V
Container unit Manual valve V914 | C2NC-1500-CU-V_914 | C2NC-1500-CU | Valves | Container unit Manual valve. Function: block air flow | Greenhack | Part of GR914 | [8 empty] | 9263-4F | 4F | MS-A-V914 |  | 0 | 0 | 0 | 0 | Ambient air | Aluminium | 24x24" |  | Manual valve | [7 empty] | 0 |  |  |  |  | Ambient air | [5 empty] | Manual valve |  |  |  |  | Ambient air | [8 empty] | 0 | Ambient air |  |  | Manual valve |  |  | V
Container unit Manual valve V915 | C2NC-1500-CU-V_915 | C2NC-1500-CU | Valves | Container unit Manual valve. Function: block air flow | Greenhack | Part of GR914 | [8 empty] | 9263-4F | 4F | MS-A-V915 |  | 0 | 0 | 0 | 0 | Ambient air | Aluminium | 24x24" |  | Manual valve | [7 empty] | 0 |  |  |  |  | Ambient air | [5 empty] | Manual valve |  |  |  |  | Ambient air | [8 empty] | 0 | Ambient air |  |  | Manual valve |  |  | V
Control area container Heater HE900 | C2NC-1500-CU-HE_900 | C2NC-1500-CU | Equipment | Control area container Heater. Function: Heating | TPI Corporation | Hazardous-Location Electric Heater, 3.6 kW, 480V AC, 3-phase, Convection Heating Method | [8 empty] | 9263-4F | 4F | MS-A-HE900 |  | 480 VAC | NA | NA | NA | Ambient air | Steel | 40x18x9" |  | Heater | [7 empty] | 0 |  |  |  |  | Ambient air | [5 empty] | Heater |  |  |  |  | Ambient air | [8 empty] | 480 VAC | Ambient air |  |  | Heater |  |  | HE
Control area container Grid GR900 | C2NC-1500-CU-GR_900 | C2NC-1500-CU | Equipment | Control area container Grid. Function: Air inlet | Systemair | PZAL-500x500-S | [8 empty] | 9263-4F | 4F | MS-A-GR900 |  | 0 | 0 | 0 | 0 | Ambient air | Aluminium | 500x500 mm |  | Grid | [7 empty] | 0 |  |  |  |  | Ambient air | [5 empty] | Grid |  |  |  |  | Ambient air | [8 empty] | 0 | Ambient air |  |  | Grid |  |  | GR
Control area container Fan FA900 | C2NC-1500-CU-FA_900 | C2NC-1500-CU | Equipment | Control area container Fan. Function: Refresh air inside container | J&D Manufacturing | VES201C | [8 empty] | 9263-4F | 4F | MS-A-FA900 |  | 120 VAC | NA | NA | NA | Ambient air | Aluminium | 500x500 mm |  | Fan | [7 empty] | 0 |  |  |  |  | Ambient air | [5 empty] | Fan |  |  |  |  | Ambient air | [8 empty] | 120 VAC | Ambient air |  |  | Fan |  |  | FA
Control area container Manual valve V900 | C2NC-1500-CU-V_900 | C2NC-1500-CU | Valves | Control area container Manual valve. Function: Block air flow | Systemair | RK-500x500-R | [8 empty] | 9263-4F | 4F | MS-A-V900 |  | 0 | 0 | 0 | 0 | Ambient air | Aluminium | 500x500 mm |  | Manual valve | [7 empty] | 0 |  |  |  |  | Ambient air | [5 empty] | Manual valve |  |  |  |  | Ambient air | [8 empty] | 0 | Ambient air |  |  | Manual valve |  |  | V
Control area container Emergency stop ES900 | C2NC-1500-CU-ES_900 | C2NC-1500-CU | Instruments | Control area container Emergency stop. Function: STOP INSTALLATION | Schneider | 9001SK | [8 empty] | 9263-4F | 4F | MS-A-ES900 |  | 24 VDC | NA | NA | NA | NA | - | 0 |  | Emergency stop | [7 empty] | NA |  |  |  |  | NA | [5 empty] | Emergency stop |  |  |  |  | NA | [8 empty] | 24 VDC | NA |  |  | Emergency stop |  |  | ES
Control area container Manual valve V901 | C2NC-1500-CU-V_901 | C2NC-1500-CU | Valves | Control area container Manual valve. Function: Block air flow | Systemair | RK-400x400-R | [8 empty] | 9263-4F | 4F | MS-A-V901 |  | 0 | 0 | 0 | 0 | Ambient air | Aluminium | 400x400 mm |  | Manual valve | [7 empty] | 0 |  |  |  |  | Ambient air | [5 empty] | Manual valve |  |  |  |  | Ambient air | [8 empty] | 0 | Ambient air |  |  | Manual valve |  |  | V
Control area container Grid GR901 | C2NC-1500-CU-GR_901 | C2NC-1500-CU | Equipment | Control area container Grid. Function: Air outlet | Systemair | PZAL-400x400-S | [8 empty] | 9263-4F | 4F | MS-A-GR901 |  | 0 | 0 | 0 | 0 | Ambient air | Aluminium | 400x400 mm |  | Grid | [7 empty] | 0 |  |  |  |  | Ambient air | [5 empty] | Grid |  |  |  |  | Ambient air | [8 empty] | 0 | Ambient air |  |  | Grid |  |  | GR
Control area container Temperature transmitter TT900 | C2NC-1500-CU-TT_900 | C2NC-1500-CU | Instruments | Control area container Temperature transmitter. Function: MEASURE TEMPERATURE CONTROL ROOM | Endress & Hauser | TST434-J1A4DW (inclusive TMT181-I PCP FM+CSA, Class I, Div 1+2 ) RTD Thermometer TST434 | [8 empty] | 9263-4F | 4F | MS-A-TT900 |  | 24 VDC | NA | NA | NA | Ambient air | Composition of materials | NA |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | Ambient air | [5 empty] | Temperature transmitter |  |  |  |  | Ambient air | [8 empty] | 24 VDC | Ambient air |  |  | Temperature transmitter |  | Analog | TT
Control area container Temperature transmitter TT901 | C2NC-1500-CU-TT_901 | C2NC-1500-CU | Instruments | Control area container Temperature transmitter. Function: MEASURE TEMPERATURE OF AMBIENT | Endress & Hauser | TST434-J1A4DW (inclusive TMT181-I PCP FM+CSA, Class I, Div 1+2 ) RTD Thermometer TST434 | [8 empty] | 9263-4F | 4F | MS-A-TT901 |  | 24 VDC | NA | NA | NA | Ambient air | Composition of materials | NA |  | Temperature transmitter | [7 empty] | NA |  |  |  |  | Ambient air | [5 empty] | Temperature transmitter |  |  |  |  | Ambient air | [8 empty] | 24 VDC | Ambient air |  |  | Temperature transmitter |  | Analog | TT
Sales gas compressor Sales gas compressor GC570 | C2NC-1500-GC-GC_570 | C2NC-1500-GC | Equipment | Sales gas compressor Sales gas compressor. Function: PRESSURIZE GAS | Safe | SW373B10,5-EM | [8 empty] | 9263-5A | 5A | MS-A-GC570 |  | 0 | 0 | 0 | 0 | Gas | Composition of materials | 6" 150# in / 2" 600# out |  | Sales gas compressor | [7 empty] | 0 |  |  |  |  | Gas | [5 empty] | Sales gas compressor |  |  |  |  | Gas | [8 empty] | 0 | Gas |  |  | Sales gas compressor |  | Analog | GC
Sales gas compressor Dry cooler fan FA570 | C2NC-1500-GC-FA_570 | C2NC-1500-GC | Equipment | Sales gas compressor Dry cooler fan. Function: PRESSURIZE GAS | Thermokey | V shaped 8 fan air cooler 22F0013086 | [8 empty] | 9263-5A | 5A | MS-A-FA570 |  | 0 | 0 | 0 | 0 | Gas | Composition of materials | 3" 150# |  | Dry cooler fan | [7 empty] | 0 |  |  |  |  | Gas | [5 empty] | Dry cooler fan |  |  |  |  | Gas | [8 empty] | 0 | Gas |  |  | Dry cooler fan |  |  | FA

## 1600 - Utilities
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual RQD | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Material of Construction | Instrument Diameter | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes
Utilities Compressed Air | C2NC-1600-CMP | C2NC-1600 | Locations And Facilities | Utilities Compressed Air
Utilities Service Water | C2NC-1600-SW | C2NC-1600 | Locations And Facilities | Utilities Service Water
Utilities Potable Water | C2NC-1600-PW | C2NC-1600 | Locations And Facilities | Utilities Potable Water
Utilities Hot Water | C2NC-1600-HW | C2NC-1600 | Locations And Facilities | Utilities Hot Water
Utilities Boiler | C2NC-1600-BOL | C2NC-1600 | Locations And Facilities | Utilities Boiler
Utilities Flares | C2NC-1600-FL | C2NC-1600 | Locations And Facilities | Utilities Flares
Utilities Natural Gas | C2NC-1600-NG | C2NC-1600 | Locations And Facilities | Utilities Natural Gas
1 Inch Tube Compressed Air Line 02 | CNC2-1600-1_WC01_AI_1640_02 | C2NC-1600 | Lines | 1 Inch Tube Compressed Air Line | [11 empty] | D0-2 | 1_WC01_AI_1640_02 | [10 empty] | Compressed Air | Tube | 1 inch |  |  | N
1 Inch Tube Compressed Air Line 03 | CNC2-1600-1_WC01_AI_1640_03 | C2NC-1600 | Lines | 1 Inch Tube Compressed Air Line | [11 empty] | D0-9 | 1_WC01_AI_1640_03 | [10 empty] | Compressed Air | Tube | 1 inch |  |  | N
1 Inch Tube Compressed Air Line 04 | CNC2-1600-1_WC01_AI_1640_04 | C2NC-1600 | Lines | 1 Inch Tube Compressed Air Line | [11 empty] | D0-9 | 1_WC01_AI_1640_04 | [10 empty] | Compressed Air | Tube | 1 inch |  |  | N
3 Inch PVC Service Water Line 06 | CNC2-1600-3_AC30_WS_1610_06 | C2NC-1600 | Lines | 3 Inch PVC Service Water Line | [11 empty] | D0-1 | 3_AC30_WS_1610_06 | [10 empty] | Service Water | PVC | 3 inch |  |  | N
4 Inch PVC Hot Water Line 09 | CNC2-1600-4_AC30_WH_1634_09 | C2NC-1600 | Lines | 4 Inch PVC Hot Water Line | [11 empty] | D0-9 | 4_AC30_WH_1634_09 | [10 empty] | Hot Water | PVC | 4 inch |  |  | N
4 Inch PVC Hot Water Line 10 | CNC2-1600-4_AC30_WH_1634_10 | C2NC-1600 | Lines | 4 Inch PVC Hot Water Line | [11 empty] | D0-9 | 4_AC30_WH_1634_10 | [10 empty] | Hot Water | PVC | 4 inch |  |  | N
4 Inch PVC Hot Water Line 11 | CNC2-1600-4_AC30_WH_1634_11 | C2NC-1600 | Lines | 4 Inch PVC Hot Water Line | [11 empty] | D0-9 | 4_AC30_WH_1634_11 | [10 empty] | Hot Water | PVC | 4 inch |  |  | N
4 Inch PVC Hot Water Line 07 | CNC2-1600-4_AC30_WH_1640_07 | C2NC-1600 | Lines | 4 Inch PVC Hot Water Line | [11 empty] | D0-2 | 4_AC30_WH_1640_07 | [10 empty] | Hot Water | PVC | 4 inch |  |  | N
4 Inch PVC Hot Water Line 08 | CNC2-1600-4_AC30_WH_1640_08 | C2NC-1600 | Lines | 4 Inch PVC Hot Water Line | [11 empty] | D0-2 | 4_AC30_WH_1640_08 | [10 empty] | Hot Water | PVC | 4 inch |  |  | N
6 Inch PVC Hot Water Line 07 | CNC2-1600-6_AC30_WH_1640_07 | C2NC-1600 | Lines | 6 Inch PVC Hot Water Line | [11 empty] | D0-2 | 6_AC30_WH_1640_07 | [10 empty] | Hot Water | PVC | 6 inch |  |  | N
6 Inch PVC Hot Water Line 08 | CNC2-1600-6_AC30_WH_1640_08 | C2NC-1600 | Lines | 6 Inch PVC Hot Water Line | [11 empty] | D0-2 | 6_AC30_WH_1640_08 | [10 empty] | Hot Water | PVC | 6 inch |  |  | N
6 Inch PVC Hot Water Line 09 | CNC2-1600-6_AC30_WH_1640_09 | C2NC-1600 | Lines | 6 Inch PVC Hot Water Line | [11 empty] | D0-9 | 6_AC30_WH_1640_09 | [10 empty] | Hot Water | PVC | 6 inch |  |  | N
6 Inch PVC Hot Water Line 10 | CNC2-1600-6_AC30_WH_1640_10 | C2NC-1600 | Lines | 6 Inch PVC Hot Water Line | [11 empty] | D0-9 | 6_AC30_WH_1640_10 | [10 empty] | Hot Water | PVC | 6 inch |  |  | N
6 Inch PVC Hot Water Line 11 | CNC2-1600-6_AC30_WH_1640_11 | C2NC-1600 | Lines | 6 Inch PVC Hot Water Line | [11 empty] | D0-9 | 6_AC30_WH_1640_11 | [10 empty] | Hot Water | PVC | 6 inch |  |  | N

## 1700 - BioSolids
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Material of Construction | Instrument Diameter | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes
Utilities Dryer | C2NC-1600-DR | C2NC-1600 | Locations And Facilities | Utilities Dryer

## 1700 working tab
P&ID DRW # | P&ID sheet | tag | Instrument des | Motor des | type
139-401

## 1800 - Water Managment
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Material of Construction | Instrument Diameter | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes
Aeration Blowers - Aeration blower A | C2NC-1800-ABL-B_63500 | C2NC-1800-ABL | Equipment | Aeration blower A | Aerzen | [8 empty] | AN-0119 A01-01 | 9 | B_63500 | [8 empty] | Blower | [25 empty] | 9.36 x 7.56 | 7.7
Aeration Blowers - Aeration blower B | C2NC-1800-ABL-B_63501 | C2NC-1800-ABL | Equipment | Aeration blower B | Aerzen | [8 empty] | AN-0119 A01-01 | 9 | B_63501 | [8 empty] | Blower | [25 empty] | 9.36 x 7.56 | 7.7
Aeration Blowers - Aeration blower C | C2NC-1800-ABL-B_63502 | C2NC-1800-ABL | Equipment | Aeration blower C | Aerzen | [8 empty] | AN-0119 A01-01 | 9 | B_63502 | [8 empty] | Blower | [25 empty] | 9.36 x 7.56 | 7.7
Aeration Blowers - Aeration blower D | C2NC-1800-ABL-B_63503 | C2NC-1800-ABL | Equipment | Aeration blower D | Aerzen | [8 empty] | AN-0119 A01-01 | 9 | B_63503 | [8 empty] | Blower | [25 empty] | 9.36 x 7.56 | 7.7
Aeration Blowers - Aeration blower E | C2NC-1800-ABL-B_63504 | C2NC-1800-ABL | Equipment | Aeration blower E | Aerzen | [8 empty] | AN-0119 A01-01 | 9 | B_63504 | [8 empty] | Blower | [25 empty] | 9.36 x 7.56 | 7.7
Anoxic Tank - Submersible mixer in Anoxic tank A | C2NC-1800-ANX-MX_63100A | C2NC-1800-ANX | Equipment | Submersible mixer in Anoxic tank A | UTS Products | [8 empty] | AN-0119 A01-01 | 6 | MX_63100A | [8 empty] | Mixer
Anoxic Tank - Submersible mixer in Anoxic tank A | C2NC-1800-ANX-MX_63100B | C2NC-1800-ANX | Equipment | Submersible mixer in Anoxic tank A | UTS Products | [8 empty] | AN-0119 A01-01 | 6 | MX_63100B | [8 empty] | Mixer
Anoxic Tank - Submersible mixer in Anoxic tank A | C2NC-1800-ANX-MX_63100C | C2NC-1800-ANX | Equipment | Submersible mixer in Anoxic tank A | UTS Products | [8 empty] | AN-0119 A01-01 | 6 | MX_63100C | [8 empty] | Mixer
Anoxic Tank - Submersible mixer in Anoxic tank A | C2NC-1800-ANX-MX_63100D | C2NC-1800-ANX | Equipment | Submersible mixer in Anoxic tank A | UTS Products | [8 empty] | AN-0119 A01-01 | 6 | MX_63100D | [8 empty] | Mixer
Anoxic Tank - Aeration feed pump A - from anoxic tank to aerobic tank | C2NC-1800-ANX-P_63101 | C2NC-1800-ANX | Equipment | Aeration feed pump A - from anoxic tank to aerobic tank | [9 empty] | AN-0119 A01-01 | 6 | P_63101 | [8 empty] | Pump
Anoxic Tank - Aeration feed pump B - from anoxic tank to aerobic tank | C2NC-1800-ANX-P_63102 | C2NC-1800-ANX | Equipment | Aeration feed pump B - from anoxic tank to aerobic tank | [9 empty] | AN-0119 A01-01 | 6 | P_63102 | [8 empty] | Pump
Anoxic Tank - Aeration feed pump C - from anoxic tank to aerobic tank | C2NC-1800-ANX-P_63103 | C2NC-1800-ANX | Equipment | Aeration feed pump C - from anoxic tank to aerobic tank | [9 empty] | AN-0119 A01-01 | 6 | P_63103 | [8 empty] | Pump
Caustic Dosing System - Sodium hydroxide feed pump A | C2NC-1800-CHEM-CAUS-P_31100A | C2NC-1800-CHEM-CAUS | Equipment | Sodium hydroxide feed pump A | [9 empty] | AN-0119 A01-01 | 19 | P_31100A | [8 empty] | Pump
Caustic Dosing System - Sodium hydroxide feed pump B | C2NC-1800-CHEM-CAUS-P_31100B | C2NC-1800-CHEM-CAUS | Equipment | Sodium hydroxide feed pump B | [9 empty] | AN-0119 A01-01 | 19 | P_31100B | [8 empty] | Pump
Acid Dosing System - Citric acid feed pump | C2NC-1800-CHEM-CITR-P_32100 | C2NC-1800-CHEM-CITR | Equipment | Citric acid feed pump | [9 empty] | AN-0119 A01-01 | 19 | P_32100 | [8 empty] | Pump
Antifoam Dosing System - Antifoam feed pump A | C2NC-1800-CHEM-FOAM-P_37100A | C2NC-1800-CHEM-FOAM | Equipment | Antifoam feed pump A | [9 empty] | AN-0119 A01-01 | 19 | P_37100A | [8 empty] | Pump
Antifoam Dosing System - Antifoam feed pump B | C2NC-1800-CHEM-FOAM-P_37100B | C2NC-1800-CHEM-FOAM | Equipment | Antifoam feed pump B | [9 empty] | AN-0119 A01-01 | 19 | P_37100B | [8 empty] | Pump
Sodium Hypochlorite System - Sodium hypochlorite feed pump | C2NC-1800-CHEM-HYPO-P_31200 | C2NC-1800-CHEM-HYPO | Equipment | Sodium hypochlorite feed pump | [9 empty] | AN-0119 A01-01 | 19 | P_31200 | [8 empty] | Pump
Emulsion Polymer WAS - Emulsion polymer make-up unit for WAS dewatering polymer system | C2NC-1800-FLOC-PHU_35200 | C2NC-1800-FLOC | Equipment | Emulsion polymer make-up unit for WAS dewatering polymer system | [9 empty] | AN-0119 A01-01 | 17 | PHU_35200 | [8 empty] | Polymer Makeup Unit
MBR - Membrane Blower A | C2NC-1800-MBR-B_65101 | C2NC-1800-MBR | Equipment | Membrane Blower A | Anaergia IS | [8 empty] | AN-0119 A01-01 | 12 | B_65101 | [8 empty] | Blower | [25 empty] | 40 x 8 | 9.5
MBR - Membrane Blower B | C2NC-1800-MBR-B_65102 | C2NC-1800-MBR | Equipment | Membrane Blower B | Anaergia IS | [8 empty] | AN-0119 A01-01 | 12 | B_65102 | [8 empty] | Blower | [25 empty] | 40 x 8 | 9.5
MBR - Membrane permeate ejector | C2NC-1800-MBR-EJ_65100 | C2NC-1800-MBR | Equipment | Membrane permeate ejector | [9 empty] | AN-0119 A01-01 | 10 | EJ_65100 | [8 empty] | Ejector
MBR - Membrane A in membrane tank A | C2NC-1800-MBR-MEM_65100A | C2NC-1800-MBR | Equipment | Membrane A in membrane tank A | Fibracast | [8 empty] | AN-0119 A01-01 | 10 | MEM_65100A | [8 empty] | Membrane
MBR - Membrane B in membrane tank A | C2NC-1800-MBR-MEM_65100B | C2NC-1800-MBR | Equipment | Membrane B in membrane tank A | Fibracast | [8 empty] | AN-0119 A01-01 | 10 | MEM_65100B | [8 empty] | Membrane
MBR - Membrane A in membrane tank B | C2NC-1800-MBR-MEM_65101A | C2NC-1800-MBR | Equipment | Membrane A in membrane tank B | Fibracast | [8 empty] | AN-0119 A01-01 | 10 | MEM_65101A | [8 empty] | Membrane
MBR - Membrane B in membrane tank B | C2NC-1800-MBR-MEM_65101B | C2NC-1800-MBR | Equipment | Membrane B in membrane tank B | Fibracast | [8 empty] | AN-0119 A01-01 | 10 | MEM_65101B | [8 empty] | Membrane
Permeate System - Permeate Pump A | C2NC-1800-PRM-P_65301 | C2NC-1800-PRM | Equipment | Permeate Pump A | Anaergia IS | [8 empty] | AN-0119 A01-01 | 13 | P_65301 | [8 empty] | Pump | [25 empty] | 40 x 8 | 9.5
Permeate System - Permeate Pump B | C2NC-1800-PRM-P_65302 | C2NC-1800-PRM | Equipment | Permeate Pump B | Anaergia IS | [8 empty] | AN-0119 A01-01 | 13 | P_65302 | [8 empty] | Pump | [25 empty] | 40 x 8 | 9.5
Permeate System - Permeate Tank | C2NC-1800-PRM-TK_65300 | C2NC-1800-PRM | Equipment | Permeate Tank | [9 empty] | AN-0119 A01-01 | 13 | TK_65300 | [8 empty] | Tank
WAS and RAS Systems - Return Activated Sludge Pump A | C2NC-1800-RAS-P_65203 | C2NC-1800-RAS | Equipment | Return Activated Sludge Pump A | Anaergia IS | [8 empty] | AN-0119 A01-01 | 14 | P_65203 | [8 empty] | Pump | [25 empty] | 40 x 8 | 9.5
WAS and RAS Systems - Return Activated Sludge Pump B | C2NC-1800-RAS-P_65204 | C2NC-1800-RAS | Equipment | Return Activated Sludge Pump B | Anaergia IS | [8 empty] | AN-0119 A01-01 | 14 | P_65204 | [8 empty] | Pump | [25 empty] | 40 x 8 | 9.5
WAS and RAS Systems - Waste Activated Sludge Pump A | C2NC-1800-RAS-P_65206 | C2NC-1800-RAS | Equipment | Waste Activated Sludge Pump A | Anaergia IS | [8 empty] | AN-0119 A01-01 | 15 | P_65206 | [8 empty] | Pump | [25 empty] | 7.2 x 8 | 4.33
WAS and RAS Systems - Waste Activated Sludge Pump B | C2NC-1800-RAS-P_65207 | C2NC-1800-RAS | Equipment | Waste Activated Sludge Pump B | Anaergia IS | [8 empty] | AN-0119 A01-01 | 15 | P_65207 | [8 empty] | Pump | [25 empty] | 7.2 x 8 | 4.33
WAS Screw Dewatering Press - Mixer for WAS Dewatering Press Flocculation Tank | C2NC-1800-WAS-MX_51401 | C2NC-1800-WAS | Equipment | Mixer for WAS Dewatering Press Flocculation Tank | [9 empty] | AN-0119 A01-01 | 16 | MX_51401 | [8 empty] | Mixer
WAS Screw Dewatering Press - WAS Dewatering Screw Press | C2NC-1800-WAS-PKG_51400 | C2NC-1800-WAS | Equipment | WAS Dewatering Screw Press | [9 empty] | AN-0119 A01-01 | 16 | PKG_51400 | [8 empty] | Package | [25 empty] | 16.4 x ???
Aeration Blowers - Differential Pressure Indicator - DPI_63500 | C2NC-1800-ABL-DPI_63500 | C2NC-1800-ABL | Instruments | Differential Pressure Indicator within the Aeration Blowers system - Differential pressure gauge for aeration blower (B-63500) | Wika | 716.11 |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | DPI_63500 | [42 empty] | AA |  |  |  | Differential Pressure Indicator
Aeration Blowers - Differential Pressure Indicator - DPI_63501 | C2NC-1800-ABL-DPI_63501 | C2NC-1800-ABL | Instruments | Differential Pressure Indicator within the Aeration Blowers system - Differential pressure gauge for aeration blower (B-63501) | Wika | 716.11 |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | DPI_63501 | [42 empty] | AA |  |  |  | Differential Pressure Indicator
Aeration Blowers - Differential Pressure Indicator - DPI_63502 | C2NC-1800-ABL-DPI_63502 | C2NC-1800-ABL | Instruments | Differential Pressure Indicator within the Aeration Blowers system - Differential pressure gauge for aeration blower (B-63502) | Wika | 716.11 |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | DPI_63502 | [42 empty] | AA |  |  |  | Differential Pressure Indicator
Aeration Blowers - Differential Pressure Indicator - DPI_63503 | C2NC-1800-ABL-DPI_63503 | C2NC-1800-ABL | Instruments | Differential Pressure Indicator within the Aeration Blowers system - Differential pressure gauge for aeration blower (B-63503) | Wika | 716.11 |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | DPI_63503 | [42 empty] | AA |  |  |  | Differential Pressure Indicator
Aeration Blowers - Differential Pressure Indicator - DPI_63504 | C2NC-1800-ABL-DPI_63504 | C2NC-1800-ABL | Instruments | Differential Pressure Indicator within the Aeration Blowers system - Differential pressure gauge for aeration blower (B-63504) | Wika | 716.11 |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | DPI_63504 | [42 empty] | AA |  |  |  | Differential Pressure Indicator
Aeration Blowers - Flow Switch - FS_63500 | C2NC-1800-ABL-FS_63500 | C2NC-1800-ABL | Instruments | Flow Switch within the Aeration Blowers system - Flow switch for air line from aeration blower (B-63500) | ACControls | Sierra 616 InnovaSwitch 615-FS42-NX-N04-S6-2-240-LE-0 |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | FS_63500 | [42 empty] | AA |  |  |  | Flow Switch |  | Digital | Insertion 1/2" MNPT
Aeration Blowers - Flow Switch - FS_63501 | C2NC-1800-ABL-FS_63501 | C2NC-1800-ABL | Instruments | Flow Switch within the Aeration Blowers system - Flow switch for air line from aeration blower (B-63501) | ACControls | Sierra 616 InnovaSwitch 615-FS42-NX-N04-S6-2-240-LE-0 |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | FS_63501 | [42 empty] | AA |  |  |  | Flow Switch |  | Digital | Insertion 1/2" MNPT
Aeration Blowers - Flow Switch - FS_63502 | C2NC-1800-ABL-FS_63502 | C2NC-1800-ABL | Instruments | Flow Switch within the Aeration Blowers system - Flow switch for air line from aeration blower (B-63502) | ACControls | Sierra 616 InnovaSwitch 615-FS42-NX-N04-S6-2-240-LE-0 |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | FS_63502 | [42 empty] | AA |  |  |  | Flow Switch |  | Digital | Insertion 1/2" MNPT
Aeration Blowers - Flow Switch - FS_63503 | C2NC-1800-ABL-FS_63503 | C2NC-1800-ABL | Instruments | Flow Switch within the Aeration Blowers system - Flow switch for air line from aeration blower (B-63503) | ACControls | Sierra 616 InnovaSwitch 615-FS42-NX-N04-S6-2-240-LE-0 |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | FS_63503 | [42 empty] | AA |  |  |  | Flow Switch |  | Digital | Insertion 1/2" MNPT
Aeration Blowers - Flow Switch - FS_63504 | C2NC-1800-ABL-FS_63504 | C2NC-1800-ABL | Instruments | Flow Switch within the Aeration Blowers system - Flow switch for air line from aeration blower (B-63504) | ACControls | Sierra 616 InnovaSwitch 615-FS42-NX-N04-S6-2-240-LE-0 |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | FS_63504 | [42 empty] | AA |  |  |  | Flow Switch |  | Digital | Insertion 1/2" MNPT
Aeration Blowers - Pressure Indicator Transmitter - PIT_63500 | C2NC-1800-ABL-PIT_63500 | C2NC-1800-ABL | Instruments | Pressure Indicator Transmitter within the Aeration Blowers system - PIT for air line to aerobic tank (TK-63200) | Anaergia | (PMC51B-AABADBH63KFA1VXJR+Z1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | PIT_63500 | [42 empty] | AA |  |  |  | Pressure Transmitter w/ indicator |  | Analog | Insertion 1/4" FNPT w/ 1/2" MNPT
Aeration Blowers - Pressure Indicator Transmitter - PIT_63501 | C2NC-1800-ABL-PIT_63501 | C2NC-1800-ABL | Instruments | Pressure Indicator Transmitter within the Aeration Blowers system - PIT for air line to aerobic tank (TK-63300) | Anaergia | (PMC51B-AABADBH63KFA1VXJR+Z1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | PIT_63501 | [42 empty] | AA |  |  |  | Pressure Transmitter w/ indicator |  | Analog | Insertion 1/4" FNPT w/ 1/2" MNPT
Aeration Blowers - Pressure Switch High - PSH_63500 | C2NC-1800-ABL-PSH_63500 | C2NC-1800-ABL | Instruments | Pressure Switch High within the Aeration Blowers system - Pressure switch for aeration blower (B-63500) | Ashcroft | B424BXC815# |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | PSH_63500 | [42 empty] | AA |  |  |  | Pressure Switch High |  | Digital
Aeration Blowers - Pressure Switch High - PSH_63501 | C2NC-1800-ABL-PSH_63501 | C2NC-1800-ABL | Instruments | Pressure Switch High within the Aeration Blowers system - Pressure switch for aeration blower (B-63501) | Ashcroft | B424BXC815# |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | PSH_63501 | [42 empty] | AA |  |  |  | Pressure Switch High |  | Digital
Aeration Blowers - Pressure Switch High - PSH_63502 | C2NC-1800-ABL-PSH_63502 | C2NC-1800-ABL | Instruments | Pressure Switch High within the Aeration Blowers system - Pressure switch for aeration blower (B-63502) | Ashcroft | B424BXC815# |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | PSH_63502 | [42 empty] | AA |  |  |  | Pressure Switch High |  | Digital
Aeration Blowers - Pressure Switch High - PSH_63503 | C2NC-1800-ABL-PSH_63503 | C2NC-1800-ABL | Instruments | Pressure Switch High within the Aeration Blowers system - Pressure switch for aeration blower (B-63503) | Ashcroft | B424BXC815# |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | PSH_63503 | [42 empty] | AA |  |  |  | Pressure Switch High |  | Digital
Aeration Blowers - Pressure Switch High - PSH_63504 | C2NC-1800-ABL-PSH_63504 | C2NC-1800-ABL | Instruments | Pressure Switch High within the Aeration Blowers system - Pressure switch for aeration blower (B-63504) | Ashcroft | B424BXC815# |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | PSH_63504 | [42 empty] | AA |  |  |  | Pressure Switch High |  | Digital
Aeration Blowers - Temperature Indicator - TI_63500 | C2NC-1800-ABL-TI_63500 | C2NC-1800-ABL | Instruments | Temperature Indicator within the Aeration Blowers system - Temperature indicator in air line from aeration blower (B-63500) | Reotemp | LL0601F49-SSTS |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | TI_63500 | [42 empty] | AA |  |  |  | Temperature Indicator |  |  | Insertion 1/2" MNPT
Aeration Blowers - Temperature Indicator - TI_63501 | C2NC-1800-ABL-TI_63501 | C2NC-1800-ABL | Instruments | Temperature Indicator within the Aeration Blowers system - Temperature indicator in air line from aeration blower (B-63501) | Reotemp | LL0601F49-SSTS |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | TI_63501 | [42 empty] | AA |  |  |  | Temperature Indicator |  |  | Insertion 1/2" MNPT
Aeration Blowers - Temperature Indicator - TI_63502 | C2NC-1800-ABL-TI_63502 | C2NC-1800-ABL | Instruments | Temperature Indicator within the Aeration Blowers system - Temperature indicator in air line from aeration blower (B-63502) | Reotemp | LL0601F49-SSTS |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | TI_63502 | [42 empty] | AA |  |  |  | Temperature Indicator |  |  | Insertion 1/2" MNPT
Aeration Blowers - Temperature Indicator - TI_63503 | C2NC-1800-ABL-TI_63503 | C2NC-1800-ABL | Instruments | Temperature Indicator within the Aeration Blowers system - Temperature indicator in air line from aeration blower (B-63503) | Reotemp | LL0601F49-SSTS |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | TI_63503 | [42 empty] | AA |  |  |  | Temperature Indicator |  |  | Insertion 1/2" MNPT
Aeration Blowers - Temperature Indicator - TI_63504 | C2NC-1800-ABL-TI_63504 | C2NC-1800-ABL | Instruments | Temperature Indicator within the Aeration Blowers system - Temperature indicator in air line from aeration blower (B-63504) | Reotemp | LL0601F49-SSTS |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | TI_63504 | [42 empty] | AA |  |  |  | Temperature Indicator |  |  | Insertion 1/2" MNPT
Aeration Blowers - Temperature Transmitter w/ Indicator - TIT_63500 | C2NC-1800-ABL-TIT_63500 | C2NC-1800-ABL | Instruments | Temperature Transmitter w/ Indicator within the Aeration Blowers system - TIT for air line to aerobic tank (TK-63200) | Endress and Hauser | RTD Assembly TH13, TW type US Style TH13-2A23A2GILAAK |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | TIT_63500 | [42 empty] | AA |  |  |  | Temperature Transmitter w/ Indicator |  | Analog | Insertion 3/4" MNPT
Aeration Blowers - Temperature Transmitter w/ Indicator - TIT_63501 | C2NC-1800-ABL-TIT_63501 | C2NC-1800-ABL | Instruments | Temperature Transmitter w/ Indicator within the Aeration Blowers system - TIT for air line to aerobic tank (TK-63300) | Endress and Hauser | RTD Assembly TH13, TW type US Style TH13-2A23A2GILAAK |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 9 | TIT_63501 | [42 empty] | AA |  |  |  | Temperature Transmitter w/ Indicator |  | Analog | Insertion 3/4" MNPT
Aeration Blowers - Temperature Switch - TS_63500 | C2NC-1800-ABL-TS_63500 | C2NC-1800-ABL | Instruments | Temperature Switch within the Aeration Blowers system - Temperature switch for aeration blower (B-63500) | Ashcroft | T420T05030XNH 150-260F |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | TS_63500 | [42 empty] | AA |  |  |  | Temperature Switch |  | Digital
Aeration Blowers - Temperature Switch - TS_63501 | C2NC-1800-ABL-TS_63501 | C2NC-1800-ABL | Instruments | Temperature Switch within the Aeration Blowers system - Temperature switch for aeration blower (B-63501) | Ashcroft | T420T05030XNH 150-260F |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | TS_63501 | [42 empty] | AA |  |  |  | Temperature Switch |  | Digital
Aeration Blowers - Temperature Switch - TS_63502 | C2NC-1800-ABL-TS_63502 | C2NC-1800-ABL | Instruments | Temperature Switch within the Aeration Blowers system - Temperature switch for aeration blower (B-63502) | Ashcroft | T420T05030XNH 150-260F |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | TS_63502 | [42 empty] | AA |  |  |  | Temperature Switch |  | Digital
Aeration Blowers - Temperature Switch - TS_63503 | C2NC-1800-ABL-TS_63503 | C2NC-1800-ABL | Instruments | Temperature Switch within the Aeration Blowers system - Temperature switch for aeration blower (B-63503) | Ashcroft | T420T05030XNH 150-260F |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | TS_63503 | [42 empty] | AA |  |  |  | Temperature Switch |  | Digital
Aeration Blowers - Temperature Switch - TS_63504 | C2NC-1800-ABL-TS_63504 | C2NC-1800-ABL | Instruments | Temperature Switch within the Aeration Blowers system - Temperature switch for aeration blower (B-63504) | Ashcroft | T420T05030XNH 150-260F |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | TS_63504 | [42 empty] | AA |  |  |  | Temperature Switch |  | Digital
Aeration Blowers - Temperature Switch High - TSH_63500 | C2NC-1800-ABL-TSH_63500 | C2NC-1800-ABL | Instruments | Temperature Switch High within the Aeration Blowers system - Temperature switch for aeration blower (B-63500) | Westinghouse | Manufacturer supplied thermocouple |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | TSH_63500 | [42 empty] | AA |  |  |  | Temperature Switch High |  | Digital
Aeration Blowers - Temperature Switch High - TSH_63501 | C2NC-1800-ABL-TSH_63501 | C2NC-1800-ABL | Instruments | Temperature Switch High within the Aeration Blowers system - Temperature switch for aeration blower (B-63501) | Westinghouse | Manufacturer supplied thermocouple |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | TSH_63501 | [42 empty] | AA |  |  |  | Temperature Switch High |  | Digital
Aeration Blowers - Temperature Switch High - TSH_63502 | C2NC-1800-ABL-TSH_63502 | C2NC-1800-ABL | Instruments | Temperature Switch High within the Aeration Blowers system - Temperature switch for aeration blower (B-63502) | Westinghouse | Manufacturer supplied thermocouple |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | TSH_63502 | [42 empty] | AA |  |  |  | Temperature Switch High |  | Digital
Aeration Blowers - Temperature Switch High - TSH_63503 | C2NC-1800-ABL-TSH_63503 | C2NC-1800-ABL | Instruments | Temperature Switch High within the Aeration Blowers system - Temperature switch for aeration blower (B-63503) | Westinghouse | Manufacturer supplied thermocouple |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | TSH_63503 | [42 empty] | AA |  |  |  | Temperature Switch High |  | Digital
Aeration Blowers - Temperature Switch High - TSH_63504 | C2NC-1800-ABL-TSH_63504 | C2NC-1800-ABL | Instruments | Temperature Switch High within the Aeration Blowers system - Temperature switch for aeration blower (B-63504) | Westinghouse | Manufacturer supplied thermocouple |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | TSH_63504 | [42 empty] | AA |  |  |  | Temperature Switch High |  | Digital
Anoxic Tank - Process Analyzer - AIT_63100 | C2NC-1800-ANX-AIT_63100 | C2NC-1800-ANX | Instruments | Process Analyzer within the Anoxic Tank system - Redox sensor in anoxic tank (TK-63100) | Endress and Hauser | (CPF81E-AA5LAD1+Z1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 6 | AIT_63100 | [42 empty] | ML |  |  |  | Process Analyzer |  |  | Tank mounted
Anoxic Tank - Process Analyzer - AIT_63101 | C2NC-1800-ANX-AIT_63101 | C2NC-1800-ANX | Instruments | Process Analyzer within the Anoxic Tank system - pH and Temperature sensor in RAS Line | Endress and Hauser | (COS61D-AAA1A3+Z1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 14 | AIT_63101 | [42 empty] | RAS |  |  |  | Process Analyzer |  |  | Insertion 2" ANSI150 flange
Anoxic Tank - Level Switch High - LSH_63100 | C2NC-1800-ANX-LSH_63100 | C2NC-1800-ANX | Instruments | Level Switch High within the Anoxic Tank system - Level Switch for Anoxic tank (TK-63200) | Endress and Hauser | Liquipoint T FTW31 FTW31-A2A2BB4A |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 6 | LSH_63100 | [42 empty] | ML |  |  |  | Level Switch High |  | Digital | Insertion 1.5" MNPT
Anoxic Tank - Level Transmitter - LT_63100 | C2NC-1800-ANX-LT_63100 | C2NC-1800-ANX | Instruments | Level Transmitter within the Anoxic Tank system - Level Transmitter in Anoxic tank (TK-63200) | Endress and Hauser | Micropilot FMR50 (FMR50-AAACCDBMRGF+NFZ1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 6 | LT_63100 | [42 empty] | ML |  |  |  | Level Transmitter |  | Analog | Insertion 1/2" NPT
Aerobic Tank A - Process Analyzer - AIT_63200 | C2NC-1800-ARB_A-AIT_63200 | C2NC-1800-ARB_A | Instruments | Process Analyzer within the Aerobic Tank A system - Dissolved Oxygen Senor in aerobic tank (TK-63200) | Endress and Hauser | (COS61D-AAA1A3+Z1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 7 | AIT_63200 | [42 empty] | ML |  |  |  | Process Analyzer |  |  | Tank mounted
Aerobic Tank A - Process Analyzer - AIT_63201 | C2NC-1800-ARB_A-AIT_63201 | C2NC-1800-ARB_A | Instruments | Process Analyzer within the Aerobic Tank A system - pH and Temperature sensor in overline line to membrane tank (TK-65100) | Endress and Hauser |  |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 7 | AIT_63201 | [42 empty] | ML |  |  |  | Process Analyzer
Aerobic Tank A - Process Analyzer - AIT_63202 | C2NC-1800-ARB_A-AIT_63202 | C2NC-1800-ARB_A | Instruments | Process Analyzer within the Aerobic Tank A system - SS sensor in overline line to membrane tank (TK-65100) | Endress and Hauser | CUA451-B1D |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 7 | AIT_63202 | [42 empty] | ML |  |  |  | Process Analyzer |  |  | Insertion 2" ANSI150 flange
Aerobic Tank A - Process Analyzer - AIT_63203 | C2NC-1800-ARB_A-AIT_63203 | C2NC-1800-ARB_A | Instruments | Process Analyzer within the Aerobic Tank A system - Dissolved Oxygen Senor in aerobic tank (TK-63200) | Endress and Hauser | (COS61D-AAA1A3+Z1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 7 | AIT_63203 | [42 empty] | ML |  |  |  | Process Analyzer |  |  | Tank mounted
Aerobic Tank A - Flow Indicator Transmitter - FIT_63200 | C2NC-1800-ARB_A-FIT_63200 | C2NC-1800-ARB_A | Instruments | Flow Indicator Transmitter within the Aerobic Tank A system - FIT in air line to aerobic tank (TK-63200) | Endress and Hauser | T-mass I 300, 6I3BL2, 335mm 13" (6I3BL2-AAIBAEDFADSANA1AAGA2+PFZ1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 7 | FIT_63200 | [42 empty] | AA |  |  |  | Flow Meter w/ indicator |  | Analog | Insertion 3/4" w/ 1" NPT Male
Aerobic Tank A - Level Transmitter - LT_63200 | C2NC-1800-ARB_A-LT_63200 | C2NC-1800-ARB_A | Instruments | Level Transmitter within the Aerobic Tank A system - LT in aerobic tank (TK-63200) | Endress and Hauser | Micropilot FMR50 (FMR50-AAACCDBMRGF+NFZ1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 7 | LT_63200 | [42 empty] | ML |  |  |  | Level Transmitter |  | Analog | Insertion 1/2" NPT
Aerobic Tank A - Pressure Indicator - PI_63200 | C2NC-1800-ARB_A-PI_63200 | C2NC-1800-ARB_A | Instruments | Pressure Indicator within the Aerobic Tank A system - Pressure guage in air line to aerobic tank (TK-63200) | Reotemp | PT45P1A2P15-D-T-TS |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 7 | PI_63200 | [42 empty] | AA |  |  |  | Pressure Indicator |  |  | Insertion 1/2" NPT
Aerobic Tank B - Process Analyzer - AIT_63300 | C2NC-1800-ARB_B-AIT_63300 | C2NC-1800-ARB_B | Instruments | Process Analyzer within the Aerobic Tank B system - Dissolved Oxygen Senor in aerobic tank (TK-63300) | Endress and Hauser | (COS61D-AAA1A3+Z1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 8 | AIT_63300 | [42 empty] | ML |  |  |  | Process Analyzer |  |  | Tank mounted
Aerobic Tank B - Process Analyzer - AIT_63301 | C2NC-1800-ARB_B-AIT_63301 | C2NC-1800-ARB_B | Instruments | Process Analyzer within the Aerobic Tank B system - pH and Temperature sensor in overline line to membrane tank (TK-65101) | Endress and Hauser |  |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 8 | AIT_63301 | [42 empty] | ML |  |  |  | Process Analyzer
Aerobic Tank B - Process Analyzer - AIT_63302 | C2NC-1800-ARB_B-AIT_63302 | C2NC-1800-ARB_B | Instruments | Process Analyzer within the Aerobic Tank B system - SS sensor in overline line to membrane tank (TK-65101) | Endress and Hauser | CUA451-B1D |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 8 | AIT_63302 | [42 empty] | ML |  |  |  | Process Analyzer |  |  | Insertion 2" ANSI150 flange
Aerobic Tank B - Process Analyzer - AIT_63303 | C2NC-1800-ARB_B-AIT_63303 | C2NC-1800-ARB_B | Instruments | Process Analyzer within the Aerobic Tank B system - Dissolved Oxygen Senor in aerobic tank (TK-63300) | Endress and Hauser | (COS61D-AAA1A3+Z1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 8 | AIT_63303 | [42 empty] | ML |  |  |  | Process Analyzer |  |  | Tank mounted
Aerobic Tank B - Flow Indicator Transmitter - FIT_63300 | C2NC-1800-ARB_B-FIT_63300 | C2NC-1800-ARB_B | Instruments | Flow Indicator Transmitter within the Aerobic Tank B system - FIT in air line to aerobic tank (TK-63300) | Endress and Hauser | T-mass I 300, 6I3BL2, 335mm 13" (6I3BL2-AAIBAEDFADSANA1AAGA2+PFZ1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 8 | FIT_63300 | [42 empty] | AA |  |  |  | Flow Meter w/ indicator |  | Analog | Insertion 3/4" w/ 1" NPT Male
Aerobic Tank B - Level Transmitter - LT_63300 | C2NC-1800-ARB_B-LT_63300 | C2NC-1800-ARB_B | Instruments | Level Transmitter within the Aerobic Tank B system - LT in aerobic tank (TK-63300) | Endress and Hauser | Micropilot FMR50 (FMR50-AAACCDBMRGF+NFZ1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 8 | LT_63300 | [42 empty] | ML |  |  |  | Level Transmitter |  | Analog | Insertion 1/2" NPT
Aerobic Tank B - Pressure Indicator - PI_63300 | C2NC-1800-ARB_B-PI_63300 | C2NC-1800-ARB_B | Instruments | Pressure Indicator within the Aerobic Tank B system - Pressure guage in air line to aerobic tank (TK-63300) | Reotemp | PT45P1A2P15-D-T-TS |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 8 | PI_63300 | [42 empty] | AA |  |  |  | Pressure Indicator |  |  | Insertion 1/2" NPT
Caustic Dosing System - Level Indicator Transmitter - LIT_31100 | C2NC-1800-CHEM-CAUS-LIT_31100 | C2NC-1800-CHEM-CAUS | Instruments | Level Indicator Transmitter within the Caustic Dosing system - LIT in Sodium hydroxide tank (TK-31100) | [9 empty] | AN-1156 A01 01 | 19 | LIT_31100 | [42 empty] | CAU |  |  |  | Level Transmitter w/ indicator |  | Analog
Caustic Dosing System - Pressure Indicator - PI_31100 | C2NC-1800-CHEM-CAUS-PI_31100 | C2NC-1800-CHEM-CAUS | Instruments | Pressure Indicator within the Caustic Dosing system - Pressure guage for caustic pump (P-35100A) | Grifco | GG050P21T |  |  |  | Water America |  |  |  | AN-1156 A01 01 | 19 | PI_31100 | [42 empty] | CAU |  |  |  | Pressure Indicator
Caustic Dosing System - Pressure Indicator - PI_31101 | C2NC-1800-CHEM-CAUS-PI_31101 | C2NC-1800-CHEM-CAUS | Instruments | Pressure Indicator within the Caustic Dosing system - Pressure guage for caustic pump (P-35100B) | Grifco | GG050P21T |  |  |  | Water America |  |  |  | AN-1156 A01 01 | 19 | PI_31101 | [42 empty] | CAU |  |  |  | Pressure Indicator
Acid Dosing System - Pressure Indicator - PI_32100 | C2NC-1800-CHEM-CITR-PI_32100 | C2NC-1800-CHEM-CITR | Instruments | Pressure Indicator within the Acid Dosing system - Pressure guage in citric acid feed line | Grifco | GG050P21T |  |  |  | Water America |  |  |  | AN-1156 A01 01 | 19 | PI_32100 | [42 empty] | CIT |  |  |  | Pressure Indicator
Antifoam Dosing System - Pressure Indicator - PI_37100 | C2NC-1800-CHEM-FOAM-PI_37100 | C2NC-1800-CHEM-FOAM | Instruments | Pressure Indicator within the Antifoam Dosing system - Pressure guage for antifoam pump (P-37100A) | Grifco | GG050P21T |  |  |  | Water America |  |  |  | AN-1156 A01 01 | 19 | PI_37100 | [42 empty] | AFM |  |  |  | Pressure Indicator
Antifoam Dosing System - Pressure Indicator - PI_37101 | C2NC-1800-CHEM-FOAM-PI_37101 | C2NC-1800-CHEM-FOAM | Instruments | Pressure Indicator within the Antifoam Dosing system - Pressure guage for antifoam pump (P-37100B) | Grifco | GG050P21T |  |  |  | Water America |  |  |  | AN-1156 A01 01 | 19 | PI_37101 | [42 empty] | AFM |  |  |  | Pressure Indicator
Sodium Hypochlorite System - Pressure Indicator - PI_31200 | C2NC-1800-CHEM-HYPO-PI_31200 | C2NC-1800-CHEM-HYPO | Instruments | Pressure Indicator within the Sodium Hypochlorite system - Pressure guage in hypochloride feed line | Grifco | GG050P21T |  |  |  | Water America |  |  |  | AN-1156 A01 01 | 19 | PI_31200 | [42 empty] | HYP |  |  |  | Pressure Indicator
MBR - Differential Pressure Indicator - DPI_65101 | C2NC-1800-MBR-DPI_65101 | C2NC-1800-MBR | Instruments | Differential Pressure Indicator within the MBR system - Differential pressure gauge for membrane blower (B-65101) | Wika | 716.11 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | DPI_65101 | [42 empty] | AA |  |  |  | Differential Pressure Indicator
MBR - Differential Pressure Indicator - DPI_65102 | C2NC-1800-MBR-DPI_65102 | C2NC-1800-MBR | Instruments | Differential Pressure Indicator within the MBR system - Differential pressure gauge for membrane blower (B-65102) | Wika | 716.11 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | DPI_65102 | [42 empty] | AA |  |  |  | Differential Pressure Indicator
MBR - Flow Indicator Transmitter - FIT_65100 | C2NC-1800-MBR-FIT_65100 | C2NC-1800-MBR | Instruments | Flow Indicator Transmitter within the MBR system - FIT in overflow line to Membrane tank (TK-65100) | Endress and Hauser | Promag W10 5WBB2F-AAEAEBJA0DUA1KGAA1+ |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 7 | FIT_65100 | [42 empty] | ML |  |  |  | Flow Meter w/ indicator |  | Analog | In Line 10" ANSI 150#
MBR - Flow Indicator Transmitter - FIT_65101 | C2NC-1800-MBR-FIT_65101 | C2NC-1800-MBR | Instruments | Flow Indicator Transmitter within the MBR system - FIT in overflow line to Membrane tank (TK-65101) | Endress and Hauser | Promag W10 5WBB2F-AAEAEBJA0DUA1KGAA1+ |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 8 | FIT_65101 | [42 empty] | ML |  |  |  | Flow Meter w/ indicator |  | Analog | In Line 10" ANSI 150#
MBR - Flow Indicator Transmitter - FIT_65102 | C2NC-1800-MBR-FIT_65102 | C2NC-1800-MBR | Instruments | Flow Indicator Transmitter within the MBR system - FIT in air line to membrane tank (TK-65100) | Endress and Hauser | 6I3BL1-AAIBABBFADSANA2AAGA2+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | FIT_65102 | [42 empty] | AA |  |  |  | Flow Meter w/ indicator |  | Analog
MBR - Flow Indicator Transmitter - FIT_65103 | C2NC-1800-MBR-FIT_65103 | C2NC-1800-MBR | Instruments | Flow Indicator Transmitter within the MBR system - FIT in air line to membrane tank (TK-65101) | Endress and Hauser | 6I3BL1-AAIBABBFADSANA2AAGA2+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | FIT_65103 | [42 empty] | AA |  |  |  | Flow Meter w/ indicator |  | Analog
MBR - Level Indicator Transmitter - LIT_65100 | C2NC-1800-MBR-LIT_65100 | C2NC-1800-MBR | Instruments | Level Indicator Transmitter within the MBR system - LIT for membrane tank (TK-65100) | Endress and Hauser | FMB50-CD21JD1HGERGJB3U+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | LIT_65100 | [42 empty] | ML |  |  |  | Level Transmitter w/ indicator |  | Analog
MBR - Level Indicator Transmitter - LIT_65101 | C2NC-1800-MBR-LIT_65101 | C2NC-1800-MBR | Instruments | Level Indicator Transmitter within the MBR system - LIT for membrane tank (TK-65101) | Endress and Hauser | FMB50-CD21JD1HGERGJB3U+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | LIT_65101 | [42 empty] | ML |  |  |  | Level Transmitter w/ indicator |  | Analog
MBR - Level Switch High - LSH_65100 | C2NC-1800-MBR-LSH_65100 | C2NC-1800-MBR | Instruments | Level Switch High within the MBR system - Level high Switch for membrane tank (TK-65100) | Endress and Hauser | FTL31-CA4M2BAVAJ+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | LSH_65100 | [42 empty] | ML |  |  |  | Level Switch High |  | Digital
MBR - Level Switch High - LSH_65101 | C2NC-1800-MBR-LSH_65101 | C2NC-1800-MBR | Instruments | Level Switch High within the MBR system - Level high Switch for membrane tank (TK-65101) | Endress and Hauser | FTL31-CA4M2BAVAJ+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | LSH_65101 | [42 empty] | ML |  |  |  | Level Switch High |  | Digital
MBR - Level Switch Low - LSL_65100 | C2NC-1800-MBR-LSL_65100 | C2NC-1800-MBR | Instruments | Level Switch Low within the MBR system - Level low switch permeate to ejector (EJ-65100) | Endress and Hauser | FTW33-CA4MWVJ+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | LSL_65100 | [42 empty] | PER |  |  |  | Level Switch Low |  | Digital
MBR - Level Switch Low - LSL_65101 | C2NC-1800-MBR-LSL_65101 | C2NC-1800-MBR | Instruments | Level Switch Low within the MBR system - Level low switch permeate to ejector (EJ-65101) | Endress and Hauser | FTW33-CA4MWVJ+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | LSL_65101 | [42 empty] | PER |  |  |  | Level Switch Low |  | Digital
MBR - Level Switch Low - LSL_65102 | C2NC-1800-MBR-LSL_65102 | C2NC-1800-MBR | Instruments | Level Switch Low within the MBR system - Level low Switch for membrane tank (TK-65100) | Endress and Hauser | FTL31-CA4M2BAVAJ+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | LSL_65102 | [42 empty] | ML |  |  |  | Level Switch Low |  | Digital
MBR - Level Switch Low - LSL_65103 | C2NC-1800-MBR-LSL_65103 | C2NC-1800-MBR | Instruments | Level Switch Low within the MBR system - Level low Switch for membrane tank (TK-65101) | Endress and Hauser | FTL31-CA4M2BAVAJ+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | LSL_65103 | [42 empty] | ML |  |  |  | Level Switch Low |  | Digital
MBR - Pressure Indicator - PI_65100 | C2NC-1800-MBR-PI_65100 | C2NC-1800-MBR | Instruments | Pressure Indicator within the MBR system - Manometer on Ejector | Piab |  |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | PI_65100 | [42 empty] | Compressed Air |  |  |  | Pressure Indicator
MBR - Pressure Indicator - PI_65101 | C2NC-1800-MBR-PI_65101 | C2NC-1800-MBR | Instruments | Pressure Indicator within the MBR system - Manometer on Ejector | Piab |  |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | PI_65101 | [42 empty] | Compressed Air |  |  |  | Pressure Indicator
MBR - Pressure Indicator Transmitter - PIT_65100 | C2NC-1800-MBR-PIT_65100 | C2NC-1800-MBR | Instruments | Pressure Indicator Transmitter within the MBR system - PIT on permeate line from membrane tank (TK-65100) | Endress and Hauser | PMC51-CD21JD1MGJRKJA+F1N2Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | PIT_65100 | [42 empty] | PER |  |  |  | Pressure Transmitter w/ indicator |  | Analog
MBR - Pressure Indicator Transmitter - PIT_65101 | C2NC-1800-MBR-PIT_65101 | C2NC-1800-MBR | Instruments | Pressure Indicator Transmitter within the MBR system - PIT on permeate line from membrane tank (TK-65101) | Endress and Hauser | PMC51-CD21JD1MGJRKJA+F1N2Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 10 | PIT_65101 | [42 empty] | PER |  |  |  | Pressure Transmitter w/ indicator |  | Analog
MBR - Pressure Switch High - PSH_65100 | C2NC-1800-MBR-PSH_65100 | C2NC-1800-MBR | Instruments | Pressure Switch High within the MBR system - Perssure switch in permeate to ejector | [9 empty] | AN-1156 A01 01 | 10 | PSH_65100 | [42 empty] | PER |  |  |  | Pressure Switch High |  | Digital
MBR - Pressure Switch High - PSH_65101 | C2NC-1800-MBR-PSH_65101 | C2NC-1800-MBR | Instruments | Pressure Switch High within the MBR system - Pressure switch for membrane blower (B-65101) | Ashcroft | B424BXC815# |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | PSH_65101 | [42 empty] | AA |  |  |  | Pressure Switch High |  | Digital
MBR - Pressure Switch High - PSH_65102 | C2NC-1800-MBR-PSH_65102 | C2NC-1800-MBR | Instruments | Pressure Switch High within the MBR system - Pressure switch for membrane blower (B-65102) | Ashcroft | B424BXC815# |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | PSH_65102 | [42 empty] | AA |  |  |  | Pressure Switch High |  | Digital
MBR - Temperature Indicator - TI_65101 | C2NC-1800-MBR-TI_65101 | C2NC-1800-MBR | Instruments | Temperature Indicator within the MBR system - Temperature indicator in air line from membrane blower (B-65101) | Winter |  |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | TI_65101 | [42 empty] | AA |  |  |  | Temperature Indicator
MBR - Temperature Indicator - TI_65102 | C2NC-1800-MBR-TI_65102 | C2NC-1800-MBR | Instruments | Temperature Indicator within the MBR system - Temperature indicator in air line from membrane blower (B-65102) | Winter |  |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | TI_65102 | [42 empty] | AA |  |  |  | Temperature Indicator
MBR - Temperature Switch - TS_65101 | C2NC-1800-MBR-TS_65101 | C2NC-1800-MBR | Instruments | Temperature Switch within the MBR system - Temperature switch for membrane blower (B-65101) | Ashcroft | T420T05030XNH 150-260F |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | TS_65101 | [42 empty] | AA |  |  |  | Temperature Switch |  | Digital
MBR - Temperature Switch - TS_65102 | C2NC-1800-MBR-TS_65102 | C2NC-1800-MBR | Instruments | Temperature Switch within the MBR system - Temperature switch for membrane blower (B-65102) | Ashcroft | T420T05030XNH 150-260F |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | TS_65102 | [42 empty] | AA |  |  |  | Temperature Switch |  | Digital
MBR - Temperature Switch High - TSH_65101 | C2NC-1800-MBR-TSH_65101 | C2NC-1800-MBR | Instruments | Temperature Switch High within the MBR system - Temperature switch for membrane blower (B-65101) | Westinghouse | Manufacturer supplied thermocouple |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | TSH_65101 | [42 empty] | AA |  |  |  | Temperature Switch High |  | Digital
MBR - Temperature Switch High - TSH_65102 | C2NC-1800-MBR-TSH_65102 | C2NC-1800-MBR | Instruments | Temperature Switch High within the MBR system - Temperature switch for membrane blower (B-65102) | Westinghouse | Manufacturer supplied thermocouple |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 12 | TSH_65102 | [42 empty] | AA |  |  |  | Temperature Switch High |  | Digital
Permeate System - Process Analyzer - AIT_65300 | C2NC-1800-PRM-AIT_65300 | C2NC-1800-PRM | Instruments | Process Analyzer within the Permeate system - SS Sensor for permeate line | Hach | LXV445.99.23112 and LXV525.99AA1551 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 13 | AIT_65300 | [42 empty] | PER |  |  |  | Process Analyzer
Permeate System - Flow Indicator Transmitter - FIT_65301 | C2NC-1800-PRM-FIT_65301 | C2NC-1800-PRM | Instruments | Flow Indicator Transmitter within the Permeate system - FIT in permeate line to permeate tank (TK-65300) | Endress and Hauser | 5W4C1F-C6HLHA0DQA140A+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 13 | FIT_65301 | [42 empty] | PER |  |  |  | Flow Meter w/ indicator |  | Analog
Permeate System - Flow Indicator Transmitter - FIT_65302 | C2NC-1800-PRM-FIT_65302 | C2NC-1800-PRM | Instruments | Flow Indicator Transmitter within the Permeate system - FIT in permeate line to permeate tank (TK-65300) | Endress and Hauser | 5W4C1F-C6HLHA0DQA140A+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 13 | FIT_65302 | [42 empty] | PER |  |  |  | Flow Meter w/ indicator |  | Analog
Permeate System - Level Indicator Transmitter - LIT_65300 | C2NC-1800-PRM-LIT_65300 | C2NC-1800-PRM | Instruments | Level Indicator Transmitter within the Permeate system - LIT in permeate tank (TK-65300) | Endress and Hauser | (PMP71B-AABADJH6BD3HEAAAAJG2+Z1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 13 | LIT_65300 | [42 empty] | PER |  |  |  | Level Transmitter w/ indicator |  | Analog | Insertion 1/2" NPT
Permeate System - Level Switch Low - LSL_65300 | C2NC-1800-PRM-LSL_65300 | C2NC-1800-PRM | Instruments | Level Switch Low within the Permeate system - Level switch in permeate tank (TK-65300) | Endress and Hauser | FTI51-A5H1ACJ23D1A |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 13 | LSL_65300 | [42 empty] | PER |  |  |  | Level Switch Low |  | Digital | Insertion NPS 1" Cl.150 RF
Permeate System - Pressure Indicating Switch - PIS_65301 | C2NC-1800-PRM-PIS_65301 | C2NC-1800-PRM | Instruments | Pressure Indicating Switch within the Permeate system - Pressure switch for permeate feed pump (P-65301) | Wika | PI-004-REA01-MFRKG/US/ /P |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 13 | PIS_65301 | [42 empty] | PER |  |  |  | Pressure Indicating Switch |  | Digital
Permeate System - Pressure Indicating Switch - PIS_65302 | C2NC-1800-PRM-PIS_65302 | C2NC-1800-PRM | Instruments | Pressure Indicating Switch within the Permeate system - Pressure switch for permeate feed pump (P-65302) | Wika | PI-004-REA01-MFRKG/US/ /P |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 13 | PIS_65302 | [42 empty] | PER |  |  |  | Pressure Indicating Switch |  | Digital
Permeate System - Pressure Indicating Switch - PIS_65303 | C2NC-1800-PRM-PIS_65303 | C2NC-1800-PRM | Instruments | Pressure Indicating Switch within the Permeate system - Pressure switch for permeate feed pump (P-65301) | Wika | PI-004-REA01-MFRKG/US/ /P |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 13 | PIS_65303 | [42 empty] | PER |  |  |  | Pressure Indicating Switch |  | Digital
Permeate System - Pressure Indicating Switch - PIS_65304 | C2NC-1800-PRM-PIS_65304 | C2NC-1800-PRM | Instruments | Pressure Indicating Switch within the Permeate system - Pressure switch for permeate feed pump (P-65302) | Wika | PI-004-REA01-MFRKG/US/ /P |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 13 | PIS_65304 | [42 empty] | PER |  |  |  | Pressure Indicating Switch |  | Digital
Permeate System - Temperature Transmitter w/ Indicator - TIT_65301 | C2NC-1800-PRM-TIT_65301 | C2NC-1800-PRM | Instruments | Temperature Transmitter w/ Indicator within the Permeate system - TIT in permeate feed pump line (P-65301) | Endress and Hauser | TM131-CABBBAB1BA3AGAC3AE2BA1+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 13 | TIT_65301 | [42 empty] | PER |  |  |  | Temperature Transmitter w/ Indicator |  | Analog
Permeate System - Temperature Transmitter w/ Indicator - TIT_65302 | C2NC-1800-PRM-TIT_65302 | C2NC-1800-PRM | Instruments | Temperature Transmitter w/ Indicator within the Permeate system - TIT in permeate feed pump line (P-65302) | Endress and Hauser | TM131-CABBBAB1BA3AGAC3AE2BA1+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 13 | TIT_65302 | [42 empty] | PER |  |  |  | Temperature Transmitter w/ Indicator |  | Analog
WAS and RAS Systems - Flow Indicator Transmitter - FIT_65203 | C2NC-1800-RAS-FIT_65203 | C2NC-1800-RAS | Instruments | Flow Indicator Transmitter within the WAS and RAS Systems system - FIT in RAS line from RAS pumps (P-65203,P-65204) | Endress and Hauser | 5W4C3H-C6HLHA0DQA140A+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 14 | FIT_65203 | [42 empty] | RAS |  |  |  | Flow Meter w/ indicator |  | Analog
WAS and RAS Systems - Flow Indicator Transmitter - FIT_65206 | C2NC-1800-RAS-FIT_65206 | C2NC-1800-RAS | Instruments | Flow Indicator Transmitter within the WAS and RAS Systems system - FIT in line feeding dewatering press (TK-510401) | Endress and Hauser | 5W4C1H-C6HLHA0DQA140A+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 15 | FIT_65206 | [42 empty] | WAS |  |  |  | Flow Meter w/ indicator |  | Analog
WAS and RAS Systems - Level Indicator Transmitter - LIT_65200 | C2NC-1800-RAS-LIT_65200 | C2NC-1800-RAS | Instruments | Level Indicator Transmitter within the WAS and RAS Systems system - LIT in RAS tank A (TK-65200) | Endress and Hauser | FMB50-CD21JD1HGERGJB3U+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 11 | LIT_65200 | [42 empty] | RAS/WAS |  |  |  | Level Transmitter w/ indicator |  | Analog
WAS and RAS Systems - Level Indicator Transmitter - LIT_65201 | C2NC-1800-RAS-LIT_65201 | C2NC-1800-RAS | Instruments | Level Indicator Transmitter within the WAS and RAS Systems system - LIT in RAS tank B (TK-65201) | Endress and Hauser | FMB50-CD21JD1HGERGJB3U+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 11 | LIT_65201 | [42 empty] | RAS/WAS |  |  |  | Level Transmitter w/ indicator |  | Analog
WAS and RAS Systems - Level Switch Low - LSL_65200 | C2NC-1800-RAS-LSL_65200 | C2NC-1800-RAS | Instruments | Level Switch Low within the WAS and RAS Systems system - Level switch in RAS tank A (TK-65200) | Endress and Hauser | FTL31-CA4M2BAVAJ+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 11 | LSL_65200 | [42 empty] | RAS/WAS |  |  |  | Level Switch Low |  | Digital
WAS and RAS Systems - Level Switch Low - LSL_65201 | C2NC-1800-RAS-LSL_65201 | C2NC-1800-RAS | Instruments | Level Switch Low within the WAS and RAS Systems system - Level switch in RAS tank B (TK-65201) | Endress and Hauser | FTL31-CA4M2BAVAJ+Z1 |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 11 | LSL_65201 | [42 empty] | RAS/WAS |  |  |  | Level Switch Low |  | Digital
WAS and RAS Systems - Pressure Indicator - PI_65203 | C2NC-1800-RAS-PI_65203 | C2NC-1800-RAS | Instruments | Pressure Indicator within the WAS and RAS Systems system - Pressure guage for RAS pump (P-65203) | Winter |  |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 14 | PI_65203 | [42 empty] | RAS |  |  |  | Pressure Indicator
WAS and RAS Systems - Pressure Indicator - PI_65204 | C2NC-1800-RAS-PI_65204 | C2NC-1800-RAS | Instruments | Pressure Indicator within the WAS and RAS Systems system - Pressure guage for RAS pump (P-65204) | Winter |  |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 14 | PI_65204 | [42 empty] | RAS |  |  |  | Pressure Indicator
WAS and RAS Systems - Pressure Indicator - PI_65206 | C2NC-1800-RAS-PI_65206 | C2NC-1800-RAS | Instruments | Pressure Indicator within the WAS and RAS Systems system - Pressure guage for WAS pump (P-65206) | Winter |  |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 15 | PI_65206 | [42 empty] | WAS |  |  |  | Pressure Indicator
WAS and RAS Systems - Pressure Indicator - PI_65207 | C2NC-1800-RAS-PI_65207 | C2NC-1800-RAS | Instruments | Pressure Indicator within the WAS and RAS Systems system - Pressure guage for WAS pump (P-65207) | Winter |  |  |  |  | AIS |  |  |  | AN-1156 A01 01 | 15 | PI_65207 | [42 empty] | WAS |  |  |  | Pressure Indicator
WAS and RAS Systems - Pressure Indicator Transmitter - PIT_65200 | C2NC-1800-RAS-PIT_65200 | C2NC-1800-RAS | Instruments | Pressure Indicator Transmitter within the WAS and RAS Systems system - PIT on WAS to WAS Dewatering press | Endress and Hauser | (PMC51B-AABADBH63KFA1VXJR+Z1) |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 15 | PIT_65200 | [42 empty] | WAS |  |  |  | Pressure Transmitter w/ indicator |  | Analog | Insertion 1/4" FNPT w/ 1/2" MNPT
WAS and RAS Systems - Pressure Switch High - PSH_65201 | C2NC-1800-RAS-PSH_65201 | C2NC-1800-RAS | Instruments | Pressure Switch High within the WAS and RAS Systems system - Pressure switch for WAS Pump (P-65206) | Ashcroft | B424BXC815# |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 15 | PSH_65201 | [42 empty] | WAS |  |  |  | Pressure Switch High |  | Digital | Insertion 1/4" FNPT w/ 1/2" MNPT
WAS and RAS Systems - Pressure Switch High - PSH_65202 | C2NC-1800-RAS-PSH_65202 | C2NC-1800-RAS | Instruments | Pressure Switch High within the WAS and RAS Systems system - Pressure switch for WAS Pump (P-65207) | Ashcroft | B424BXC815# |  |  |  | Anaergia |  |  |  | AN-1156 A01 01 | 15 | PSH_65202 | [42 empty] | WAS |  |  |  | Pressure Switch High |  | Digital | Insertion 1/4" FNPT w/ 1/2" MNPT
WAS and RAS Systems - Temperature Switch High - TSH_65206 | C2NC-1800-RAS-TSH_65206 | C2NC-1800-RAS | Instruments | Temperature Switch High within the WAS and RAS Systems system - Temperature switch for WAS pump (P-65206) | [9 empty] | AN-1156 A01 01 | 15 | TSH_65206 | [42 empty] | WAS |  |  |  | Temperature Switch High |  | Digital
WAS and RAS Systems - Temperature Switch High - TSH_65207 | C2NC-1800-RAS-TSH_65207 | C2NC-1800-RAS | Instruments | Temperature Switch High within the WAS and RAS Systems system - Temperature switch for WAS pump (P-65207) | [9 empty] | AN-1156 A01 01 | 15 | TSH_65207 | [42 empty] | WAS |  |  |  | Temperature Switch High |  | Digital
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_01 | C2NC-1800-ABL-12 _ AA _ 63501 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63501 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | Aeration Blower A | Aeration Blowers Header | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_02 | C2NC-1800-ABL-12 _ AA _ 63502 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63502 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | Aeration Blower C | Aeration Blowers Header | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_03 | C2NC-1800-ABL-12 _ AA _ 63503 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63503 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | Aeration Blower B | Aeration Blowers Header | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_06 | C2NC-1800-ABL-12 _ AA _ 63506 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63506 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | Aeration Blower D | Aeration Blowers Header | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_07 | C2NC-1800-ABL-12 _ AA _ 63507 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63507 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | Aeration Blower E | Aeration Blowers Header | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_08 | C2NC-1800-ABL-12 _ AA _ 63508 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63508 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | Aeration Blowers Header | After Cooler 1 | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_09 | C2NC-1800-ABL-12 _ AA _ 63509 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63509 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | After Cooler 1 | Aerobic Tank A | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_10 | C2NC-1800-ABL-12 _ AA _ 63510 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63510 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | Aeration Blowers Header | After Cooler 2 | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_11 | C2NC-1800-ABL-12 _ AA _ 63511 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63511 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | After Cooler 2 | Aerobic Tank A | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_12 | C2NC-1800-ABL-12 _ AA _ 63512 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63512 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | Aeration Blowers Header | After Cooler 3 | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_13 | C2NC-1800-ABL-12 _ AA _ 63513 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63513 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | After Cooler 3 | Aerobic Tank B | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_14 | C2NC-1800-ABL-12 _ AA _ 63514 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63514 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | Aeration Blowers Header | After Cooler 4 | N | 25 |  | 150 #
12 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_15 | C2NC-1800-ABL-12 _ AA _ 63515 _ SSA1 | C2NC-1800-ABL | Lines | 12 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 12 _ AA _ 63515 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 12 | After Cooler 4 | Areobic Tank B | N | 25 |  | 150 #
16 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_04 | C2NC-1800-ABL-16 _ AA _ 63504 _ SSA1 | C2NC-1800-ABL | Lines | 16 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 16 _ AA _ 63504 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 16 | Aeration Blowers | Aerobic Tank A | N | 25 |  | 150 #
16 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_05 | C2NC-1800-ABL-16 _ AA _ 63505 _ SSA1 | C2NC-1800-ABL | Lines | 16 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 16 _ AA _ 63505 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 16 | Aeration Blowers | Aerobic Tank B | N | 25 |  | 150 #
16 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_16 | C2NC-1800-ABL-16 _ AA _ 63516 _ SSA1 | C2NC-1800-ABL | Lines | 16 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 16 _ AA _ 63516 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 16 | Aeration Blowers Header | Aeration Blowers Header | N | 25 |  | 150 #
16 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_17 | C2NC-1800-ABL-16 _ AA _ 63517 _ SSA1 | C2NC-1800-ABL | Lines | 16 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 9 | 16 _ AA _ 63517 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 16 | Aeration Blowers Header | Aeration Blowers Header | N | 25 |  | 150 #
16 Inch Stainless Steel Aeration Blowers Areation Air in SBR system Line 635_18 | C2NC-1800-ABL-16 _ AA _ 63518 _ SSA1 | C2NC-1800-ABL | Lines | 16 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 7 | 16 _ AA _ 63518 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 16 | Aeration Blowers | Aerobic Tank A | N | 100 |  | 150 #
10 Inch PVC Aerobic Tank A Mixed Liquor Line 632_01 | C2NC-1800-ARB_A-10 _ ML _ 63201 _ PVC | C2NC-1800-ARB_A | Lines | 10 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 7 | 10 _ ML _ 63201 _ PVC | [10 empty] | Mixed Liquor | PVC | 10 | Aerobic Tank A | Aerobic Tank A Exit Header | N | 100 |  | 150 #
10 Inch PVC Aerobic Tank A Mixed Liquor Line 632_02 | C2NC-1800-ARB_A-10 _ ML _ 63202 _ PVC | C2NC-1800-ARB_A | Lines | 10 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 7 | 10 _ ML _ 63202 _ PVC | [10 empty] | Mixed Liquor | PVC | 10 | Aerobic Tank A | Membrane Tanks | N | 100 |  | 150 #
10 Inch PVC Aerobic Tank A Mixed Liquor Line 632_03 | C2NC-1800-ARB_A-10 _ ML _ 63203 _ PVC | C2NC-1800-ARB_A | Lines | 10 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 10 | 10 _ ML _ 63203 _ PVC | [10 empty] | Mixed Liquor | PVC | 10 | Aerobic Tanks | Membrane Tank A | N | 100 |  | 150 #
10 Inch PVC Aerobic Tank A Mixed Liquor Line 632_05 | C2NC-1800-ARB_A-10 _ ML _ 63205 _ PVC | C2NC-1800-ARB_A | Lines | 10 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 7 | 10 _ ML _ 63205 _ PVC | [10 empty] | Mixed Liquor | PVC | 10 | Aerobic Tank A | Aerobic Tank B | N | 100 |  | 150 #
6 Inch Carbon Steel Aerobic Tank A Mixed Liquor Line 632_04 | C2NC-1800-ARB_A-6 _ ML _ 63204 _ CSA | C2NC-1800-ARB_A | Lines | 6 Inch Carbon Steel Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 7 | 6 _ ML _ 63204 _ CSA | [10 empty] | Mixed Liquor | Carbon Steel | 6 | Aerobic Tank A | Drain/Outlet | N | 100 |  | 150 #
10 Inch PVC Aerobic Tank B Mixed Liquor Line 633_01 | C2NC-1800-ARB_B-10 _ ML _ 63301 _ PVC | C2NC-1800-ARB_B | Lines | 10 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 8 | 10 _ ML _ 63301 _ PVC | [10 empty] | Mixed Liquor | PVC | 10 | Aerobic Tank B | Aerobic Tank B Exit Header | N | 100 |  | 150 #
10 Inch PVC Aerobic Tank B Mixed Liquor Line 633_02 | C2NC-1800-ARB_B-10 _ ML _ 63302 _ PVC | C2NC-1800-ARB_B | Lines | 10 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 8 | 10 _ ML _ 63302 _ PVC | [10 empty] | Mixed Liquor | PVC | 10 | Aerobic Tank B | Membrane Tanks | N | 100 |  | 150 #
10 Inch PVC Aerobic Tank B Mixed Liquor Line 633_03 | C2NC-1800-ARB_B-10 _ ML _ 63303 _ PVC | C2NC-1800-ARB_B | Lines | 10 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 10 | 10 _ ML _ 63303 _ PVC | [10 empty] | Mixed Liquor | PVC | 10 | Aerobic Tanks | Membrane Tank B | N | 100 |  | 150 #
6 Inch Carbon Steel Aerobic Tank B Mixed Liquor Line 633_04 | C2NC-1800-ARB_B-6 _ ML _ 63304 _ CSA | C2NC-1800-ARB_B | Lines | 6 Inch Carbon Steel Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 8 | 6 _ ML _ 63304 _ CSA | [10 empty] | Mixed Liquor | Carbon Steel | 6 | Aerobic Tank B | Drain/Outlet | N | 100 |  | 150 #
0.5 Inch PVC Caustic Dosing System Caustic Line 311_01 | C2NC-1800-CHEM-CAUS-0.5 _ CAU _ 31101 _ PVC2 | C2NC-1800-CHEM-CAUS | Lines | 0.5 Inch PVC Caustic Line | [9 empty] | AN-1156 A01 01 | 19 | 0.5 _ CAU _ 31101 _ PVC2 | [10 empty] | Caustic | PVC | 0.5 | Sodium Hydroxide Tank | Sodium Hydroxide Pumps | N | 100 |  | 150 #
0.5 Inch PVC Caustic Dosing System Caustic Line 311_02 | C2NC-1800-CHEM-CAUS-0.5 _ CAU _ 31102 _ PVC2 | C2NC-1800-CHEM-CAUS | Lines | 0.5 Inch PVC Caustic Line | [9 empty] | AN-1156 A01 01 | 19 | 0.5 _ CAU _ 31102 _ PVC2 | [10 empty] | Caustic | PVC | 0.5 | Sodium Hydroxide Pumps | Sodium Hydroxide Header | N | 100 |  | 150 #
0.75 Inch PVC Caustic Dosing System Caustic Line 311_03 | C2NC-1800-CHEM-CAUS-0.75 _ CAU _ 31103 _ PVC2 | C2NC-1800-CHEM-CAUS | Lines | 0.75 Inch PVC Caustic Line | [9 empty] | AN-1156 A01 01 | 19 | 0.75 _ CAU _ 31103 _ PVC2 | [10 empty] | Caustic | PVC | 0.75 | Sodium Hydroxide Pump A | Sodium Hydroxide Header | N | 100 |  | 150 #
0.75 Inch PVC Caustic Dosing System Caustic Line 311_04 | C2NC-1800-CHEM-CAUS-0.75 _ CAU _ 31104 _ PVC2 | C2NC-1800-CHEM-CAUS | Lines | 0.75 Inch PVC Caustic Line | [9 empty] | AN-1156 A01 01 | 19 | 0.75 _ CAU _ 31104 _ PVC2 | [10 empty] | Caustic | PVC | 0.75 | Sodium Hydroxide Pump B | Sodium Hydroxide Header | N | 100 |  | 150 #
1 Inch PVC Acid Dosing System Citric Acid Line 321_01 | C2NC-1800-CHEM-CITR-1 _ CIT _ 32101 _ PVC | C2NC-1800-CHEM-CITR | Lines | 1 Inch PVC Citric Acid Line | [9 empty] | AN-1156 A01 01 | 19 | 1 _ CIT _ 32101 _ PVC | [10 empty] | Citric Acid | PVC | 1 | Citric Acid Tote | Citric Acid Pump | N | 50 |  | 150 #
1 Inch PVC Acid Dosing System Citric Acid Line 321_02 | C2NC-1800-CHEM-CITR-1 _ CIT _ 32102 _ PVC | C2NC-1800-CHEM-CITR | Lines | 1 Inch PVC Citric Acid Line | [9 empty] | AN-1156 A01 01 | 19 | 1 _ CIT _ 32102 _ PVC | [10 empty] | Citric Acid | PVC | 1 | Citric Acid Pump | Membrane Permeate Lines | N | 50 |  | 150 #
0.5 Inch PVC Antifoam Dosing System Antifoam Line 371_01 | C2NC-1800-CHEM-FOAM-0.5 _ AFM _ 37101 _ PVC | C2NC-1800-CHEM-FOAM | Lines | 0.5 Inch PVC Antifoam Line | [9 empty] | AN-1156 A01 01 | 19 | 0.5 _ AFM _ 37101 _ PVC | [10 empty] | Antifoam | PVC | 0.5 | Antifoam Tote | Antifoam Pumps | N | 50 |  | 150 #
0.5 Inch PVC Antifoam Dosing System Antifoam Line 371_02 | C2NC-1800-CHEM-FOAM-0.5 _ AFM _ 37102 _ PVC | C2NC-1800-CHEM-FOAM | Lines | 0.5 Inch PVC Antifoam Line | [9 empty] | AN-1156 A01 01 | 19 | 0.5 _ AFM _ 37102 _ PVC | [10 empty] | Antifoam | PVC | 0.5 | Antifoam Pumps | Antifoam Header | N | 50 |  | 150 #
0.5 Inch PVC Antifoam Dosing System Antifoam Line 371_03 | C2NC-1800-CHEM-FOAM-0.5 _ AFM _ 37103 _ PVC | C2NC-1800-CHEM-FOAM | Lines | 0.5 Inch PVC Antifoam Line | [9 empty] | AN-1156 A01 01 | 19 | 0.5 _ AFM _ 37103 _ PVC | [10 empty] | Antifoam | PVC | 0.5 | Antifoam Header | Aerobic Tank A | N | 50 |  | 150 #
0.5 Inch PVC Antifoam Dosing System Antifoam Line 371_04 | C2NC-1800-CHEM-FOAM-0.5 _ AFM _ 37104 _ PVC | C2NC-1800-CHEM-FOAM | Lines | 0.5 Inch PVC Antifoam Line | [9 empty] | AN-1156 A01 01 | 19 | 0.5 _ AFM _ 37104 _ PVC | [10 empty] | Antifoam | PVC | 0.5 | Antifoam Header | Aerobic Tank B | N | 50 |  | 150 #
0.5 Inch PVC Antifoam Dosing System Antifoam Line 371_05 | C2NC-1800-CHEM-FOAM-0.5 _ AFM _ 37105 _ PVC | C2NC-1800-CHEM-FOAM | Lines | 0.5 Inch PVC Antifoam Line | [9 empty] | AN-1156 A01 01 | 19 | 0.5 _ AFM _ 37105 _ PVC | [10 empty] | Antifoam | PVC | 0.5 | Antifoam Header | Membrane Tanks | N | 50 |  | 150 #
0.5 Inch PVC Antifoam Dosing System Antifoam Line 371_06 | C2NC-1800-CHEM-FOAM-0.5 _ AFM _ 37106 _ PVC | C2NC-1800-CHEM-FOAM | Lines | 0.5 Inch PVC Antifoam Line | [9 empty] | AN-1156 A01 01 | 19 | 0.5 _ AFM _ 37106 _ PVC | [10 empty] | Antifoam | PVC | 0.5 | Antifoam Header | RAS Tanks | N | 50 |  | 150 #
0.75 Inch PVC Antifoam Dosing System Antifoam Line 371_08 | C2NC-1800-CHEM-FOAM-0.75 _ AFM _ 37108 _ PVC | C2NC-1800-CHEM-FOAM | Lines | 0.75 Inch PVC Antifoam Line | [9 empty] | AN-1156 A01 01 | 19 | 0.75 _ AFM _ 37108 _ PVC | [10 empty] | Antifoam | PVC | 0.75 | Antifoam Pump A | Antifoam Header | N | 50 |  | 150 #
0.75 Inch PVC Antifoam Dosing System Antifoam Line 371_10 | C2NC-1800-CHEM-FOAM-0.75 _ AFM _ 37110 _ PVC | C2NC-1800-CHEM-FOAM | Lines | 0.75 Inch PVC Antifoam Line | [9 empty] | AN-1156 A01 01 | 19 | 0.75 _ AFM _ 37110 _ PVC | [10 empty] | Antifoam | PVC | 0.75 | Antifoam Pump B | Antifoam Header | N | 50 |  | 150 #
0.5 Inch PVC Sodium Hypochlorite System Sodium Hypoclorite Line 312_01 | C2NC-1800-CHEM-HYPO-0.5 _ HYP _ 31201 _ PVC | C2NC-1800-CHEM-HYPO | Lines | 0.5 Inch PVC Sodium Hypoclorite Line | [9 empty] | AN-1156 A01 01 | 19 | 0.5 _ HYP _ 31201 _ PVC | [10 empty] | Sodium Hypoclorite | PVC | 0.5 | Sodium Hypochlorite Tote | Sodium Hypochlorite Pump | N | 50 |  | 150 #
0.5 Inch PVC Sodium Hypochlorite System Sodium Hypoclorite Line 312_02 | C2NC-1800-CHEM-HYPO-0.5 _ HYP _ 31202 _ PVC | C2NC-1800-CHEM-HYPO | Lines | 0.5 Inch PVC Sodium Hypoclorite Line | [9 empty] | AN-1156 A01 01 | 19 | 0.5 _ HYP _ 31202 _ PVC | [10 empty] | Sodium Hypoclorite | PVC | 0.5 | Sodium Hypochlorite Pump | Membrane Permeate Lines | N | 50 |  | 150 #
0.75 Inch PVC Emulsion Polymer WAS Polymer Line 352_04 | C2NC-1800-FLOC-0.75 _ POL _ 35204 _ PVC | C2NC-1800-FLOC | Lines | 0.75 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 17 | 0.75 _ POL _ 35204 _ PVC | [10 empty] | Polymer | PVC | 0.75 | WAS Liquid Polymer Pump | WAS Dewatering Polymer Aging Tank | N | 100 |  | 150 #
0.75 Inch PVC Emulsion Polymer WAS Potable Water Line 352_03 | C2NC-1800-FLOC-0.75 _ PW _ 35203 _ PVC | C2NC-1800-FLOC | Lines | 0.75 Inch PVC Potable Water Line | [9 empty] | AN-1156 A01 01 | 17 | 0.75 _ PW _ 35203 _ PVC | [10 empty] | Potable Water | PVC | 0.75 | Potable Water Inlet | WAS Dewatering Polymer Aging Tank | N | 100 |  | 150 #
1 Inch PVC Emulsion Polymer WAS Polymer Line 352_01 | C2NC-1800-FLOC-1 _ POL _ 35201 _ PVC | C2NC-1800-FLOC | Lines | 1 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 17 | 1 _ POL _ 35201 _ PVC | [10 empty] | Polymer | PVC | 1 | WAS Dewatering Emulsion Polymer Storage Tote | WAS Liquid Polymer Pump | N | 100 |  | 150 #
1.5 Inch PVC Emulsion Polymer WAS Polymer Line 352_02 | C2NC-1800-FLOC-1.5 _ POL _ 35202 _ PVC | C2NC-1800-FLOC | Lines | 1.5 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 17 | 1.5 _ POL _ 35202 _ PVC | [10 empty] | Polymer | PVC | 1.5 | WAS Polymer Dilution Pump | WAS Dewatering Press | N | 100 |  | 150 #
1.5 Inch PVC Emulsion Polymer WAS Polymer Line 352_05 | C2NC-1800-FLOC-15 _ POL _ 35205 _ PVC | C2NC-1800-FLOC | Lines | 1.5 Inch PVC Polymer Line | [9 empty] | AN-1156 A01 01 | 17 | 1.5 _ POL _ 35205 _ PVC | [10 empty] | Polymer | PVC | 1.5 | WAS Dewatering Polymer Aging Tank | WAS Polymer Dilution Pump | N | 100 |  | 150 #
0.5 Inch PVC MBR Permeate Line 651_06 | C2NC-1800-MBR-0.5 _ PER _ 65106 _ PVC | C2NC-1800-MBR | Lines | 0.5 Inch PVC Permeate Line | [9 empty] | AN-1156 A01 01 | 10 | 0.5 _ PER _ 65106 _ PVC | [10 empty] | Permeate | PVC | 0.5 | Ejector 1 | RAS Tank B | N | 100 |  | 150 #
0.5 Inch PVC MBR Permeate Line 651_07 | C2NC-1800-MBR-0.5 _ PER _ 65107 _ PVC | C2NC-1800-MBR | Lines | 0.5 Inch PVC Permeate Line | [9 empty] | AN-1156 A01 01 | 10 | 0.5 _ PER _ 65107 _ PVC | [10 empty] | Permeate | PVC | 0.5 | Ejector 2 | RAS Tank B | N | 100 |  | 150 #
12 Inch PVC MBR Mixed Liquor Line 651_10 | C2NC-1800-MBR-12 _ ML _ 65110 _ PVC | C2NC-1800-MBR | Lines | 12 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 10 | 12 _ ML _ 65110 _ PVC | [10 empty] | Mixed Liquor | PVC | 12 | Membrane Tank A | MBR Recirculation Pump A | N | 100 |  | 150 #
12 Inch PVC MBR Mixed Liquor Line 651_13 | C2NC-1800-MBR-12 _ ML _ 65113 _ PVC | C2NC-1800-MBR | Lines | 12 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 10 | 12 _ ML _ 65113 _ PVC | [10 empty] | Mixed Liquor | PVC | 12 | Membrane Tank B | MBR Recirculation Pump B | N | 100 |  | 150 #
6 Inch Stainless Steel MBR Permeate Line 651_04 | C2NC-1800-MBR-6 _ PER _ 65104 _ SSA1 | C2NC-1800-MBR | Lines | 6 Inch Stainless Steel Permeate Line | [9 empty] | AN-1156 A01 01 | 10 | 6 _ PER _ 65104 _ SSA1 | [10 empty] | Permeate | Stainless Steel | 6 | Membrane A | Permeate Pump A | N | 100 |  | 150 #
6 Inch Stainless Steel MBR Permeate Line 651_05 | C2NC-1800-MBR-6 _ PER _ 65105 _ SSA1 | C2NC-1800-MBR | Lines | 6 Inch Stainless Steel Permeate Line | [9 empty] | AN-1156 A01 01 | 10 | 6 _ PER _ 65105 _ SSA1 | [10 empty] | Permeate | Stainless Steel | 6 | Membrane B | Permeate Pump B | N | 100 |  | 150 #
8 Inch Stainless Steel MBR Areation Air in SBR system Line 651_01 | C2NC-1800-MBR-8 _ AA _ 65101 _ SSA1 | C2NC-1800-MBR | Lines | 8 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 10 | 8 _ AA _ 65101 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 8 | Membrane Blowers | Membrane Tank A | N | 15 |  | 150 #
8 Inch Stainless Steel MBR Areation Air in SBR system Line 651_02 | C2NC-1800-MBR-8 _ AA _ 65102 _ SSA1 | C2NC-1800-MBR | Lines | 8 Inch Stainless Steel Areation Air in SBR system Line | [9 empty] | AN-1156 A01 01 | 10 | 8 _ AA _ 65102 _ SSA1 | [10 empty] | Areation Air in SBR system | Stainless Steel | 8 | Membrane Blowers | Membrane Tank B | N | 15 |  | 150 #
8 Inch PVC MBR Mixed Liquor Line 651_11 | C2NC-1800-MBR-8 _ ML _ 65111 _ PVC | C2NC-1800-MBR | Lines | 8 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 10 | 8 _ ML _ 65111 _ PVC | [10 empty] | Mixed Liquor | PVC | 8 | MBR Recirculation Pump A | Membrane Tank A | N | 100 |  | 150 #
8 Inch PVC MBR Mixed Liquor Line 651_12 | C2NC-1800-MBR-8 _ ML _ 65112 _ PVC | C2NC-1800-MBR | Lines | 8 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 10 | 8 _ ML _ 65112 _ PVC | [10 empty] | Mixed Liquor | PVC | 8 | MBR Recirculation Pump A | Membrane Tank A | N | 100 |  | 150 #
8 Inch PVC MBR Mixed Liquor Line 651_14 | C2NC-1800-MBR-8 _ ML _ 65114 _ PVC | C2NC-1800-MBR | Lines | 8 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 10 | 8 _ ML _ 65114 _ PVC | [10 empty] | Mixed Liquor | PVC | 8 | MBR Recirculation Pump B | Membrane Tank B | N | 100 |  | 150 #
8 Inch PVC MBR Mixed Liquor Line 651_15 | C2NC-1800-MBR-8 _ ML _ 65115 _ PVC | C2NC-1800-MBR | Lines | 8 Inch PVC Mixed Liquor Line | [9 empty] | AN-1156 A01 01 | 10 | 8 _ ML _ 65115 _ PVC | [10 empty] | Mixed Liquor | PVC | 8 | MBR Recirculation Pump B | Membrane Tank B | N | 100 |  | 150 #
4 Inch PVC Permeate System Permeate Line 653_06 | C2NC-1800-PRM-4 _ PER _ 65306 _ PVC | C2NC-1800-PRM | Lines | 4 Inch PVC Permeate Line | [9 empty] | AN-1156 A01 01 | 13 | 4 _ PER _ 65306 _ PVC | [10 empty] | Permeate | PVC | 4 | Permeate Feed Pump A | Membrane Tank A | N | 100 |  | 150 #
4 Inch PVC Permeate System Permeate Line 653_07 | C2NC-1800-PRM-4 _ PER _ 65307 _ PVC | C2NC-1800-PRM | Lines | 4 Inch PVC Permeate Line | [9 empty] | AN-1156 A01 01 | 13 | 4 _ PER _ 65307 _ PVC | [10 empty] | Permeate | PVC | 4 | Permeate Feed Pump B | Membrane Tank B | N | 100 |  | 150 #
6 Inch Stainless Steel Permeate System Permeate Line 653_01 | C2NC-1800-PRM-6 _ PER _ 65301 _ SSA1 | C2NC-1800-PRM | Lines | 6 Inch Stainless Steel Permeate Line | [9 empty] | AN-1156 A01 01 | 13 | 6 _ PER _ 65301 _ SSA1 | [10 empty] | Permeate | Stainless Steel | 6 | Permeate Feed Pump A | MBR Container Exit | N | 100 |  | 150 #
6 Inch Stainless Steel Permeate System Permeate Line 653_02 | C2NC-1800-PRM-6 _ PER _ 65302 _ SSA1 | C2NC-1800-PRM | Lines | 6 Inch Stainless Steel Permeate Line | [9 empty] | AN-1156 A01 01 | 13 | 6 _ PER _ 65302 _ SSA1 | [10 empty] | Permeate | Stainless Steel | 6 | Permeate Feed Pump B | MBR Container Exit | N | 100 |  | 150 #
6 Inch PVC Permeate System Permeate Line 653_04 | C2NC-1800-PRM-6 _ PER _ 65304 _ PVC | C2NC-1800-PRM | Lines | 6 Inch PVC Permeate Line | [9 empty] | AN-1156 A01 01 | 13 | 6 _ PER _ 65304 _ PVC | [10 empty] | Permeate | PVC | 6 | Permeate Tank | Discharge | N | 100 |  | 150 #
6 Inch PVC Permeate System Permeate Line 653_05 | C2NC-1800-PRM-6 _ PER _ 65305 _ PVC | C2NC-1800-PRM | Lines | 6 Inch PVC Permeate Line | [9 empty] | AN-1156 A01 01 | 13 | 6 _ PER _ 65305 _ PVC | [10 empty] | Permeate | PVC | 6 | Permeate Pump A/MBR Container | Permeate Tank | N | 100 |  | 150 #
6 Inch PVC Permeate System Permeate Line 653_03 | C2NC-1800-PRM-8 _ PER _ 65303 _ PVC | C2NC-1800-PRM | Lines | 6 Inch PVC Permeate Line | [9 empty] | AN-1156 A01 01 | 13 | 8 _ PER _ 65303 _ PVC | [10 empty] | Permeate | PVC | 6 | Permeate Pump B/MBR Container | Permeate Tank | N | 100 |  | 150 #
10 Inch PVC WAS and RAS Systems Reutrn Activated Sludge Line 652_02 | C2NC-1800-RAS-10 _ RAS _ 65202 _ PVC | C2NC-1800-RAS | Lines | 10 Inch PVC Reutrn Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 11 | 10 _ RAS _ 65202 _ PVC | [10 empty] | Reutrn Activated Sludge | PVC | 10 | WAS Header | RAS Pump A | N | 100 |  | 150 #
10 Inch PVC WAS and RAS Systems Reutrn Activated Sludge Line 652_04 | C2NC-1800-RAS-10 _ RAS _ 65204 _ PVC | C2NC-1800-RAS | Lines | 10 Inch PVC Reutrn Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 14 | 10 _ RAS _ 65204 _ PVC | [10 empty] | Reutrn Activated Sludge | PVC | 10 | RAS Tank A | RAS Pump A | N | 100 |  | 150 #
10 Inch PVC WAS and RAS Systems Reutrn Activated Sludge Line 652_06 | C2NC-1800-RAS-10 _ RAS _ 65206 _ PVC | C2NC-1800-RAS | Lines | 10 Inch PVC Reutrn Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 14 | 10 _ RAS _ 65206 _ PVC | [10 empty] | Reutrn Activated Sludge | PVC | 10 | RAS Tank B | RAS Pump B | N | 100 |  | 150 #
12 Inch PVC WAS and RAS Systems Reutrn Activated Sludge Line 652_01 | C2NC-1800-RAS-12 _ RAS _ 65201 _ PVC | C2NC-1800-RAS | Lines | 12 Inch PVC Reutrn Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 6 | 12 _ RAS _ 65201 _ PVC | [10 empty] | Reutrn Activated Sludge | PVC | 12 | RAS Pumps | Anoxic Tank | N | 100 |  | 150 #
12 Inch PVC WAS and RAS Systems Reutrn Activated Sludge Line 652_05 | C2NC-1800-RAS-12 _ RAS _ 65205 _ PVC | C2NC-1800-RAS | Lines | 12 Inch PVC Reutrn Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 14 | 12 _ RAS _ 65205 _ PVC | [10 empty] | Reutrn Activated Sludge | PVC | 12 | RAS Pump A | RAS Pump Discharge Header | N | 100 |  | 150 #
12 Inch PVC WAS and RAS Systems Reutrn Activated Sludge Line 652_07 | C2NC-1800-RAS-12 _ RAS _ 65207 _ PVC | C2NC-1800-RAS | Lines | 12 Inch PVC Reutrn Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 14 | 12 _ RAS _ 65207 _ PVC | [10 empty] | Reutrn Activated Sludge | PVC | 12 | RAS Pump B | RAS Pump Discharge Header | N | 100 |  | 150 #
12 Inch PVC WAS and RAS Systems Reutrn Activated Sludge Line 652_08 | C2NC-1800-RAS-12 _ RAS _ 65208 _ PVC | C2NC-1800-RAS | Lines | 12 Inch PVC Reutrn Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 7 | 12 _ RAS _ 65208 _ PVC | [10 empty] | Reutrn Activated Sludge | PVC | 12 | RAS Pumps | Aerobic Tank A | N | 100 |  | 150 #
12 Inch PVC WAS and RAS Systems Reutrn Activated Sludge Line 652_09 | C2NC-1800-RAS-12 _ RAS _ 65209 _ PVC | C2NC-1800-RAS | Lines | 12 Inch PVC Reutrn Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 8 | 12 _ RAS _ 65209 _ PVC | [10 empty] | Reutrn Activated Sludge | PVC | 12 | RAS Pumps | Aerobic Tank B | N | 100 |  | 150 #
4 Inch PVC WAS and RAS Systems Waste Activated Sludge Line 652_11 | C2NC-1800-RAS-4 _ WAS _ 65211 _ PVC | C2NC-1800-RAS | Lines | 4 Inch PVC Waste Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 15 | 4 _ WAS _ 65211 _ PVC | [10 empty] | Waste Activated Sludge | PVC | 4 | WAS Pump A | WAS Pump Discharge Header | N | 100 |  | 150 #
4 Inch PVC WAS and RAS Systems Waste Activated Sludge Line 652_13 | C2NC-1800-RAS-4 _ WAS _ 65213 _ PVC | C2NC-1800-RAS | Lines | 4 Inch PVC Waste Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 15 | 4 _ WAS _ 65213 _ PVC | [10 empty] | Waste Activated Sludge | PVC | 4 | WAS Pump B | WAS Pump Discharge Header | N | 100 |  | 150 #
4 Inch PVC WAS and RAS Systems Waste Activated Sludge Line 652_15 | C2NC-1800-RAS-4 _ WAS _ 65215 _ PVC | C2NC-1800-RAS | Lines | 4 Inch PVC Waste Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 15 | 4 _ WAS _ 65215 _ PVC | [10 empty] | Waste Activated Sludge | PVC | 4 | WAS Pump Discharge Header | WAS Dewatering Press/MBR Container Exit | N | 100 |  | 150 #
4 Inch PVC WAS and RAS Systems Waste Activated Sludge Line 652_17 | C2NC-1800-RAS-4 _ WAS _ 65217 _ PVC1 | C2NC-1800-RAS | Lines | 4 Inch PVC Waste Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 16 | 4 _ WAS _ 65217 _ PVC1 | [10 empty] | Waste Activated Sludge | PVC | 4 | Below Grade WAS Line Segment |  | N | 100 |  | 150 #
4 Inch PVC WAS and RAS Systems Waste Activated Sludge Line 652_18 | C2NC-1800-RAS-4 _ WAS _ 65218 _ PVC | C2NC-1800-RAS | Lines | 4 Inch PVC Waste Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 16 | 4 _ WAS _ 65218 _ PVC | [10 empty] | Waste Activated Sludge | PVC | 4 | WAS Pumps/MBR Container | Below Grade WAS Line Segment | N | 100 |  | 150 #
6 Inch PVC WAS and RAS Systems Waste Activated Sludge Line 652_03 | C2NC-1800-RAS-6 _ WAS _ 65203 _ PVC | C2NC-1800-RAS | Lines | 6 Inch PVC Waste Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 11 | 6 _ WAS _ 65203 _ PVC | [10 empty] | Waste Activated Sludge | PVC | 6 | WAS Header | WAS Pump A | N | 100 |  | 150 #
6 Inch PVC WAS and RAS Systems Waste Activated Sludge Line 652_10 | C2NC-1800-RAS-6 _ WAS _ 65210 _ PVC | C2NC-1800-RAS | Lines | 6 Inch PVC Waste Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 15 | 6 _ WAS _ 65210 _ PVC | [10 empty] | Waste Activated Sludge | PVC | 6 | RAS Header | WAS Pump A | N | 100 |  | 150 #
6 Inch PVC WAS and RAS Systems Waste Activated Sludge Line 652_12 | C2NC-1800-RAS-6 _ WAS _ 65212 _ PVC | C2NC-1800-RAS | Lines | 6 Inch PVC Waste Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 15 | 6 _ WAS _ 65212 _ PVC | [10 empty] | Waste Activated Sludge | PVC | 6 | RAS Header | WAS Pump B | N | 100 |  | 150 #
6 Inch PVC WAS and RAS Systems Waste Activated Sludge Line 652_19 | C2NC-1800-RAS-6 _ WAS _ 65219 _ PVC | C2NC-1800-RAS | Lines | 6 Inch PVC Waste Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 16 | 6 _ WAS _ 65219 _ PVC | [10 empty] | Waste Activated Sludge | PVC | 6 | Below Grade WAS Line Segment | WAS Dewatering Press Flocculation Tank | N | 100 |  | 150 #
6 Inch PVC WAS and RAS Systems Waste Activated Sludge Line 652_20 | C2NC-1800-RAS-6 _ WAS _ 65220 _ PVC | C2NC-1800-RAS | Lines | 6 Inch PVC Waste Activated Sludge Line | [9 empty] | AN-1156 A01 01 | 11 | 6 _ WAS _ 65220 _ PVC | [10 empty] | Waste Activated Sludge | PVC | 6 | WAS Header | WAS Pump B | N | 100 |  | 150 #
4 Inch PVC WAS Screw Dewatering Press SSD Filtrate Line 514_01 | C2NC-1800-WAS-4 _ FLT _ 51401 _ PVC1 | C2NC-1800-WAS | Lines | 4 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 16 | 4 _ FLT _ 51401 _ PVC1 | [10 empty] | SSD Filtrate | PVC | 4 | WAS Dewatering Press Exit - Above Grade | WAS Filtrate Sump | N | 100 |  | 150 #
4 Inch PVC WAS Screw Dewatering Press SSD Filtrate Line 514_02 | C2NC-1800-WAS-4 _ FLT _ 51402 _ PVC | C2NC-1800-WAS | Lines | 4 Inch PVC SSD Filtrate Line | [9 empty] | AN-1156 A01 01 | 16 | 4 _ FLT _ 51402 _ PVC | [10 empty] | SSD Filtrate | PVC | 4 | WAS Dewatering Press | WAS Dewatering Press Exit - Below Grade | N | 100 |  | 150 #
1800 - Waste Water Treatment Plant | C2NC-1800 | C2NC | Locations And Facilities | Waste Water Treatment Plant
Aeration Blowers | C2NC-1800-ABL | C2NC-1800 | Locations And Facilities | Aeration Blowers
Anoxic Tank | C2NC-1800-ANX | C2NC-1800 | Locations And Facilities | Anoxic Tank
Aerobic Tank A | C2NC-1800-ARB_A | C2NC-1800 | Locations And Facilities | Aerobic Tank A
Aerobic Tank B | C2NC-1800-ARB_B | C2NC-1800 | Locations And Facilities | Aerobic Tank B
Chemical Dosing | C2NC-1800-CHEM | C2NC-1800 | Locations And Facilities | Chemical Dosing
Caustic Dosing System | C2NC-1800-CHEM-CAUS | C2NC-1800-CHEM | Locations And Facilities | Caustic Dosing System
Acid Dosing System | C2NC-1800-CHEM-CITR | C2NC-1800-CHEM | Locations And Facilities | Acid Dosing System
Antifoam Dosing System | C2NC-1800-CHEM-FOAM | C2NC-1800-CHEM | Locations And Facilities | Antifoam Dosing System
Sodium Hypochlorite System | C2NC-1800-CHEM-HYPO | C2NC-1800-CHEM | Locations And Facilities | Sodium Hypochlorite System
Emulsion Polymer WAS | C2NC-1800-FLOC | C2NC-1800 | Locations And Facilities | Emulsion Polymer WAS
Membrane Bio-Reactor | C2NC-1800-MBR | C2NC-1800 | Locations And Facilities | Membrane Bio-Reactor
Permeate System | C2NC-1800-PRM | C2NC-1800 | Locations And Facilities | Permeate System
WAS and RAS Syetem | C2NC-1800-RAS | C2NC-1800 | Locations And Facilities | WAS and RAS Syetem
WAS Screw Dewatering Press System | C2NC-1800-WAS | C2NC-1800 | Locations And Facilities | WAS Screw Dewatering Press System
Anoxic Tank - Anoxic tank | C2NC-1800-ANX-TK_63100 | C2NC-1800-ANX | Tanks | Anoxic tank | [9 empty] | AN-0119 A01-01 | 6 | TK_63100 | [8 empty] | Tank | [25 empty] | 66.5 x 155 | 29.5
Aerobic Tank A - Aerobic tank A | C2NC-1800-ARB_A-TK_63200 | C2NC-1800-ARB_A | Tanks | Aerobic tank A | [9 empty] | AN-0119 A01-01 | 7 | TK_63200 | [8 empty] | Tank | [25 empty] | 75.25 x 135 | 29.5
Aerobic Tank B - Aerobic tank B | C2NC-1800-ARB_B-TK_63300 | C2NC-1800-ARB_B | Tanks | Aerobic tank B | [9 empty] | AN-0119 A01-01 | 8 | TK_63300 | [8 empty] | Tank | [25 empty] | 75.25 x 135 | 29.5
Caustic Dosing System - Sodium hydroxide tank | C2NC-1800-CHEM-CAUS-TK_31100 | C2NC-1800-CHEM-CAUS | Tanks | Sodium hydroxide tank | [9 empty] | AN-0119 A01-01 | 19 | TK_31100 | [8 empty] | Tank
Acid Dosing System - Citric acid tote | C2NC-1800-CHEM-CITR-TK_32100 | C2NC-1800-CHEM-CITR | Tanks | Citric acid tote | [9 empty] | AN-0119 A01-01 | 19 | TK_32100 | [8 empty] | Tank
Antifoam Dosing System - Antifoam tote | C2NC-1800-CHEM-FOAM-TK_37100 | C2NC-1800-CHEM-FOAM | Tanks | Antifoam tote | [9 empty] | AN-0119 A01-01 | 19 | TK_37100 | [8 empty] | Tank
Sodium Hypochlorite System - Sodium hypochlorite tote | C2NC-1800-CHEM-HYPO-TK_31200 | C2NC-1800-CHEM-HYPO | Tanks | Sodium hypochlorite tote | [9 empty] | AN-0119 A01-01 | 19 | TK_31200 | [8 empty] | Tank
Emulsion Polymer WAS - Emulsion polymer sotrage tote for WAS dewatering polymer system | C2NC-1800-FLOC-TK_35200 | C2NC-1800-FLOC | Tanks | Emulsion polymer sotrage tote for WAS dewatering polymer system | [9 empty] | AN-0119 A01-01 | 17 | TK_35200 | [8 empty] | Tank
MBR - Membrane Tank A | C2NC-1800-MBR-TK_65100 | C2NC-1800-MBR | Tanks | Membrane Tank A | Anaergia IS | [8 empty] | AN-0119 A01-01 | 10 | TK_65100 | [8 empty] | Tank | [25 empty] | 22.33 x 8 | 10.67
MBR - Membrane Tank B | C2NC-1800-MBR-TK_65101 | C2NC-1800-MBR | Tanks | Membrane Tank B | Anaergia IS | [8 empty] | AN-0119 A01-01 | 10 | TK_65101 | [8 empty] | Tank | [25 empty] | 22.33 x 8 | 10.67
WAS and RAS Systems - Mixed Liquor Overflow Tank | C2NC-1800-RAS-TK_65200 | C2NC-1800-RAS | Tanks | Mixed Liquor Overflow Tank | [9 empty] | AN-0119 A01-01 | 11 | TK_65200 | [8 empty] | Tank
WAS Screw Dewatering Press - Flocculation tank for WAS Dewatering Press | C2NC-1800-WAS-TK_51401 | C2NC-1800-WAS | Tanks | Flocculation tank for WAS Dewatering Press | [9 empty] | AN-0119 A01-01 | 16 | TK_51401 | [8 empty] | Tank | [25 empty] | 2.95 x 2.95 | 5.91
Aeration Blowers - Swing Check Valve - 00 | C2NC-1800-ABL-CV_63500 | C2NC-1800-ABL | Valves | Aeration Blowers Check Valve |  | SWING |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | CV_63500 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 12 |  |  | Manual | Swing Check Valve | N.A | FLG
Aeration Blowers - Swing Check Valve - 01 | C2NC-1800-ABL-CV_63501 | C2NC-1800-ABL | Valves | Aeration Blowers Check Valve |  | SWING |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | CV_63501 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 12 |  |  | Manual | Swing Check Valve | N.A | FLG
Aeration Blowers - Swing Check Valve - 02 | C2NC-1800-ABL-CV_63502 | C2NC-1800-ABL | Valves | Aeration Blowers Check Valve |  | SWING |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | CV_63502 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 12 |  |  | Manual | Swing Check Valve | N.A | FLG
Aeration Blowers - Swing Check Valve - 03 | C2NC-1800-ABL-CV_63503 | C2NC-1800-ABL | Valves | Aeration Blowers Check Valve |  | SWING |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | CV_63503 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 12 |  |  | Manual | Swing Check Valve | N.A | FLG
Aeration Blowers - Swing Check Valve - 04 | C2NC-1800-ABL-CV_63504 | C2NC-1800-ABL | Valves | Aeration Blowers Check Valve |  | SWING |  |  |  | Aerzen |  |  |  | AN-1156 A01 01 | 9 | CV_63504 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 12 |  |  | Manual | Swing Check Valve | N.A | FLG
Aeration Blowers - Butterfly Valve - 03 | C2NC-1800-ABL-MV_63503 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve - MAXSEAL 16IN 150# LUG BFVEPOXY COATED DI BODY, SS DISC, 17-4PH SS SHAFT, EPDM SEAT, GEAR OPERATED |  | 52-DI-SS-S7-E-G-400 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 9 | MV_63503 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 16 |  |  | Manual | Butterfly Valve | Manual | LUG
Aeration Blowers - Butterfly Valve - 05 | C2NC-1800-ABL-MV_63505 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve - MAXSEAL 16IN 150# LUG BFVEPOXY COATED DI BODY, SS DISC, 17-4PH SS SHAFT, EPDM SEAT, GEAR OPERATED |  | 52-DI-SS-S7-E-G-400 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 9 | MV_63505 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 16 |  |  | Manual | Butterfly Valve | Manual | LUG
Aeration Blowers - Butterfly Valve - 06 | C2NC-1800-ABL-MV_63506 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve - MAXSEAL 16IN 150# LUG BFVEPOXY COATED DI BODY, SS DISC, 17-4PH SS SHAFT, EPDM SEAT, GEAR OPERATED |  | 52-DI-SS-S7-E-G-400 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 9 | MV_63506 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 16 |  |  | Manual | Butterfly Valve | Manual | LUG
Aeration Blowers - Butterfly Valve - 07 | C2NC-1800-ABL-MV_63507 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve - MAXSEAL 16IN 150# LUG BFVEPOXY COATED DI BODY, SS DISC, 17-4PH SS SHAFT, EPDM SEAT, GEAR OPERATED |  | 52-DI-SS-S7-E-G-400 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 9 | MV_63507 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 16 |  |  | Manual | Butterfly Valve | Manual | LUG
Aeration Blowers - Butterfly Valve - 09 | C2NC-1800-ABL-MV_63509 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve - MAXSEAL 16IN 150# LUG BFVEPOXY COATED DI BODY, SS DISC, 17-4PH SS SHAFT, EPDM SEAT, GEAR OPERATED |  | 52-DI-SS-S7-E-G-400 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 9 | MV_63509 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 16 |  |  | Manual | Butterfly Valve | Manual | LUG
Aeration Blowers - Ball Valve - 10 | C2NC-1800-ABL-MV_63510 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve |  | 46495K21 |  |  |  | McMaster Carr |  |  |  | AN-1156 A01 01 | 9 | MV_63510 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Aeration Blowers - Butterfly Valve - 11 | C2NC-1800-ABL-MV_63511 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve - MAXSEAL 16IN 150# LUG BFVEPOXY COATED DI BODY, SS DISC, 17-4PH SS SHAFT, EPDM SEAT, GEAR OPERATED |  | 52-DI-SS-S7-E-G-400 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 9 | MV_63511 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 16 |  |  | Manual | Butterfly Valve | Manual | LUG
Aeration Blowers - Ball Valve - 12 | C2NC-1800-ABL-MV_63512 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve |  | 46495K21 |  |  |  | McMaster Carr |  |  |  | AN-1156 A01 01 | 9 | MV_63512 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Aeration Blowers - Ball Valve - 13 | C2NC-1800-ABL-MV_63513 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve |  | 46495K21 |  |  |  | McMaster Carr |  |  |  | AN-1156 A01 01 | 9 | MV_63513 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Aeration Blowers - Ball Valve - 14 | C2NC-1800-ABL-MV_63514 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve |  | 46495K21 |  |  |  | McMaster Carr |  |  |  | AN-1156 A01 01 | 9 | MV_63514 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Aeration Blowers - Ball Valve - 15 | C2NC-1800-ABL-MV_63515 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve |  | 46495K21 |  |  |  | McMaster Carr |  |  |  | AN-1156 A01 01 | 9 | MV_63515 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Aeration Blowers - Ball Valve - 16 | C2NC-1800-ABL-MV_63516 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve |  | 46495K21 |  |  |  | McMaster Carr |  |  |  | AN-1156 A01 01 | 9 | MV_63516 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Aeration Blowers - Ball Valve - 18 | C2NC-1800-ABL-MV_63518 | C2NC-1800-ABL | Valves | Aeration Blowers Manual Valve |  | 46495K21 |  |  |  | McMaster Carr |  |  |  | AN-1156 A01 01 | 9 | MV_63518 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Aeration Blowers - Pressure Relief Valve - 00 | C2NC-1800-ABL-PRV_63500 | C2NC-1800-ABL | Valves | Aeration Blowers Pressure Relief Valve - Spring loaded pressure valve with cylindrical protection jacket providing overload protection for positive displacement blower | [5 empty] | Aerzen |  |  |  | AN-1156 A01 01 | 9 | PRV_63500 | [11 empty] | SSA1 | [11 empty] | 8 |  |  | Manual | Pressure Relief Valve | TBD | Part of skid
Aeration Blowers - Pressure Relief Valve - 01 | C2NC-1800-ABL-PRV_63501 | C2NC-1800-ABL | Valves | Aeration Blowers Pressure Relief Valve - Spring loaded pressure valve with cylindrical protection jacket providing overload protection for positive displacement blower | [5 empty] | Aerzen |  |  |  | AN-1156 A01 01 | 9 | PRV_63501 | [11 empty] | SSA1 | [11 empty] | 8 |  |  | Manual | Pressure Relief Valve | TBD | Part of skid
Aeration Blowers - Pressure Relief Valve - 02 | C2NC-1800-ABL-PRV_63502 | C2NC-1800-ABL | Valves | Aeration Blowers Pressure Relief Valve - Spring loaded pressure valve with cylindrical protection jacket providing overload protection for positive displacement blower | [5 empty] | Aerzen |  |  |  | AN-1156 A01 01 | 9 | PRV_63502 | [11 empty] | SSA1 | [11 empty] | 8 |  |  | Manual | Pressure Relief Valve | TBD | Part of skid
Aeration Blowers - Pressure Relief Valve - 03 | C2NC-1800-ABL-PRV_63503 | C2NC-1800-ABL | Valves | Aeration Blowers Pressure Relief Valve - Spring loaded pressure valve with cylindrical protection jacket providing overload protection for positive displacement blower | [5 empty] | Aerzen |  |  |  | AN-1156 A01 01 | 9 | PRV_63503 | [11 empty] | SSA1 | [11 empty] | 8 |  |  | Manual | Pressure Relief Valve | TBD | Part of skid
Aeration Blowers - Pressure Relief Valve - 04 | C2NC-1800-ABL-PRV_63504 | C2NC-1800-ABL | Valves | Aeration Blowers Pressure Relief Valve - Spring loaded pressure valve with cylindrical protection jacket providing overload protection for positive displacement blower | [5 empty] | Aerzen |  |  |  | AN-1156 A01 01 | 9 | PRV_63504 | [11 empty] | SSA1 | [11 empty] | 8 |  |  | Manual | Pressure Relief Valve | TBD | Part of skid
Anoxic Tank - Knife-Gate Valve - 14 | C2NC-1800-ANX-MV_63114 | C2NC-1800-ANX | Valves | Anoxic Tank Manual Valve - DAVIS 6IN 59FE 316SS LUG STYLE KNIFE GATE VALVE, EPDM UNIDIRECTIONAL SEAT, HAND WHEEL OPERATED | [5 empty] | FCx |  |  |  | AN-1156 A01 01 | 6 | MV_63114 | [11 empty] | CSA | [11 empty] | 6 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Anoxic Tank - Knife-Gate Valve - 22 | C2NC-1800-ANX-MV_63122 | C2NC-1800-ANX | Valves | Anoxic Tank Manual Valve - 8 ORBIN OX LUG SOFT SEAT KNIFE GATE VALVE SS BODY EPDM SEAT SERIES 20-3636R-HW |  | 800203636RKGV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 6 | MV_63122 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 8 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank A - Pinch Valve - 00 | C2NC-1800-ARB_A-FV_63200 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Pneumatic Valve | [5 empty] | AKO Pinch Valves |  |  |  | AN-1156 A01 01 | 7 | FV_63200 | [11 empty] | Aluminum | [11 empty] | 10 |  |  | Automatic | Pinch Valve | Pneumatic | Flanged
Aerobic Tank A - Knife-Gate Valve - 00 | C2NC-1800-ARB_A-MV_63200 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve - 10" 20-3636R-10.0-HW ORBINOX KN1FE VALVE BODY AND GATE 316SS EPDMSEAT |  | 495ORB1000203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 7 | MV_63200 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 10 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank A - Ball Valve - 01 | C2NC-1800-ARB_A-MV_63201 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve |  | "EBRO" or similar |  |  |  | Endress and Hauser |  |  |  | AN-1156 A01 01 | 7 | MV_63201 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 2 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Aerobic Tank A - Knife-Gate Valve - 03 | C2NC-1800-ARB_A-MV_63203 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve - 10" 20-3636R-10.0-HW ORBINOX KN1FE VALVE BODY AND GATE 316SS EPDMSEAT |  | 495ORB1000203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 7 | MV_63203 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 10 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank A - Knife-Gate Valve - 04 | C2NC-1800-ARB_A-MV_63204 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve - 10" 20-3636R-10.0-HW ORBINOX KN1FE VALVE BODY AND GATE 316SS EPDMSEAT |  | 495ORB1000203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 7 | MV_63204 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 10 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank A - Knife-Gate Valve - 05 | C2NC-1800-ARB_A-MV_63205 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve - 10" 20-3636R-10.0-HW ORBINOX KN1FE VALVE BODY AND GATE 316SS EPDMSEAT |  | 495ORB1000203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 7 | MV_63205 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 10 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank A - Butterfly Valve - 06 | C2NC-1800-ARB_A-MV_63206 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve - MAXSEAL 12" 150# LUG BFVEPOXY COATED DI BODY, SS DISC AND STEM, EPDM SEAT, GEAR OPERATED. |  | MS 12IN-52DISSS6EG250 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 7 | MV_63206 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 12 |  |  | Manual | Butterfly Valve | Manual | LUG
Aerobic Tank A - Butterfly Valve - 07 | C2NC-1800-ARB_A-MV_63207 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve - MAXSEAL 12" 150# LUG BFVEPOXY COATED DI BODY, SS DISC AND STEM, EPDM SEAT, GEAR OPERATED. |  | MS 12IN-52DISSS6EG250 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 7 | MV_63207 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 12 |  |  | Manual | Butterfly Valve | Manual | LUG
Aerobic Tank A - Butterfly Valve - 08 | C2NC-1800-ARB_A-MV_63208 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve - MAXSEAL 12" 150# LUG BFVEPOXY COATED DI BODY, SS DISC AND STEM, EPDM SEAT, GEAR OPERATED. |  | MS 12IN-52DISSS6EG250 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 7 | MV_63208 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 12 |  |  | Manual | Butterfly Valve | Manual | LUG
Aerobic Tank A - Butterfly Valve - 09 | C2NC-1800-ARB_A-MV_63209 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve - MAXSEAL 12" 150# LUG BFVEPOXY COATED DI BODY, SS DISC AND STEM, EPDM SEAT, GEAR OPERATED. |  | MS 12IN-52DISSS6EG250 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 7 | MV_63209 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 12 |  |  | Manual | Butterfly Valve | Manual | LUG
Aerobic Tank A - Knife-Gate Valve - 10 | C2NC-1800-ARB_A-MV_63210 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve |  | 800203636RKGV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 7 | MV_63210 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 8 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank A - Knife-Gate Valve - 14 | C2NC-1800-ARB_A-MV_63214 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve - DAVIS 6IN 59FE 316SS LUG STYLE KNIFE GATE VALVE, EPDM UNIDIRECTIONAL SEAT, HAND WHEEL OPERATED | [5 empty] | FCx |  |  |  | AN-1156 A01 01 | 7 | MV_63214 | [11 empty] | CSA | [11 empty] | 6 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank A - Ball Valve - 15 | C2NC-1800-ARB_A-MV_63215 | C2NC-1800-ARB_A | Valves | Aerobic Tank A Manual Valve - Eliminator series Two piece Standardport ball valve, 316 Stainless steel body, ball and stem, Fire safe, Xtreme seats, Enhanced seals, Threaded ends, locking lever operated |  | NJ 1/2IN 9FB-3600XTB |  |  |  | FCX |  |  |  | AN-1156 A01 01 | 7 | MV_63215 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Aerobic Tank B - Pinch Valve - 00 | C2NC-1800-ARB_B-FV_63300 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Pneumatic Valve | [5 empty] | AKO Pinch Valves |  |  |  | AN-1156 A01 01 | 8 | FV_63300 | [11 empty] | Aluminum | [11 empty] | 10 |  |  | Automatic | Pinch Valve | Pneumatic | Flanged
Aerobic Tank B - Knife-Gate Valve - 00 | C2NC-1800-ARB_B-MV_63300 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Manual Valve - 10" 20-3636R-10.0-HW ORBINOX KN1FE VALVE BODY AND GATE 316SS EPDMSEAT |  | 495ORB1000203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 8 | MV_63300 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 10 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank B - Ball Valve - 01 | C2NC-1800-ARB_B-MV_63301 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Manual Valve |  | "EBRO" or similar |  |  |  | Endress and Hauser |  |  |  | AN-1156 A01 01 | 8 | MV_63301 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 2 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Aerobic Tank B - Knife-Gate Valve - 03 | C2NC-1800-ARB_B-MV_63303 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Manual Valve - 10" 20-3636R-10.0-HW ORBINOX KN1FE VALVE BODY AND GATE 316SS EPDMSEAT |  | 495ORB1000203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 8 | MV_63303 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 10 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank B - Knife-Gate Valve - 04 | C2NC-1800-ARB_B-MV_63304 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Manual Valve - 10" 20-3636R-10.0-HW ORBINOX KN1FE VALVE BODY AND GATE 316SS EPDMSEAT |  | 495ORB1000203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 8 | MV_63304 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 10 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank B - Butterfly Valve - 06 | C2NC-1800-ARB_B-MV_63306 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Manual Valve - MAXSEAL 12" 150# LUG BFVEPOXY COATED DI BODY, SS DISC AND STEM, EPDM SEAT, GEAR OPERATED. |  | MS 12IN-52DISSS6EG250 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 8 | MV_63306 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 12 |  |  | Manual | Butterfly Valve | Manual | LUG
Aerobic Tank B - Butterfly Valve - 07 | C2NC-1800-ARB_B-MV_63307 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Manual Valve - MAXSEAL 12" 150# LUG BFVEPOXY COATED DI BODY, SS DISC AND STEM, EPDM SEAT, GEAR OPERATED. |  | MS 12IN-52DISSS6EG250 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 8 | MV_63307 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 12 |  |  | Manual | Butterfly Valve | Manual | LUG
Aerobic Tank B - Butterfly Valve - 08 | C2NC-1800-ARB_B-MV_63308 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Manual Valve - MAXSEAL 12" 150# LUG BFVEPOXY COATED DI BODY, SS DISC AND STEM, EPDM SEAT, GEAR OPERATED. |  | MS 12IN-52DISSS6EG250 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 7 | MV_63308 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 12 |  |  | Manual | Butterfly Valve | Manual | LUG
Aerobic Tank B - Butterfly Valve - 09 | C2NC-1800-ARB_B-MV_63309 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Manual Valve - MAXSEAL 12" 150# LUG BFVEPOXY COATED DI BODY, SS DISC AND STEM, EPDM SEAT, GEAR OPERATED. |  | MS 12IN-52DISSS6EG250 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 7 | MV_63309 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 12 |  |  | Manual | Butterfly Valve | Manual | LUG
Aerobic Tank B - Knife-Gate Valve - 10 | C2NC-1800-ARB_B-MV_63310 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Manual Valve |  | 800203636RKGV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 8 | MV_63310 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 8 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank B - Knife-Gate Valve - 14 | C2NC-1800-ARB_B-MV_63314 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Manual Valve - DAVIS 6IN 59FE 316SS LUG STYLE KNIFE GATE VALVE, EPDM UNIDIRECTIONAL SEAT, HAND WHEEL OPERATED | [5 empty] | FCx |  |  |  | AN-1156 A01 01 | 8 | MV_63314 | [11 empty] | CSA | [11 empty] | 6 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Aerobic Tank B - Ball Valve - 15 | C2NC-1800-ARB_B-MV_63315 | C2NC-1800-ARB_B | Valves | Aerobic Tank B Manual Valve - Eliminator series Two piece Standardport ball valve, 316 Stainless steel body, ball and stem, Fire safe, Xtreme seats, Enhanced seals, Threaded ends, locking lever operated |  | NJ 1/2IN 9FB-3600XTB |  |  |  | FCX |  |  |  | AN-1156 A01 01 | 8 | MV_63315 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Caustic Dosing System - Swing Check Valve - 00 | C2NC-1800-CHEM-CAUS-CV_31100 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Check Valve |  | Ball |  |  |  | Grainger |  |  |  | AN-1156 A01 01 | 14 | CV_31100 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B | 0.5 |  |  | Manual | Swing Check Valve | N.A | THRD-F NPT
Caustic Dosing System - Ball Valve - 00 | C2NC-1800-CHEM-CAUS-MV_31100 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_31100 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
Caustic Dosing System - Ball Valve - 01 | C2NC-1800-CHEM-CAUS-MV_31101 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_31101 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Caustic Dosing System - Ball Valve - 02 | C2NC-1800-CHEM-CAUS-MV_31102 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_31102 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Caustic Dosing System - Ball Valve - 03 | C2NC-1800-CHEM-CAUS-MV_31103 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_31103 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Caustic Dosing System - Ball Valve - 04 | C2NC-1800-CHEM-CAUS-MV_31104 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_31104 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Caustic Dosing System - Ball Valve - 05 | C2NC-1800-CHEM-CAUS-MV_31105 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Manual Valve - SIMTECH TBB1016005 1/2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016005 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 14 | MV_31105 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
Caustic Dosing System - Ball Valve - 06 | C2NC-1800-CHEM-CAUS-MV_31106 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Manual Valve - SIMTECH TBB1016005 1/2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016005 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 19 | MV_31106 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
Caustic Dosing System - Ball Valve - 07 | C2NC-1800-CHEM-CAUS-MV_31107 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Manual Valve - SIMTECH TBB1016010 1" PVC/EPDM TU Ball Valve, Flange |  | TBB1016010 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 19 | MV_31107 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1 |  |  | Manual | Ball Valve | Manual | Flanged
Caustic Dosing System - Ball Valve - 08 | C2NC-1800-CHEM-CAUS-MV_31108 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_31108 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Caustic Dosing System - Ball Valve - 09 | C2NC-1800-CHEM-CAUS-MV_31109 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_31109 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Caustic Dosing System - Ball Valve - 10 | C2NC-1800-CHEM-CAUS-MV_31110 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_31110 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Caustic Dosing System - Pressure Control Valve - 00 | C2NC-1800-CHEM-CAUS-PRV_31100 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Pressure Relief Valve | [9 empty] | AN-1156 A01 01 | 19 | PRV_31100 | [11 empty] | PVC | [11 empty] | 0.5 |  |  | Manual | Pressure Control Valve | TBD | THRD-F NPT
Caustic Dosing System - Pressure Reduction Valve - 01 | C2NC-1800-CHEM-CAUS-PRV_31101 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Pressure Relief Valve | [9 empty] | AN-1156 A01 01 | 19 | PRV_31101 | [11 empty] | PVC | [11 empty] | 0.75 |  |  | Manual | Pressure Reduction Valve | N.A | THRD-F NPT
Caustic Dosing System - Pressure Safety Valve - 00 | C2NC-1800-CHEM-CAUS-PSV_31100 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Pressure Saftey Valve | [9 empty] | AN-1156 A01 01 | 19 | PSV_31100 | [11 empty] | PVC | [11 empty] | 1 |  |  | Manual | Pressure Safety Valve | N.A | THRD-F NPT
Caustic Dosing System - Pressure Safety Valve - 01 | C2NC-1800-CHEM-CAUS-PSV_31101 | C2NC-1800-CHEM-CAUS | Valves | Caustic Dosing System Pressure Saftey Valve | [9 empty] | AN-1156 A01 01 | 19 | PSV_31101 | [11 empty] | PVC | [11 empty] | 1 |  |  | Manual | Pressure Safety Valve | N.A | THRD-F NPT
Acid Dosing System - Ball Valve - 00 | C2NC-1800-CHEM-CITR-MV_32100 | C2NC-1800-CHEM-CITR | Valves | Acid Dosing System Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | 1/2 2-PC FP BALL 1000 WOG |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 19 | MV_32100 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
Acid Dosing System - Ball Valve - 01 | C2NC-1800-CHEM-CITR-MV_32101 | C2NC-1800-CHEM-CITR | Valves | Acid Dosing System Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | 1/2 2-PC FP BALL 1000 WOG |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 19 | MV_32101 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
Acid Dosing System - Needle Valve - 02 | C2NC-1800-CHEM-CITR-MV_32102 | C2NC-1800-CHEM-CITR | Valves | Acid Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_32102 | [11 empty] | PVC | [10 empty] | TBD | 0.5 |  |  | Manual | Needle Valve | Manual | TBD
Acid Dosing System - Ball Valve - 03 | C2NC-1800-CHEM-CITR-MV_32103 | C2NC-1800-CHEM-CITR | Valves | Acid Dosing System Manual Valve - SIMTECH TBB1016010 1" PVC/EPDM TU Ball Valve, Flange |  | TBB1016010 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 19 | MV_32103 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1 |  |  | Manual | Ball Valve | Manual | Flanged
Acid Dosing System - Ball Valve - 04 | C2NC-1800-CHEM-CITR-MV_32104 | C2NC-1800-CHEM-CITR | Valves | Acid Dosing System Manual Valve - SIMTECH TBB1016010 1" PVC/EPDM TU Ball Valve, Flange |  | TBB1016010 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 19 | MV_32104 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1 |  |  | Manual | Ball Valve | Manual | Flanged
Acid Dosing System - Ball Valve - 05 | C2NC-1800-CHEM-CITR-MV_32105 | C2NC-1800-CHEM-CITR | Valves | Acid Dosing System Manual Valve - 1 2-PC FP BALL 1000 WOG |  | TBD |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 19 | MV_32105 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1 |  |  | Manual | Ball Valve | Manual | Flanged
Acid Dosing System - Pressure Control Valve - 00 | C2NC-1800-CHEM-CITR-PRV_32100 | C2NC-1800-CHEM-CITR | Valves | Acid Dosing System Pressure Relief Valve | [9 empty] | AN-1156 A01 01 | 19 | PRV_32100 | [11 empty] | PVC | [11 empty] | 1 |  |  | Manual | Pressure Control Valve | TBD | THRD-F NPT
Acid Dosing System - Pressure Safety Valve - 00 | C2NC-1800-CHEM-CITR-PSV_32100 | C2NC-1800-CHEM-CITR | Valves | Acid Dosing System Pressure Saftey Valve | [9 empty] | AN-1156 A01 01 | 19 | PSV_32100 | [11 empty] | PVC | [11 empty] | 1 |  |  | Manual | Pressure Safety Valve | N.A | THRD-F NPT
Antifoam Dosing System - Ball Check Valve - 00 | C2NC-1800-CHEM-FOAM-CV_37100 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Check Valve - SIMTECH BCQ1016005 1/2" PVC/EPDM T.U. Ball Check, Flanged - ANSI |  | BCQ1016005 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 19 | CV_37100 | [11 empty] | PVC | [10 empty] | TBD | 0.5 |  |  | Manual | Ball Check Valve | N.A | Flanged
Antifoam Dosing System - Ball Check Valve - 01 | C2NC-1800-CHEM-FOAM-CV_37101 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Check Valve - SIMTECH BCQ1016005 1/2" PVC/EPDM T.U. Ball Check, Flanged - ANSI |  | BCQ1016005 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 19 | CV_37101 | [11 empty] | PVC | [10 empty] | TBD | 0.5 |  |  | Manual | Ball Check Valve | N.A | Flanged
Antifoam Dosing System - Ball Check Valve - 02 | C2NC-1800-CHEM-FOAM-CV_37102 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Check Valve - SIMTECH BCQ1016005 1/2" PVC/EPDM T.U. Ball Check, Flanged - ANSI |  | BCQ1016005 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 19 | CV_37102 | [11 empty] | PVC | [10 empty] | TBD | 0.5 |  |  | Manual | Ball Check Valve | N.A | Flanged
Antifoam Dosing System - Ball Check Valve - 03 | C2NC-1800-CHEM-FOAM-CV_37103 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Check Valve - SIMTECH BCQ1016005 1/2" PVC/EPDM T.U. Ball Check, Flanged - ANSI |  | BCQ1016005 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 19 | CV_37103 | [11 empty] | PVC | [10 empty] | TBD | 0.5 |  |  | Manual | Ball Check Valve | N.A | Flanged
Antifoam Dosing System - Ball Valve - 00 | C2NC-1800-CHEM-FOAM-MV_37100 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | TBD |  |  |  | Water America |  |  |  | AN-1156 A01 01 | 19 | MV_37100 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Ball Valve - 01 | C2NC-1800-CHEM-FOAM-MV_37101 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_37101 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Ball Valve - 02 | C2NC-1800-CHEM-FOAM-MV_37102 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_37102 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Ball Valve - 03 | C2NC-1800-CHEM-FOAM-MV_37103 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_37103 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Ball Valve - 04 | C2NC-1800-CHEM-FOAM-MV_37104 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_37104 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Ball Valve - 05 | C2NC-1800-CHEM-FOAM-MV_37105 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_37105 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Ball Valve - 06 | C2NC-1800-CHEM-FOAM-MV_37106 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_37106 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Ball Valve - 07 | C2NC-1800-CHEM-FOAM-MV_37107 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_37107 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Ball Valve - 08 | C2NC-1800-CHEM-FOAM-MV_37108 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | 1/2 2-PC FP BALL 1000 WOG |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 19 | MV_37108 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Ball Valve - 09 | C2NC-1800-CHEM-FOAM-MV_37109 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | 1/2 2-PC FP BALL 1000 WOG |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 19 | MV_37109 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Ball Valve - 10 | C2NC-1800-CHEM-FOAM-MV_37110 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | 1/2 2-PC FP BALL 1000 WOG |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 19 | MV_37110 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Ball Valve - 11 | C2NC-1800-CHEM-FOAM-MV_37111 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Manual Valve |  | 1/2 2-PC FP BALL 1000 WOG |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 19 | MV_37111 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
Antifoam Dosing System - Pressure Control Valve - 00 | C2NC-1800-CHEM-FOAM-PRV_37100 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Pressure Relief Valve | [9 empty] | AN-1156 A01 01 | 19 | PRV_37100 | [11 empty] | PVC | [11 empty] | 0.5 |  |  | Manual | Pressure Control Valve | TBD | THRD-F NPT
Antifoam Dosing System - Pressure Reduction Valve - 01 | C2NC-1800-CHEM-FOAM-PRV_37101 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Pressure Relief Valve | [9 empty] | AN-1156 A01 01 | 19 | PRV_37101 | [11 empty] | PVC | [11 empty] | 0.75 |  |  | Manual | Pressure Reduction Valve | N.A | THRD-F NPT
Antifoam Dosing System - Pressure Safety Valve - 00 | C2NC-1800-CHEM-FOAM-PSV_37100 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Pressure Saftey Valve | [9 empty] | AN-1156 A01 01 | 19 | PSV_37100 | [11 empty] | PVC | [11 empty] | 0.5 |  |  | Manual | Pressure Safety Valve | N.A | THRD-F NPT
Antifoam Dosing System - Pressure Safety Valve - 01 | C2NC-1800-CHEM-FOAM-PSV_37101 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Pressure Saftey Valve | [9 empty] | AN-1156 A01 01 | 19 | PSV_37101 | [11 empty] | PVC | [11 empty] | 0.5 |  |  | Manual | Pressure Safety Valve | N.A | THRD-F NPT
Antifoam Dosing System - Solenoid Valve - 00 | C2NC-1800-CHEM-FOAM-SV_37100 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Solenoid Valve - 1/2 HAYWARD SV10050 STE SOLENOID VALVE 110VAC 150#FLANGED PVC |  | 85HAY 050SV10050STE |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 19 | SV_37100 | [11 empty] | PVC | [11 empty] | 0.5 |  |  | Automatic | Solenoid Valve | Electrical | Flanged
Antifoam Dosing System - Solenoid Valve - 01 | C2NC-1800-CHEM-FOAM-SV_37101 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Solenoid Valve - 1/2 HAYWARD SV10050 STE SOLENOID VALVE 110VAC 150#FLANGED PVC |  | 85HAY 050SV10050STE |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 19 | SV_37101 | [11 empty] | PVC | [11 empty] | 0.5 |  |  | Automatic | Solenoid Valve | Electrical | Flanged
Antifoam Dosing System - Solenoid Valve - 02 | C2NC-1800-CHEM-FOAM-SV_37102 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Solenoid Valve - 1/2 HAYWARD SV10050 STE SOLENOID VALVE 110VAC 150#FLANGED PVC |  | 85HAY 050SV10050STE |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 19 | SV_37102 | [11 empty] | PVC | [11 empty] | 0.5 |  |  | Automatic | Solenoid Valve | Electrical | Flanged
Antifoam Dosing System - Solenoid Valve - 03 | C2NC-1800-CHEM-FOAM-SV_37103 | C2NC-1800-CHEM-FOAM | Valves | Antifoam Dosing System Solenoid Valve - 1/2 HAYWARD SV10050 STE SOLENOID VALVE 110VAC 150#FLANGED PVC |  | 85HAY 050SV10050STE |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 19 | SV_37103 | [11 empty] | PVC | [11 empty] | 0.5 |  |  | Automatic | Solenoid Valve | Electrical | Flanged
Sodium Hypochlorite System - Ball Valve - 00 | C2NC-1800-CHEM-HYPO-MV_31200 | C2NC-1800-CHEM-HYPO | Valves | Sodium Hypochlorite System Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | 1/2 2-PC FP BALL 1000 WOG |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 19 | MV_31200 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
Sodium Hypochlorite System - Ball Valve - 01 | C2NC-1800-CHEM-HYPO-MV_31201 | C2NC-1800-CHEM-HYPO | Valves | Sodium Hypochlorite System Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | 1/2 2-PC FP BALL 1000 WOG |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 19 | MV_31201 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
Sodium Hypochlorite System - Needle Valve - 02 | C2NC-1800-CHEM-HYPO-MV_31202 | C2NC-1800-CHEM-HYPO | Valves | Sodium Hypochlorite System Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 19 | MV_31202 | [11 empty] | PVC | [10 empty] | TBD | 0.5 |  |  | Manual | Needle Valve | Manual | TBD
Sodium Hypochlorite System - Ball Valve - 03 | C2NC-1800-CHEM-HYPO-MV_31203 | C2NC-1800-CHEM-HYPO | Valves | Sodium Hypochlorite System Manual Valve - SIMTECH TBB1016015 1-1/2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016015 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 19 | MV_31203 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
Sodium Hypochlorite System - Ball Valve - 04 | C2NC-1800-CHEM-HYPO-MV_31204 | C2NC-1800-CHEM-HYPO | Valves | Sodium Hypochlorite System Manual Valve - SIMTECH TBB1016015 1-1/2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016015 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 19 | MV_31204 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
Sodium Hypochlorite System - Ball Valve - 05 | C2NC-1800-CHEM-HYPO-MV_31205 | C2NC-1800-CHEM-HYPO | Valves | Sodium Hypochlorite System Manual Valve - 1.5 2-PC FP BALL 1000 WOG |  | 1.5 2-PC FP BALL 1000 WOG |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 19 | MV_31205 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
Sodium Hypochlorite System - Pressure Control Valve - 00 | C2NC-1800-CHEM-HYPO-PRV_31200 | C2NC-1800-CHEM-HYPO | Valves | Sodium Hypochlorite System Pressure Relief Valve | [9 empty] | AN-1156 A01 01 | 19 | PRV_31200 | [11 empty] | PVC | [11 empty] | 1.5 |  |  | Manual | Pressure Control Valve | TBD | THRD-F NPT
Sodium Hypochlorite System - Pressure Safety Valve - 00 | C2NC-1800-CHEM-HYPO-PSV_31200 | C2NC-1800-CHEM-HYPO | Valves | Sodium Hypochlorite System Pressure Saftey Valve | [9 empty] | AN-1156 A01 01 | 19 | PSV_31200 | [11 empty] | PVC | [11 empty] | 1.5 |  |  | Manual | Pressure Safety Valve | N.A | THRD-F NPT
Emulsion Polymer WAS - Ball Valve - 00 | C2NC-1800-FLOC-MV_35200 | C2NC-1800-FLOC | Valves | Emulsion Polymer WAS Manual Valve |  | 1/2 2-PC FP BALL 1000 WOG |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 17 | MV_35200 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
Emulsion Polymer WAS - Ball Valve - 01 | C2NC-1800-FLOC-MV_35201 | C2NC-1800-FLOC | Valves | Emulsion Polymer WAS Manual Valve | [9 empty] | AN-1156 A01 01 | 17 | MV_35201 | [23 empty] | 1 |  |  | Manual | Ball Valve
Emulsion Polymer WAS - Ball Valve - 02 | C2NC-1800-FLOC-MV_35202 | C2NC-1800-FLOC | Valves | Emulsion Polymer WAS Manual Valve | [9 empty] | AN-1156 A01 01 | 17 | MV_35202 | [23 empty] | 1 |  |  | Manual | Ball Valve
Emulsion Polymer WAS - Ball Valve - 03 | C2NC-1800-FLOC-MV_35203 | C2NC-1800-FLOC | Valves | Emulsion Polymer WAS Manual Valve | [9 empty] | AN-1156 A01 01 | 17 | MV_35203 | [23 empty] | 2 |  |  | Manual | Ball Valve
Emulsion Polymer WAS - Ball Valve - 04 | C2NC-1800-FLOC-MV_35204 | C2NC-1800-FLOC | Valves | Emulsion Polymer WAS Manual Valve | [9 empty] | AN-1156 A01 01 | 17 | MV_35204 | [23 empty] | 2 |  |  | Manual | Ball Valve
Emulsion Polymer WAS - Ball Valve - 05 | C2NC-1800-FLOC-MV_35205 | C2NC-1800-FLOC | Valves | Emulsion Polymer WAS Manual Valve | [9 empty] | AN-1156 A01 01 | 17 | MV_35205 | [23 empty] | 1.5 |  |  | Manual | Ball Valve
Emulsion Polymer WAS - Ball Valve - 06 | C2NC-1800-FLOC-MV_35206 | C2NC-1800-FLOC | Valves | Emulsion Polymer WAS Manual Valve | [9 empty] | AN-1156 A01 01 | 17 | MV_35206 | [23 empty] | 2 |  |  | Manual | Ball Valve
Emulsion Polymer WAS - Ball Valve - 10 | C2NC-1800-FLOC-MV_35210 | C2NC-1800-FLOC | Valves | Emulsion Polymer WAS Manual Valve |  | 1 2-PC FP BALL 1000 WOG |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 17 | MV_35210 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.75 |  |  | Manual | Ball Valve | Manual | Flanged
Emulsion Polymer WAS - Solenoid Valve - 00 | C2NC-1800-FLOC-SV_35200 | C2NC-1800-FLOC | Valves | Emulsion Polymer WAS Solenoid Valve | [9 empty] | AN-1156 A01 01 | 17 | SV_35200 | [23 empty] | 0.75 |  |  | Automatic | Solenoid Valve
MBR - Swing Check Valve - 01 | C2NC-1800-MBR-CV_65101 | C2NC-1800-MBR | Valves | MBR Check Valve - Champion Valves, Inc. Figure 8CVR15-SSES-R 8" ASME Class 150, RF Dual Disc Wafer Check, Valve, 316 SS Body, 316 SS Disc, EPDM Seat with 316 SS Spring. Retainerless Design |  | SWING |  |  |  | JB/CHAMPION |  |  |  | AN-1156 A01 01 | 12 | CV_65101 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 8 |  |  | Manual | Swing Check Valve | N.A | FLG
MBR - Swing Check Valve - 02 | C2NC-1800-MBR-CV_65102 | C2NC-1800-MBR | Valves | MBR Check Valve - Champion Valves, Inc. Figure 8CVR15-SSES-R 8" ASME Class 150, RF Dual Disc Wafer Check, Valve, 316 SS Body, 316 SS Disc, EPDM Seat with 316 SS Spring. Retainerless Design |  | SWING |  |  |  | JB/CHAMPION |  |  |  | AN-1156 A01 01 | 12 | CV_65102 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 8 |  |  | Manual | Swing Check Valve | N.A | FLG
MBR - Swing Check Valve - 03 | C2NC-1800-MBR-CV_65103 | C2NC-1800-MBR | Valves | MBR Check Valve |  | 4708K53 |  |  |  | McMaster Carr |  |  |  | AN-1156 A01 01 | 10 | CV_65103 | [11 empty] | SSA2 | [10 empty] | ASTM A479 Type 316 | 0.5 |  |  | Manual | Swing Check Valve | N.A | FLG
MBR - Swing Check Valve - 04 | C2NC-1800-MBR-CV_65104 | C2NC-1800-MBR | Valves | MBR Check Valve |  | 4708K53 |  |  |  | McMaster Carr |  |  |  | AN-1156 A01 01 | 10 | CV_65104 | [11 empty] | SSA2 | [10 empty] | ASTM A479 Type 316 | 0.5 |  |  | Manual | Swing Check Valve | N.A | FLG
MBR - Ball Check Valve - 09 | C2NC-1800-MBR-CV_65109 | C2NC-1800-MBR | Valves | MBR Check Valve | [9 empty] | AN-1156 A01 01 | 13 | CV_65109 | [11 empty] | SSA1 | [11 empty] | 1 |  |  | Manual | Ball Check Valve | N.A | Flanged
MBR - Swing Check Valve - 10 | C2NC-1800-MBR-CV_65110 | C2NC-1800-MBR | Valves | MBR Check Valve |  | SWING | [7 empty] | AN-1156 A01 01 | 13 | CV_65110 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 1 |  |  | Manual | Swing Check Valve | N.A | FLG
MBR - Swing Check Valve - 11 | C2NC-1800-MBR-CV_65111 | C2NC-1800-MBR | Valves | MBR Check Valve |  | SWING | [7 empty] | AN-1156 A01 01 | 13 | CV_65111 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 1.5 |  |  | Manual | Swing Check Valve | N.A | FLG
MBR - Swing Check Valve - 12 | C2NC-1800-MBR-CV_65112 | C2NC-1800-MBR | Valves | MBR Check Valve |  | SWING | [7 empty] | AN-1156 A01 01 | 13 | CV_65112 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 1.5 |  |  | Manual | Swing Check Valve | N.A | FLG
MBR - Knife-Gate Valve - 01 | C2NC-1800-MBR-FV_65101 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - SAV-B Investment Casting Full Bore 4â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w 2 SPDT Prox switches ( Micron) c/w Nitra solenoid 120 Vac c/w D A Cylinder (based on 80 psi air) |  | SAV-B Investment Casting Full Bore 4â€ |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 10 | FV_65101 | [11 empty] | SSA2 | [10 empty] | AISI 316/EN 1-4301 | 4 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
MBR - Knife-Gate Valve - 03 | C2NC-1800-MBR-FV_65103 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - SAV-B Investment Casting Full Bore 4â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w 2 SPDT Prox switches ( Micron) c/w Nitra solenoid 120 Vac c/w D A Cylinder (based on 80 psi air) |  | SAV-B Investment Casting Full Bore 4â€ |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 10 | FV_65103 | [11 empty] | SSA2 | [10 empty] | AISI 316/EN 1-4301 | 4 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
MBR - Knife-Gate Valve - 04 | C2NC-1800-MBR-FV_65104 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - SAV-B Investment Casting Full Bore 10â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w 2 SPDT Prox switches ( Micron) c/w Nitra solenoid 120 Vac c/w D A Cylinder (based on 80 psi air) |  | SAV-B Investment Casting Full Bore 10" |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 10 | FV_65104 | [11 empty] | PVC | [10 empty] | TBD | 10 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
MBR - Butterfly Valve - 05 | C2NC-1800-MBR-FV_65105 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - 6 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH BRAY SERIES 92 DOUBLE ACTING PNEUMATIC ACTUATOR SIZE 119, 30MM DD AND BRAY SERIES 5A SWITCH BOX, 2xSPDT MECHANICAL SWITCHES, 8 TERMINAL POINTS, IP66/IP67, cULus, CE, NEMA 4/4X, BRAY SERIES 63 SOLENOID VALVE, FLYING LEADS, NEMA 4, 120 VAC AND SPEED CONTROL |  | 6 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 10 | FV_65105 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 6 |  |  | Automatic | Butterfly Valve | Pneumatic | LUG
MBR - Butterfly Valve - 06 | C2NC-1800-MBR-FV_65106 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH BRAY SERIES 92 DOUBLE ACTING PNEUMATIC ACTUATOR SIZE 83, 19MM DD AND BRAY SERIES 5A SWITCH BOX, 2xSPDT MECHANICAL SWITCHES, 8 TERMINAL POINTS, IP66/IP67, cULus, CE, NEMA 4/4X |  | 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 13 | FV_65106 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 4 |  |  | Automatic | Butterfly Valve | Pneumatic | LUG
MBR - Butterfly Valve - 07 | C2NC-1800-MBR-FV_65107 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - 6 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH BRAY SERIES 92 DOUBLE ACTING PNEUMATIC ACTUATOR SIZE 119, 30MM DD AND BRAY SERIES 5A SWITCH BOX, 2xSPDT MECHANICAL SWITCHES, 8 TERMINAL POINTS, IP66/IP67, cULus, CE, NEMA 4/4X, BRAY SERIES 63 SOLENOID VALVE, FLYING LEADS, NEMA 4, 120 VAC AND SPEED CONTROL |  | 6 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 10 | FV_65107 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 6 |  |  | Automatic | Butterfly Valve | Pneumatic | LUG
MBR - Butterfly Valve - 08 | C2NC-1800-MBR-FV_65108 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH BRAY SERIES 92 DOUBLE ACTING PNEUMATIC ACTUATOR SIZE 83, 19MM DD AND BRAY SERIES 5A SWITCH BOX, 2xSPDT MECHANICAL SWITCHES, 8 TERMINAL POINTS, IP66/IP67, cULus, CE, NEMA 4/4X |  | 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 13 | FV_65108 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 4 |  |  | Automatic | Butterfly Valve | Pneumatic | LUG
MBR - Ball Valve - 09 | C2NC-1800-MBR-FV_65109 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - 1" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections with PA-Series double acting pneumatic actuator with Epoxy and Rilsan coated die cast aluminum body and end caps, stainless steel shaft. With mounting for 1" Type 21 ball valve. |  | 1" Type 21 True Union Ball Valve |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 13 | FV_65109 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Automatic | Ball Valve | Pneumatic | THRD-F NPT
MBR - Ball Valve - 10 | C2NC-1800-MBR-FV_65110 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - 1" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections with PA-Series double acting pneumatic actuator with Epoxy and Rilsan coated die cast aluminum body and end caps, stainless steel shaft. PA-Series double acting pneumatic actuator with Epoxy and Rilsan coated die cast aluminum body and end caps, stainless steel shaft. With mounting for 1" Type 21 ball valve. |  | 1" Type 21 True Union Ball Valve |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 13 | FV_65110 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Automatic | Ball Valve | Pneumatic | THRD-F NPT
MBR - Ball Valve - 11 | C2NC-1800-MBR-FV_65111 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - 1-1/2" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, Viton O-Rings, socket/threaded COMBO end connections with PA-Series double acting pneumatic actuator with Epoxy and Rilsan coated die cast aluminum body and end caps, stainless steel shaft. With mounting for 1 -1/2" Type 21 ball valve. |  | 1.5" Type 21 True Union Ball Valve |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 13 | FV_65111 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1.5 |  |  | Automatic | Ball Valve | Pneumatic | THRD-F NPT
MBR - Ball Valve - 12 | C2NC-1800-MBR-FV_65112 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - 1-1/2" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, Viton O-Rings, socket/threaded COMBO end connections with PA-Series double acting pneumatic actuator with Epoxy and Rilsan coated die cast aluminum body and end caps, stainless steel shaft. With mounting for 1 -1/2" Type 21 ball valve. |  | 1.5" Type 21 True Union Ball Valve |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 13 | FV_65112 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1.5 |  |  | Automatic | Ball Valve | Pneumatic | THRD-F NPT
MBR - Knife-Gate Valve - 13 | C2NC-1800-MBR-FV_65113 | C2NC-1800-MBR | Valves | MBR Pneumatic Valve - SAV-B Investment Casting Full Bore 10â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w 2 SPDT Prox switches ( Micron) c/w Nitra solenoid 120 Vac c/w D A Cylinder (based on 80 psi air) |  | TBD |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 10 | FV_65113 | [11 empty] | PVC | [10 empty] | TBD | 10 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
MBR - Knife-Gate Valve - 00 | C2NC-1800-MBR-MV_65100 | C2NC-1800-MBR | Valves | MBR Manual Valve - SAV-B Investment Casting Full Bore 4â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w SS yoke c/w Hand wheel Operator |  | TBD |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 10 | MV_65100 | [11 empty] | PVC | [10 empty] | TBD | 4 |  |  | Manual | Knife-Gate Valve | Manual | LUG
MBR - Butterfly Valve - 01 | C2NC-1800-MBR-MV_65101 | C2NC-1800-MBR | Valves | MBR Manual Valve - 8 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH GEAR OPERATOR AND HANDWHEEL |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 12 | MV_65101 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 8 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Butterfly Valve - 02 | C2NC-1800-MBR-MV_65102 | C2NC-1800-MBR | Valves | MBR Manual Valve - 6 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 13 | MV_65102 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 6 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Knife-Gate Valve - 03 | C2NC-1800-MBR-MV_65103 | C2NC-1800-MBR | Valves | MBR Manual Valve - SAV-B Investment Casting Full Bore 4â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w SS yoke c/w Hand wheel Operator |  | "STAFSIO" or similar |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 11 | MV_65103 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Manual | Knife-Gate Valve | Manual | LUG
MBR - Knife-Gate Valve - 04 | C2NC-1800-MBR-MV_65104 | C2NC-1800-MBR | Valves | MBR Manual Valve - 495ORB1200203636RHW |  | 12" 20-3636R-12.0-HW ORBINOX KNIFE GATE VALVE BODY AND GATE 316SS EPDM SEAT MANUAL HANDWHEEL |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 10 | MV_65104 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 12 |  |  | Manual | Knife-Gate Valve | Manual | LUG
MBR - Butterfly Valve - 05 | C2NC-1800-MBR-MV_65105 | C2NC-1800-MBR | Valves | MBR Manual Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 10 | MV_65105 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 4 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Ball Valve - 06 | C2NC-1800-MBR-MV_65106 | C2NC-1800-MBR | Valves | MBR Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 10 | MV_65106 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
MBR - Ball Valve - 07 | C2NC-1800-MBR-MV_65107 | C2NC-1800-MBR | Valves | MBR Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 10 | MV_65107 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
MBR - Ball Valve - 08 | C2NC-1800-MBR-MV_65108 | C2NC-1800-MBR | Valves | MBR Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 10 | MV_65108 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
MBR - Ball Valve - 09 | C2NC-1800-MBR-MV_65109 | C2NC-1800-MBR | Valves | MBR Manual Valve - 1 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 10 | MV_65109 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
MBR - Ball Valve - 10 | C2NC-1800-MBR-MV_65110 | C2NC-1800-MBR | Valves | MBR Manual Valve - 1" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections |  | TBD |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 13 | MV_65110 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1 |  |  | Manual | Ball Valve | Manual | Flanged
MBR - Ball Valve - 11 | C2NC-1800-MBR-MV_65111 | C2NC-1800-MBR | Valves | MBR Manual Valve - 1" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections |  | TBD |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 13 | MV_65111 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1 |  |  | Manual | Ball Valve | Manual | Flanged
MBR - Ball Valve - 12 | C2NC-1800-MBR-MV_65112 | C2NC-1800-MBR | Valves | MBR Manual Valve - 1-1/2" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, Viton O-Rings, socket/threaded COMBO end connections |  | TBD |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 13 | MV_65112 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
MBR - Ball Valve - 13 | C2NC-1800-MBR-MV_65113 | C2NC-1800-MBR | Valves | MBR Manual Valve - 1-1/2" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, Viton O-Rings, socket/threaded COMBO end connections |  | TBD |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 13 | MV_65113 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
MBR - Ball Valve - 14 | C2NC-1800-MBR-MV_65114 | C2NC-1800-MBR | Valves | MBR Manual Valve - 1 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 10 | MV_65114 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
MBR - Ball Valve - 15 | C2NC-1800-MBR-MV_65115 | C2NC-1800-MBR | Valves | MBR Manual Valve - 1 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 10 | MV_65115 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
MBR - Butterfly Valve - 16 | C2NC-1800-MBR-MV_65116 | C2NC-1800-MBR | Valves | MBR Manual Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 10 | MV_65116 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 4 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Butterfly Valve - 17 | C2NC-1800-MBR-MV_65117 | C2NC-1800-MBR | Valves | MBR Manual Valve - Champion Valves, Inc. Figure 8CVR15-SSES-R 8" ASME Class 150, RF Dual Disc Wafer Check, Valve, 316 SS Body, 316 SS Disc, EPDM Seat with 316 SS Spring. Retainerless Design |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 12 | MV_65117 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 8 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Butterfly Valve - 18 | C2NC-1800-MBR-MV_65118 | C2NC-1800-MBR | Valves | MBR Manual Valve - 8 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH GEAR OPERATOR AND HANDWHEEL |  | 8" Series 30 BFV |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 12 | MV_65118 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 8 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Butterfly Valve - 19 | C2NC-1800-MBR-MV_65119 | C2NC-1800-MBR | Valves | MBR Manual Valve - 8 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH GEAR OPERATOR AND HANDWHEEL |  | 8" Series 30 BFV |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 12 | MV_65119 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 8 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Knife-Gate Valve - 20 | C2NC-1800-MBR-MV_65120 | C2NC-1800-MBR | Valves | MBR Manual Valve - 495ORB1200203636RHW |  | 12" 20-3636R-12.0-HW ORBINOX KNIFE GATE VALVE BODY AND GATE 316SS EPDM SEAT MANUAL HANDWHEEL | [7 empty] | AN-1156 A01 01 | 10 | MV_65120 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 12 |  |  | Manual | Knife-Gate Valve | Manual | LUG
MBR - Butterfly Valve - 21 | C2NC-1800-MBR-MV_65121 | C2NC-1800-MBR | Valves | MBR Manual Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 10 | MV_65121 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 4 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Butterfly Valve - 22 | C2NC-1800-MBR-MV_65122 | C2NC-1800-MBR | Valves | MBR Manual Valve - 8 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH GEAR OPERATOR AND HANDWHEEL |  | 8" Series 30 BFV |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 12 | MV_65122 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 8 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Butterfly Valve - 23 | C2NC-1800-MBR-MV_65123 | C2NC-1800-MBR | Valves | MBR Manual Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 10 | MV_65123 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 4 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Butterfly Valve - 24 | C2NC-1800-MBR-MV_65124 | C2NC-1800-MBR | Valves | MBR Manual Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 10 | MV_65124 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 4 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Knife-Gate Valve - 25 | C2NC-1800-MBR-MV_65125 | C2NC-1800-MBR | Valves | MBR Manual Valve - ELITE 12" general purpose KGV, Class 150, Lugged RF, MSS-SP81, 316SS body/gate, viton seat, 304SS yoke, V-port |  | E5422VYTW-12-V |  |  |  | FCX |  |  |  | AN-1156 A01 01 | 10 | MV_65125 | [11 empty] | PVC | [10 empty] | TBD | 12 |  |  | Manual | Knife-Gate Valve | Manual | LUG
MBR - Knife-Gate Valve - 26 | C2NC-1800-MBR-MV_65126 | C2NC-1800-MBR | Valves | MBR Manual Valve - 12" 20-3636R-12.0-HW ORBINOX KNIFE GATE VALVE BODY AND GATE 316SS EPDM SEAT MANUAL HANDWHEEL |  | 495ORB1200203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 10 | MV_65126 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 12 |  |  | Manual | Knife-Gate Valve | Manual | LUG
MBR - Butterfly Valve - 27 | C2NC-1800-MBR-MV_65127 | C2NC-1800-MBR | Valves | MBR Manual Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 10 | MV_65127 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 4 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Butterfly Valve - 28 | C2NC-1800-MBR-MV_65128 | C2NC-1800-MBR | Valves | MBR Manual Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 10 | MV_65128 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 4 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Butterfly Valve - 29 | C2NC-1800-MBR-MV_65129 | C2NC-1800-MBR | Valves | MBR Manual Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 10 | MV_65129 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 4 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Knife-Gate Valve - 30 | C2NC-1800-MBR-MV_65130 | C2NC-1800-MBR | Valves | MBR Manual Valve - SAV-B Investment Casting Full Bore 4â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w SS yoke c/w Hand wheel Operator |  | "STAFSIO" or similar |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 10 | MV_65130 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Manual | Knife-Gate Valve | Manual | LUG
MBR - Knife-Gate Valve - 31 | C2NC-1800-MBR-MV_65131 | C2NC-1800-MBR | Valves | MBR Manual Valve - SAV-B Investment Casting Full Bore 4â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w SS yoke c/w Hand wheel Operator |  | "STAFSIO" or similar |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 11 | MV_65131 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Manual | Knife-Gate Valve | Manual | LUG
MBR - Butterfly Valve - 34 | C2NC-1800-MBR-MV_65134 | C2NC-1800-MBR | Valves | MBR Manual Valve - 6 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 10 | MV_65134 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 6 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Butterfly Valve - 35 | C2NC-1800-MBR-MV_65135 | C2NC-1800-MBR | Valves | MBR Manual Valve - 6 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 10 | MV_65135 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 6 |  |  | Manual | Butterfly Valve | Manual | LUG
MBR - Knife-Gate Valve - 41 | C2NC-1800-MBR-MV_65141 | C2NC-1800-MBR | Valves | MBR Manual Valve - 10" 20-3636R-10.0-HW ORBINOX KN1FE VALVE BODY AND GATE 316SS EPDMSEAT |  | 495ORB1000203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 10 | MV_65141 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 10 |  |  | Manual | Knife-Gate Valve | Manual | LUG
MBR - Pressure Relief Valve - 01 | C2NC-1800-MBR-PRV_65101 | C2NC-1800-MBR | Valves | MBR Pressure Relief Valve - PRV installed on the blowers | [5 empty] | Aerzen |  |  |  | AN-1156 A01 01 | 12 | PRV_65101 | [11 empty] | TBD | [11 empty] | 5 |  |  | Manual | Pressure Relief Valve | TBD | THRD-F NPT
MBR - Pressure Relief Valve - 02 | C2NC-1800-MBR-PRV_65102 | C2NC-1800-MBR | Valves | MBR Pressure Relief Valve - PRV installed on the blowers | [5 empty] | Aerzen |  |  |  | AN-1156 A01 01 | 12 | PRV_65102 | [11 empty] | TBD | [11 empty] | 5 |  |  | Manual | Pressure Relief Valve | TBD | THRD-F NPT
MBR - Solenoid Valve - 00 | C2NC-1800-MBR-SV_65100 | C2NC-1800-MBR | Valves | MBR Solenoid Valve - 3/2-way-solenoid valve, direct acting 6014-C02,0FFPSBJ04-5-120/60-08 HA18+PD19 |  | TBD |  |  |  | Burkert |  |  |  | AN-1156 A01 01 | 10 | SV_65100 | [11 empty] | PVC | [10 empty] | TBD | 0.25 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
MBR - Solenoid Valve - 01 | C2NC-1800-MBR-SV_65101 | C2NC-1800-MBR | Valves | MBR Solenoid Valve - 3/2-way-solenoid valve, direct acting 6014-C02,0FFPSBJ04-5-120/60-08 HA18+PD19 |  | TBD |  |  |  | Burkert |  |  |  | AN-1156 A01 01 | 10 | SV_65101 | [11 empty] | PVC | [10 empty] | TBD | 0.25 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
Permeate System - Swing Check Valve - 02 | C2NC-1800-PRM-CV_65302 | C2NC-1800-PRM | Valves | Permeate System Check Valve |  | 4708K52 |  |  |  | McMaster Carr |  |  |  | AN-1156 A01 01 | 13 | CV_65302 | [11 empty] | SSA2 | [10 empty] | ASTM A479 Type 316 | 0.25 |  |  | Manual | Swing Check Valve | N.A | FLG
Permeate System - Butterfly Valve - 00 | C2NC-1800-PRM-FV_65300 | C2NC-1800-PRM | Valves | Permeate System Pneumatic Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH BRAY SERIES 92 DOUBLE ACTING PNEUMATIC ACTUATOR SIZE 83, 19MM DD AND BRAY SERIES 5A SWITCH BOX, 2xSPDT MECHANICAL SWITCHES, 8 TERMINAL POINTS, IP66/IP67, cULus, CE, NEMA 4/4X |  | 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 13 | FV_65300 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 4 |  |  | Automatic | Butterfly Valve | Pneumatic | LUG
Permeate System - Knife-Gate Valve - 01 | C2NC-1800-PRM-FV_65301 | C2NC-1800-PRM | Valves | Permeate System Pneumatic Valve - 11-2134R-06.0-DA KNIFE GATE VALVE STANDARD Model: EB - BIDIRECTIONAL Actuator: PNEUMATIC DOUBLE ACTING Body: DUCTILE Gate: AISI 304 Seat: EPDM Packing: ST Flange: ANSI 150 Size (INCH): 6 : MOUNTED WITH WESTLOCK 2004SBY LIMIT SWITCH 2 X SPDT MECHANICAL SWITCHES COMPLETE WITH HAFNER 120VAC SOLENOID |  | 11-2134R-06.0-DA |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 13 | FV_65301 | [11 empty] | SSA2 | [10 empty] | AISI 316/EN 1-4301 | 6 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
Permeate System - Butterfly Valve - 02 | C2NC-1800-PRM-FV_65302 | C2NC-1800-PRM | Valves | Permeate System Pneumatic Valve - 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH BRAY SERIES 92 DOUBLE ACTING PNEUMATIC ACTUATOR SIZE 83, 19MM DD AND BRAY SERIES 5A SWITCH BOX, 2xSPDT MECHANICAL SWITCHES, 8 TERMINAL POINTS, IP66/IP67, cULus, CE, NEMA 4/4X |  | 4 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 13 | FV_65302 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B | 4 |  |  | Automatic | Butterfly Valve | Pneumatic | Flanged
Permeate System - Knife-Gate Valve - 03 | C2NC-1800-PRM-FV_65303 | C2NC-1800-PRM | Valves | Permeate System Pneumatic Valve - 11-2134R-06.0-DA KNIFE GATE VALVE STANDARD Model: EB - BIDIRECTIONAL Actuator: PNEUMATIC DOUBLE ACTING Body: DUCTILE Gate: AISI 304 Seat: EPDM Packing: ST Flange: ANSI 150 Size (INCH): 6 : MOUNTED WITH WESTLOCK 2004SBY LIMIT SWITCH 2 X SPDT MECHANICAL SWITCHES COMPLETE WITH HAFNER 120VAC SOLENOID |  | 11-2134R-06.0-DA |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 13 | FV_65303 | [11 empty] | SSA2 | [10 empty] | AISI 316/EN 1-4301 | 6 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
Permeate System - Ball Valve - 00 | C2NC-1800-PRM-MV_65300 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - SIMTECH TBB1016040 4" PVC/EPDM TU Ball Valve, Flange |  | TBB1016040 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 13 | MV_65300 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1 |  |  | Manual | Ball Valve | Manual | Flanged
Permeate System - Ball Valve - 01 | C2NC-1800-PRM-MV_65301 | C2NC-1800-PRM | Valves | Permeate System Manual Valve |  | "EBRO" or similar | [7 empty] | AN-1156 A01 01 | 13 | MV_65301 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Ball Valve - 02 | C2NC-1800-PRM-MV_65302 | C2NC-1800-PRM | Valves | Permeate System Manual Valve |  | "EBRO" or similar | [7 empty] | AN-1156 A01 01 | 13 | MV_65302 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Knife-Gate Valve - 03 | C2NC-1800-PRM-MV_65303 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - DAVIS 6IN 59FE 316SS LUG STYLE KNIFE GATE VALVE, EPDM UNIDIRECTIONAL SEAT, HAND WHEEL OPERATED | [5 empty] | FCx |  |  |  | AN-1156 A01 01 | 13 | MV_65303 | [11 empty] | TBD | [11 empty] | 6 |  |  | Manual | Knife-Gate Valve | Manual | LUG
Permeate System - Butterfly Valve - 07 | C2NC-1800-PRM-MV_65307 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 6 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 13 | MV_65307 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 6 |  |  | Manual | Butterfly Valve | Manual | LUG
Permeate System - Ball Valve - 08 | C2NC-1800-PRM-MV_65308 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 13 | MV_65308 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Ball Valve - 09 | C2NC-1800-PRM-MV_65309 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 13 | MV_65309 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Ball Valve - 10 | C2NC-1800-PRM-MV_65310 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 1 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 13 | MV_65310 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Ball Valve - 11 | C2NC-1800-PRM-MV_65311 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 1 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 13 | MV_65311 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Butterfly Valve - 12 | C2NC-1800-PRM-MV_65312 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 6 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 13 | MV_65312 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 6 |  |  | Manual | Butterfly Valve | Manual | LUG
Permeate System - Butterfly Valve - 13 | C2NC-1800-PRM-MV_65313 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 6 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 13 | MV_65313 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 6 |  |  | Manual | Butterfly Valve | Manual | LUG
Permeate System - Ball Valve - 14 | C2NC-1800-PRM-MV_65314 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 13 | MV_65314 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Ball Valve - 15 | C2NC-1800-PRM-MV_65315 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 1 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 13 | MV_65315 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Ball Valve - 16 | C2NC-1800-PRM-MV_65316 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 1 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 13 | MV_65316 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Ball Valve - 17 | C2NC-1800-PRM-MV_65317 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 13 | MV_65317 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Butterfly Valve - 18 | C2NC-1800-PRM-MV_65318 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 6 in. BRAY SERIES 30 BUTTERFLY VALVE WAFER TYPE, FULL RATED, CAST IRON A 126 CLASS B BODY, 316 STAINLESS STEEL DISC, 416SS SHAFT, EPDM SEAT COMPLETE WITH HANDLE |  | "EBRO" or similar |  |  |  | Bray |  |  |  | AN-1156 A01 01 | 13 | MV_65318 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 6 |  |  | Manual | Butterfly Valve | Manual | LUG
Permeate System - Ball Valve - 19 | C2NC-1800-PRM-MV_65319 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 1 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 13 | MV_65319 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Ball Valve - 20 | C2NC-1800-PRM-MV_65320 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - 1 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 13 | MV_65320 | [11 empty] | SSA2 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
Permeate System - Needle Valve - 21 | C2NC-1800-PRM-MV_65321 | C2NC-1800-PRM | Valves | Permeate System Manual Valve - Needle valve at outlet of turbidity meter |  | TBD |  |  |  | Hach |  |  |  | AN-1156 A01 01 | 13 | MV_65321 | [11 empty] | SSA2 | [10 empty] | TBD | 0.25 |  |  | Manual | Needle Valve | Manual | THRD-F NPT
Permeate System - Solenoid Valve - 00 | C2NC-1800-PRM-SV_65300 | C2NC-1800-PRM | Valves | Permeate System Solenoid Valve - 2/2-way-solenoid valve; servo assisted 0290-A-12,0-FF-MS-NM84-BBH/UC-CY CZ34+MT05+PE94+PU09 |  | TBD |  |  |  | Burkert |  |  |  | AN-1156 A01 01 | 13 | SV_65300 | [11 empty] | SSA2 | [10 empty] | TBD | 0.5 |  |  | Automatic | Solenoid Valve | Electrical | THRD-F NPT
Permeate System - Solenoid Valve - 01 | C2NC-1800-PRM-SV_65301 | C2NC-1800-PRM | Valves | Permeate System Solenoid Valve - 2/2-way-solenoid valve; servo assisted 0290-A-12,0-FF-MS-NM84-BBH/UC-CY CZ34+MT05+PE94+PU09 |  | TBD |  |  |  | Burkert |  |  |  | AN-1156 A01 01 | 13 | SV_65301 | [11 empty] | SSA2 | [10 empty] | TBD | 1 |  |  | Automatic | Solenoid Valve | Electrical | TBD
WAS and RAS Systems - Swing Check Valve - 00 | C2NC-1800-RAS-CV_65200 | C2NC-1800-RAS | Valves | WAS and RAS Systems Check Valve - Champion Valves, Inc. Figure 12CVR12-LTBS-P-B 12" Class 125 Dimensions, Plain Face Dual Disc Wafer Check Valve, ASME Class 150 Ductile Iron Body per ASTM A395 Gr. 60-40-18, 304 SS Disc, Buna-N Seat with 316 SS SPRING RETAINERLESS DESIGN |  | 12CVR12-LTBS-P-B |  |  |  | JB/CHAMPION |  |  |  | AN-1156 A01 01 | 14 | CV_65200 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 12 |  |  | Manual | Swing Check Valve | N.A | FLG
WAS and RAS Systems - Swing Check Valve - 02 | C2NC-1800-RAS-CV_65202 | C2NC-1800-RAS | Valves | WAS and RAS Systems Check Valve - Champion Valves, Inc. Figure 12CVR12-LTBS-P-B 12" Class 125 Dimensions, Plain Face Dual Disc Wafer Check Valve, ASME Class 150 Ductile Iron Body per ASTM A395 Gr. 60-40-18, 304 SS Disc, Buna-N Seat with 316 SS SPRING RETAINERLESS DESIGN |  | 12CVR12-LTBS-P-B |  |  |  | JB/CHAMPION |  |  |  | AN-1156 A01 01 | 14 | CV_65202 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 12 |  |  | Manual | Swing Check Valve | N.A | FLG
WAS and RAS Systems - Swing Check Valve - 06 | C2NC-1800-RAS-CV_65206 | C2NC-1800-RAS | Valves | WAS and RAS Systems Check Valve - Champion Valves, Inc. Figure 4CVR12-LTBS-P-B 4" Class 125 Dimensions, Plain Face Dual Disc Wafer Check Valve, ASME Class 150 Ductile Iron Body per ASTM A395 Gr. 60-40-18, 304 SS Disc, Buna-N Seat with 316 SS Spring. Retainerless Design |  | 4CVR12-LTBS-P-B |  |  |  | JB/CHAMPION |  |  |  | AN-1156 A01 01 | 15 | CV_65206 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 4 |  |  | Manual | Swing Check Valve | N.A | FLG
WAS and RAS Systems - Swing Check Valve - 07 | C2NC-1800-RAS-CV_65207 | C2NC-1800-RAS | Valves | WAS and RAS Systems Check Valve - Champion Valves, Inc. Figure 4CVR12-LTBS-P-B 4" Class 125 Dimensions, Plain Face Dual Disc Wafer Check Valve, ASME Class 150 Ductile Iron Body per ASTM A395 Gr. 60-40-18, 304 SS Disc, Buna-N Seat with 316 SS Spring. Retainerless Design |  | 4CVR12-LTBS-P-B |  |  |  | JB/CHAMPION |  |  |  | AN-1156 A01 01 | 15 | CV_65207 | [11 empty] | SSA1 | [10 empty] | ASTM A479 Type 304 | 4 |  |  | Manual | Swing Check Valve | N.A | FLG
WAS and RAS Systems - Knife-Gate Valve - 01 | C2NC-1800-RAS-FV_65201 | C2NC-1800-RAS | Valves | WAS and RAS Systems Pneumatic Valve - MODEL: Ser. 22 Bidirectional full lug knife gate valve. BODY MATERIAL: CF8M (cast 316 SS) GATE MATERIAL: 316 SS SEAT: EPDM PACKING MATERIAL: PTFE impregnated synthetic fiber YOKE: 304 SS FLANGE CONNECTION: ANSI 150 ACTUATOR: DA CYLINDER MOUNTED WITH WESTLOCK 2004SBY LIMIT SWITCH 2 X SPDT MECHANICAL SWITCHES COMPLETE WITH HAFNER 120VAC SOLENOID |  | Ser 22 Bidirectional full lug knife gate valve |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 11 | FV_65201 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 12 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
WAS and RAS Systems - Knife-Gate Valve - 02 | C2NC-1800-RAS-FV_65202 | C2NC-1800-RAS | Valves | WAS and RAS Systems Pneumatic Valve - MODEL: Ser. 22 Bidirectional full lug knife gate valve. BODY MATERIAL: CF8M (cast 316 SS) GATE MATERIAL: 316 SS SEAT: EPDM PACKING MATERIAL: PTFE impregnated synthetic fiber YOKE: 304 SS FLANGE CONNECTION: ANSI 150 ACTUATOR: DA CYLINDER MOUNTED WITH WESTLOCK 2004SBY LIMIT SWITCH 2 X SPDT MECHANICAL SWITCHES COMPLETE WITH HAFNER 120VAC SOLENOID |  | Ser 22 Bidirectional full lug knife gate valve |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 11 | FV_65202 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 12 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
WAS and RAS Systems - Knife-Gate Valve - 03 | C2NC-1800-RAS-FV_65203 | C2NC-1800-RAS | Valves | WAS and RAS Systems Pneumatic Valve - MODEL: Ser. 22 Bidirectional full lug knife gate valve. BODY MATERIAL: CF8M (cast 316 SS) GATE MATERIAL: 316 SS SEAT: EPDM PACKING MATERIAL: PTFE impregnated synthetic fiber YOKE: 304 SS FLANGE CONNECTION: ANSI 150 ACTUATOR: DA CYLINDER MOUNTED WITH WESTLOCK 2004SBY LIMIT SWITCH 2 X SPDT MECHANICAL SWITCHES COMPLETE WITH HAFNER 120VAC SOLENOID |  | Ser 22 Bidirectional full lug knife gate valve |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 11 | FV_65203 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 12 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
WAS and RAS Systems - Knife-Gate Valve - 04 | C2NC-1800-RAS-FV_65204 | C2NC-1800-RAS | Valves | WAS and RAS Systems Pneumatic Valve - 11-2134R-06.0-DA KNIFE GATE VALVE STANDARD Model: EB - BIDIRECTIONAL Actuator: PNEUMATIC DOUBLE ACTING Body: DUCTILE Gate: AISI 304 Seat: EPDM Packing: ST Flange: ANSI 150 Size (INCH): 6 : MOUNTED WITH WESTLOCK 2004SBY LIMIT SWITCH 2 X SPDT MECHANICAL SWITCHES COMPLETE WITH HAFNER 120VAC SOLENOID |  | 11-2134R-06.0-DA |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 11 | FV_65204 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
WAS and RAS Systems - Knife-Gate Valve - 05 | C2NC-1800-RAS-FV_65205 | C2NC-1800-RAS | Valves | WAS and RAS Systems Pneumatic Valve - 11-2134R-06.0-DA KNIFE GATE VALVE STANDARD Model: EB - BIDIRECTIONAL Actuator: PNEUMATIC DOUBLE ACTING Body: DUCTILE Gate: AISI 304 Seat: EPDM Packing: ST Flange: ANSI 150 Size (INCH): 6 : MOUNTED WITH WESTLOCK 2004SBY LIMIT SWITCH 2 X SPDT MECHANICAL SWITCHES COMPLETE WITH HAFNER 120VAC SOLENOID |  | 11-2134R-06.0-DA |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 11 | FV_65205 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Automatic | Knife-Gate Valve | Pneumatic | LUG
WAS and RAS Systems - Ball Valve - 00 | C2NC-1800-RAS-MV_65200 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve |  | "EBRO" or similar |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 11 | MV_65200 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
WAS and RAS Systems - Knife-Gate Valve - 01 | C2NC-1800-RAS-MV_65201 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 11-2134R-12.0-HW KNIFE GATE VALVE STANDARD Model: EB - BIDIRECTIONAL Actuator: HANDWHEEL RISING STEM Body: DUCTILE Gate: AISI 304 Seat: EPDM Packing: ST Flange: ANSI 150 |  | "STAFSIO" or similar |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 14 | MV_65201 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 12 |  |  | Manual | Knife-Gate Valve | Manual | LUG
WAS and RAS Systems - Knife-Gate Valve - 04 | C2NC-1800-RAS-MV_65204 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - SAV-B Investment Casting Full Bore 10â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w SS yoke c/w Hand wheel Operator |  | "STAFSIO" or similar |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 14 | MV_65204 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 10 |  |  | Manual | Knife-Gate Valve | Manual | LUG
WAS and RAS Systems - Knife-Gate Valve - 05 | C2NC-1800-RAS-MV_65205 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 11-2134R-12.0-HW KNIFE GATE VALVE STANDARD Model: EB - BIDIRECTIONAL Actuator: HANDWHEEL RISING STEM Body: DUCTILE Gate: AISI 304 Seat: EPDM Packing: ST Flange: ANSI 150 |  | "STAFSIO" or similar |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 14 | MV_65205 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 12 |  |  | Manual | Knife-Gate Valve | Manual | LUG
WAS and RAS Systems - Ball Valve - 07 | C2NC-1800-RAS-MV_65207 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve |  | "EBRO" or similar |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 11 | MV_65207 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
WAS and RAS Systems - Knife-Gate Valve - 08 | C2NC-1800-RAS-MV_65208 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 12" 20-3636R-12.0-HW ORBINOX KNIFE GATE VALVE BODY AND GATE 316SS EPDM SEAT MANUAL HANDWHEEL |  | 495ORB1200203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 14 | MV_65208 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 12 |  |  | Manual | Knife-Gate Valve | Manual | LUG
WAS and RAS Systems - Ball Valve - 09 | C2NC-1800-RAS-MV_65209 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - SIMTECH TBB1016005 1/2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016005 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 11 | MV_65209 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
WAS and RAS Systems - Ball Valve - 10 | C2NC-1800-RAS-MV_65210 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1-1/2" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections |  | TBD |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 14 | MV_65210 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
WAS and RAS Systems - Ball Valve - 11 | C2NC-1800-RAS-MV_65211 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | TBD |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 14 | MV_65211 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
WAS and RAS Systems - Ball Valve - 12 | C2NC-1800-RAS-MV_65212 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1-1/2" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections |  | TBD |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 14 | MV_65212 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
WAS and RAS Systems - Ball Valve - 13 | C2NC-1800-RAS-MV_65213 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1-1/2" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections |  | TBD |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 14 | MV_65213 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
WAS and RAS Systems - Ball Valve - 14 | C2NC-1800-RAS-MV_65214 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1-1/2" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections |  | TBD |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 14 | MV_65214 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
WAS and RAS Systems - Ball Valve - 15 | C2NC-1800-RAS-MV_65215 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | TBD |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 14 | MV_65215 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
WAS and RAS Systems - Knife-Gate Valve - 16 | C2NC-1800-RAS-MV_65216 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - ELITE 12" general purpose KGV, Class 150, Lugged RF, MSS-SP81, 316SS body/gate, viton seat, 304SS yoke, V-port |  | E5422VYTW-12-V |  |  |  | FCX |  |  |  | AN-1156 A01 01 | 6 | MV_65216 | [11 empty] | CSA | [11 empty] | 12 |  |  | Manual | Knife-Gate Valve | Manual | LUG
WAS and RAS Systems - Knife-Gate Valve - 17 | C2NC-1800-RAS-MV_65217 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - ELITE 12" general purpose KGV, Class 150, Lugged RF, MSS-SP81, 316SS body/gate, viton seat, 304SS yoke, V-port |  | E5422VYTW-12-V |  |  |  | FCX |  |  |  | AN-1156 A01 01 | 7 | MV_65217 | [11 empty] | CSA | [11 empty] | 12 |  |  | Manual | Knife-Gate Valve | Manual | LUG
WAS and RAS Systems - Knife-Gate Valve - 18 | C2NC-1800-RAS-MV_65218 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 12" 20-3636R-12.0-HW ORBINOX KNIFE GATE VALVE BODY AND GATE 316SS EPDM SEAT MANUAL HANDWHEEL |  | 495ORB1200203636RHW |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 8 | MV_65218 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 12 |  |  | Manual | Knife-Gate Valve | Manual | LUG
WAS and RAS Systems - Ball Valve - 19 | C2NC-1800-RAS-MV_65219 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - SIMTECH TBB1016005 1/2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016005 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 11 | MV_65219 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 0.5 |  |  | Manual | Ball Valve | Manual | Flanged
WAS and RAS Systems - Ball Valve - 20 | C2NC-1800-RAS-MV_65220 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve |  | 46495K22 |  |  |  | McMaster Carr |  |  |  | AN-1156 A01 01 | 14 | MV_65220 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.75 |  |  | Manual | Ball Valve | Manual | TBD
WAS and RAS Systems - Knife-Gate Valve - 29 | C2NC-1800-RAS-MV_65229 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - SAV-B Investment Casting Full Bore 10â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w SS yoke c/w Hand wheel Operator |  | TBD |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 14 | MV_65229 | [11 empty] | PVC | [10 empty] | TBD | 10 |  |  | Manual | Knife-Gate Valve | Manual | LUG
WAS and RAS Systems - Knife-Gate Valve - 30 | C2NC-1800-RAS-MV_65230 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 11-2134R-06.0-HW KNIFE GATE VALVE STANDARD Model: EB - BIDIRECTIONAL Actuator: HANDWHEEL RISING STEM Body: DUCTILE Gate: AISI 304 Seat: EPDM Packing: ST Flange: ANSI 150 |  | "STAFSIO" or similar |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 15 | MV_65230 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Manual | Knife-Gate Valve | Manual | Flanged-Wafer
WAS and RAS Systems - Knife-Gate Valve - 31 | C2NC-1800-RAS-MV_65231 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - SAV-B Investment Casting Full Bore 4â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w SS yoke c/w Hand wheel Operator |  | "STAFSIO" or similar |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 15 | MV_65231 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Manual | Knife-Gate Valve | Manual | Flanged-Lug
WAS and RAS Systems - Knife-Gate Valve - 32 | C2NC-1800-RAS-MV_65232 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - SAV-B Investment Casting Full Bore 4â€ c/w 304 SS Body & Gate c/w EPDM Seat c/w PTFE Packing c/w SS yoke c/w Hand wheel Operator |  | "STAFSIO" or similar |  |  |  | SA Valves |  |  |  | AN-1156 A01 01 | 15 | MV_65232 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Manual | Knife-Gate Valve | Manual | Flanged-Lug
WAS and RAS Systems - Knife-Gate Valve - 33 | C2NC-1800-RAS-MV_65233 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve |  | "STAFSIO" or similar | [7 empty] | AN-1156 A01 01 | 15 | MV_65233 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Manual | Knife-Gate Valve | Manual | LUG
WAS and RAS Systems - Knife-Gate Valve - 34 | C2NC-1800-RAS-MV_65234 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 11-2134R-06.0-HW KNIFE GATE VALVE STANDARD Model: EB - BIDIRECTIONAL Actuator: HANDWHEEL RISING STEM Body: DUCTILE Gate: AISI 304 Seat: EPDM Packing: ST Flange: ANSI 150 |  | "STAFSIO" or similar |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 11 | MV_65234 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 6 |  |  | Manual | Knife-Gate Valve | Manual | LUG
WAS and RAS Systems - Ball Valve - 41 | C2NC-1800-RAS-MV_65241 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1-1/2" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections |  | "EBRO" or similar |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 15 | MV_65241 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
WAS and RAS Systems - Ball Valve - 42 | C2NC-1800-RAS-MV_65242 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections |  | "EBRO" or similar |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 15 | MV_65242 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
WAS and RAS Systems - Ball Valve - 43 | C2NC-1800-RAS-MV_65243 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1-1/2" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections |  | "EBRO" or similar |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 15 | MV_65243 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
WAS and RAS Systems - Ball Valve - 44 | C2NC-1800-RAS-MV_65244 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1" Type 21 True Union Ball Valve, PVC Body and shaft, teflon seats, EPDM O-Rings, socket/threaded COMBO end connections |  | "EBRO" or similar |  |  |  | Chemline |  |  |  | AN-1156 A01 01 | 15 | MV_65244 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 1 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
WAS and RAS Systems - Ball Valve - 45 | C2NC-1800-RAS-MV_65245 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 15 | MV_65245 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
WAS and RAS Systems - Ball Valve - 46 | C2NC-1800-RAS-MV_65246 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 15 | MV_65246 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
WAS and RAS Systems - Ball Valve - 47 | C2NC-1800-RAS-MV_65247 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 15 | MV_65247 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
WAS and RAS Systems - Ball Valve - 48 | C2NC-1800-RAS-MV_65248 | C2NC-1800-RAS | Valves | WAS and RAS Systems Manual Valve - 1/2 2-PC FP BALL 1000 WOG |  | "EBRO" or similar |  |  |  | Pinnacle |  |  |  | AN-1156 A01 01 | 15 | MV_65248 | [11 empty] | SSA1 | [10 empty] | ASTM A 351 CF 8 | 0.5 |  |  | Manual | Ball Valve | Manual | THRD-F NPT
WAS Screw Dewatering Press - Swing Check Valve - 00 | C2NC-1800-WAS-CV_51400 | C2NC-1800-WAS | Valves | WAS Screw Dewatering Press Check Valve - I" 150# FLGD PVC SWING CHECK VALVE HAYWARDYCl0I00F |  | 85HAYI00YCI0I00FSCV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 16 | CV_51400 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B | 1.5 |  |  | Manual | Swing Check Valve | N.A | Flanged
WAS Screw Dewatering Press - Ball Valve - 00 | C2NC-1800-WAS-MV_51400 | C2NC-1800-WAS | Valves | WAS Screw Dewatering Press Manual Valve - SIMTECH TBB1016010 1" PVC/EPDM TU Ball Valve, Flange |  | TBB1016010 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 16 | MV_51400 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
WAS Screw Dewatering Press - Knife-Gate Valve - 01 | C2NC-1800-WAS-MV_51401 | C2NC-1800-WAS | Valves | WAS Screw Dewatering Press Manual Valve |  | 11-2134R-06.0-HW , KNIFE GATE VALVE STANDARD , Model: EB - BIDIRECTIONAL, Actuator: HANDWHEEL RISING STEM , Body: DUCTILE , Gate: AISI 304, Seat: EPDM, Packing: ST, Flange: ANSI 150 |  |  |  | JB/ORBINOX |  |  |  | AN-1156 A01 01 | 15 | MV_51401 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 4 |  |  | Manual | Knife-Gate Valve | Manual | Flanged-Wafer
WAS Screw Dewatering Press - Ball Valve - 02 | C2NC-1800-WAS-MV_51402 | C2NC-1800-WAS | Valves | WAS Screw Dewatering Press Manual Valve - SIMTECH TBB1016020 2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016020 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 16 | MV_51402 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 2 |  |  | Manual | Ball Valve | Manual | Flanged
WAS Screw Dewatering Press - Ball Valve - 03 | C2NC-1800-WAS-MV_51403 | C2NC-1800-WAS | Valves | WAS Screw Dewatering Press Manual Valve - SIMTECH TBB1016020 2" PVC/EPDM TU Ball Valve, Flange |  | TBB1016020 |  |  |  | Fluiteco |  |  |  | AN-1156 A01 01 | 16 | MV_51403 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1.5 |  |  | Manual | Ball Valve | Manual | Flanged
WAS Screw Dewatering Press - Ball Valve - 04 | C2NC-1800-WAS-MV_51404 | C2NC-1800-WAS | Valves | WAS Screw Dewatering Press Manual Valve |  | TBD | [7 empty] | AN-1156 A01 01 | 16 | MV_51404 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 4 |  |  | Manual | Ball Valve | Manual | Flanged
WAS Screw Dewatering Press - Knife-Gate Valve - 05 | C2NC-1800-WAS-MV_51405 | C2NC-1800-WAS | Valves | WAS Screw Dewatering Press Manual Valve - 3 ORBINOX LUG SOFT SEAT KNJFE GATE VALVESS BODY EPDM SEAT SERIES 20-3636R-HW |  | 300203636RKGV |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 16 | MV_51405 | [11 empty] | SSA1 | [10 empty] | AISI 304/EN 1-4301 | 3 |  |  | Manual | Knife-Gate Valve | Manual | LUG
WAS Screw Dewatering Press - Ball Valve - 06 | C2NC-1800-WAS-MV_51406 | C2NC-1800-WAS | Valves | WAS Screw Dewatering Press Manual Valve - SIMTECH TBB1016010 1" PVC/EPDM TU Ball Valve, Flange |  | TBB1016010 |  |  |  | FCx |  |  |  | AN-1156 A01 01 | 16 | MV_51406 | [11 empty] | PVC | [10 empty] | PVC Type 1 Grade 1, Class 12454-B, Teflon Seat | 1 |  |  | Manual | Ball Valve | Manual | Flanged
WAS Screw Dewatering Press - Solenoid Valve - 00 | C2NC-1800-WAS-SV_51400 | C2NC-1800-WAS | Valves | WAS Screw Dewatering Press Solenoid Valve - PVC Soldenoid valve 110VAX 150# Flanged |  | 85HAY100SV10100STE |  |  |  | Macomb |  |  |  | AN-1156 A01 01 | 16 | SV_51400 | [11 empty] | PVC | [10 empty] | TBD | 1 |  |  | Automatic | Solenoid Valve | Electrical | TBD

## Panels
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Material of Construction | Instrument Diameter | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes
Panel List for 01-E-1000-500
Panel Title | Downstream Panels | Downstream Panel Drawing
SWG-50-4160-A
UTX-50-4160-A
SWG-50-4160-B
UTX-50-4160-B
SWBD-50-480-A |  | 01-E-1500-501
UTX-50-480-A
SWBD-40-480-A |  | 01-E-1400-500
UTX-40-480-A
SWBD-20-480-A |  | 01-E-1100-500 & 01-E-1200-500
UTX-20-480-A
MCC-80-480-A
UTX-80-480-A |  | 01-E-1800-500
UTX-P7-208-A
SWBD-P7-208-A |  | 01-E-1000-501
UTX-30-480-A
SWBD-30-480-A |  | 01-E-1300-500 & 01-E-1300-501

## Permits
Asset Name | Asset Code | Location Code | Category | Asset Description | Make | Model | Serial Number | Charge Department Code | Account Code | Supplier/Manufacturer Name | Supplier/Manufacturer Number | Manual Found | Global | P&ID Doc Name | P&ID Page | P&ID Tag | Equipment | Equipment Voltage | Equipment Amps | Equipment Power | Equipment Fluid | Equipment Material of Construction | Equipment Diameter | Equipment Power Feed Location | Equipment Type | Lines | Line Fluid | Line Material of Construction | Line Diameter | Line From | Line To | Line Insulation | Line Design Pressure | Line Schedule | Line Flange Class | Valves | Valve Voltage | Valve Fluid | Valve Material of Construction | Valve Diameter | Valve Power Feed Location | Valve Seal Material | Valve Auto/Manual | Valve Type | Valve Actuator Type | Valve Connections Type | Valve Seat Material | Tanks | Tank Fluid | Tank Material of Construction | Tank Diameter | Tank Height | Tank Volume | Tank Working Volume | Tank Working Height | Tank Type | Instruments | Instrument Voltage | Instrument Fluid | Instrument Material of Construction | Instrument Diameter | Instrument Power Feed Location | Instrument Type | Instrument Wire Count | Instrument Analog/Digital | Instrument Mount Detail | Panels | Panels Voltage | Panels Amps | Panels Power Feed Location | Panel Type | Permits | Permit Number | Permit Description | Permit Title | Permit Permitting Body | Permit Plant Area | Permit Revision Number | Permit Expiry | Packages | Package Voltage | Package Amps | Package Power | Package Power Feed Location | Notes | Unspc Code | Barcode | Facility Latitude | Facility Longitude | Facility Street Address | Facility City | Facility Postal Code | Facility Province | Facility Country | User/User Group name/Personnel Code | Calibration Needed | Aisle | Row | Bin | Low-level asset codes